02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault167 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault79 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault169 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.0 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.0 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault170 | Single Phase Fault with Stuck Breaker on 6815TP38 69.000 (647016) 69 kV Bus a. Apply Fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault171 | Single Phase Fault with Stuck Breaker on 6815TP98 69.000 (647017) 69 kV Bus a. Apply Fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.6. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.8. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault172 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.4. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.5. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault173 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault174 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault175 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault176 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault177 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault178 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault179 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault180 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault181 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault182 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault183 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault184 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault185 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault186 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault187 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault188 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault189 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault190 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault191 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault192 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault193 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault194 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault166 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault196 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault197 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault198 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault199 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault200 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault201 | Single Phase Fault with Stuck Breaker on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply Fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault202 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault203 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault204 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to EGYCTR2G (641089) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault205 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault206 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault207 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault208 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault209 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault210 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault211 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault212 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault213 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault214 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault215 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault216 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault217 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault218 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault219 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault220 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault221 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault222 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault223 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault224 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault225 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault226 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault227 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault228 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault229 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault230 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault231 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault232 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault233 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault234 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault235 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault236 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault237 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault238 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault239 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault240 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault241 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault242 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault243 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault244 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault245 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.2. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.3. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 b.4. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.5. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.6. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault246 | Single Phase Fault with Stuck Breaker on S985 8 69.000 (647985) 69 kV Bus a. Apply Fault at the S985 8 69.000 (647985) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTSMTH8 (640320) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.2. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.3. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault247 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.5. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault248 | Single Phase Fault with Stuck Breaker on 6815TP38 69.000 (647016) 69 kV Bus a. Apply Fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.9. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault249 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault250 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault251 | Single Phase Fault with Stuck Breaker on S912 8 69.000 (647912) 69 kV Bus a. Apply Fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault252 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault253 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault254 | Single Phase Fault with Stuck Breaker on S923 8 69.000 (647923) 69 kV Bus a. Apply Fault at the S923 8 69.000 (647923) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 b.3. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault255 | Single Phase Fault with Stuck Breaker on S924 8 69.000 (647924) 69 kV Bus a. Apply Fault at the S924 8 69.000 (647924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault256 | Single Phase Fault with Stuck Breaker on S928 8 69.000 (647928) 69 kV Bus a. Apply Fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault257 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.6. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault258 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault259 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault260 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.5. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault261 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault262 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault263 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault264 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to J748POI (87487) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault265 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault266 | Single Phase Fault with Stuck Breaker on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply Fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #2 b.2. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault267 | Single Phase Fault with Stuck Breaker on CLATONA7 115.00 (640111) 115 kV Bus a. Apply Fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault268 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault269 | Single Phase Fault with Stuck Breaker on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply Fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.2. GUIDE R7 (640206) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault270 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault271 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault272 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault273 | Single Phase Fault with Stuck Breaker on ORD 7 115.00 (640308) 115 kV Bus a. Apply Fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORD 7 (640308) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 b.2. ORD 7 (640308) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault274 | Single Phase Fault with Stuck Breaker on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply Fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. ST.LIB 7 (640353) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault275 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 b.2. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault276 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERRYC3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. CHERRYC3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault277 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault278 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault279 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault280 | Single Phase Fault with Stuck Breaker on ROSEMONT 7115.00 (640583) 115 kV Bus a. Apply Fault at the ROSEMONT 7115.00 (640583) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEMONT 7 (640583) 115.0 kV to GUIDE R7 (640206) 115.0 kV Transmission Circuit #1 b.2. ROSEMONT 7 (640583) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault281 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault282 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault283 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault284 | Single Phase Fault with Stuck Breaker on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #2 b.2. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault285 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault286 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault287 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault288 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault289 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault290 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault291 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault292 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE7 (640313) 115.0 kV to HILDRTH7 (640222) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault293 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.2. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault294 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault295 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault296 | Single Phase Fault with Stuck Breaker on HASTCTY7 115.00 (641088) 115 kV Bus a. Apply Fault at the HASTCTY7 115.00 (641088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTCTY7 (641088) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. HASTCTY7 (641088) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault297 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S3456 3 (645456) 345.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault298 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault299 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault300 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault301 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY2 (652552) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault166 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault303 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault304 | Single Phase Fault with Stuck Breaker on BROKENB7 115.00 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 b.2. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault305 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault306 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. GENOA 7 (640181) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault307 | Single Phase Fault with Stuck Breaker on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.2. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault308 | Single Phase Fault with Stuck Breaker on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply Fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.LOUP 7 (640284) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.2. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault309 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault310 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault311 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault312 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault313 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault314 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault315 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault316 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARD AVE 3 (635219) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault317 | Single Phase Fault with Stuck Breaker on KNOX 8 69.000 (635243) 69 kV Bus a. Apply Fault at the KNOX 8 69.000 (635243) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOX 8 (635243) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 b.2. KNOX 8 (635243) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault318 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLND 3 (635400) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. HIGHLND 3 (635400) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault319 | Single Phase Fault with Stuck Breaker on MUDDY CREEK7115.00 (640455) 115 kV Bus a. Apply Fault at the MUDDY CREEK7115.00 (640455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUDDY CREEK7 (640455) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 b.2. MUDDY CREEK7 (640455) 115.0 kV to BROKENB7 (640089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault320 | Single Phase Fault with Stuck Breaker on S.SIOUXCITY7115.00 (640424) 115 kV Bus a. Apply Fault at the S.SIOUXCITY7115.00 (640424) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.SIOUXCITY7 (640424) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. S.SIOUXCITY7 (640424) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault321 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault322 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault323 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault324 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault325 | Single Phase Fault with Stuck Breaker on GRPR2 3 345.00 (648520) 345 kV Bus a. Apply Fault at the GRPR2 3 345.00 (648520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR2 3 (648520) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #1 b.2. GRPR2 3 (648520) 345.0 kV to GRPR21X9 (648521) 34.5 kV to GRPR21Y9 (648522) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault326 | Single Phase Fault with Stuck Breaker on GRPR_DMY_BUS345.00 (648527) 345 kV Bus a. Apply Fault at the GRPR_DMY_BUS345.00 (648527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z1 b.2. GRPR_DMY_BUS (648527) 345.0 kV to GRPR12X9 (648517) 34.5 kV to GRPR12Y9 (648518) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault327 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault328 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault329 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault330 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault331 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault332 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault333 | Single Phase Fault with Stuck Breaker on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply Fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.2. HARTGTN7 (640212) 115.0 kV to BELDEN 7 (640080) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault334 | Single Phase Fault with Stuck Breaker on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault335 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault336 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault337 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERDL4 (640330) 230.0 kV to C.CREEK4 (640093) 230.0 kV Transmission Circuit #1 b.2. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault338 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 b.2. SHELCRK3 (640342) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault339 | Single Phase Fault with Stuck Breaker on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply Fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault340 | Single Phase Fault with Stuck Breaker on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply Fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. SUTTON 7 (640372) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault341 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault342 | Single Phase Fault with Stuck Breaker on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply Fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.2. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault343 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YORK SW7 (640413) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. YORK SW7 (640413) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault344 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault345 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault346 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING4 (640214) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault347 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.2. S1254 5 (646254) 161.0 kV to S1249 5 (646249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault348 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S906 S 8 (647906) 69.0 kV to S904 8 (647904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault349 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault350 | Single Phase Fault with Stuck Breaker on S910 8 69.000 (647910) 69 kV Bus a. Apply Fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to S908 8 (647908) 69.0 kV Transmission Circuit #1 b.2. S910 8 (647910) 69.0 kV to JCT205 8 (647105) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault351 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault352 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault353 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY5 (652566) 161.0 kV to PLYMOTH5 (635223) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault354 | Single Phase Fault with Stuck Breaker on OAKLAND7 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault355 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault356 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault357 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault358 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault359 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault168 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault361 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault362 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault363 | Single Phase Fault with Stuck Breaker on MONOLITH 7 (640591) 115 kV Bus a. Apply Fault at the MONOLITH 7 (640591) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault364 | Single Phase Fault with Stuck Breaker on TOBIAS 3 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault365 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault366 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault367 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault368 | Single Phase Fault with Stuck Breaker on MCCOOL 3 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault369 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault370 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault371 | Single Phase Fault with Stuck Breaker on PAULINE7 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault372 | Single Phase Fault with Stuck Breaker on HILDRTH7 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault374 | Single Phase Fault with Stuck Breaker on S910 8 (647910) 69 kV Bus a. Apply Fault at the S910 8 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault375 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault376 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault377 | Single Phase Fault with Stuck Breaker on HOSKINS7 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault378 | Single Phase Fault with Stuck Breaker on NORFOLK7 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault379 | Single Phase Fault with Stuck Breaker on BELDEN 7 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault380 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault381 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault382 | Single Phase Fault with Stuck Breaker on ORD 7 (640308) 115 kV Bus a. Apply Fault at the ORD 7 (640308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORD 7 (640308) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault383 | Single Phase Fault with Stuck Breaker on BROKENB7 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault384 | Single Phase Fault with Stuck Breaker on LOUPCTY7 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault385 | Single Phase Fault with Stuck Breaker on ST.LIB 7 (640353) 115 kV Bus a. Apply Fault at the ST.LIB 7 (640353) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault386 | Single Phase Fault with Stuck Breaker on ALBION 7 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault387 | Single Phase Fault with Stuck Breaker on GENOA 7 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault1 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault2 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault3 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault4 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault5 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault6 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault7 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault8 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault9 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault10 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault11 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault12 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault13 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault14 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault15 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault16 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault17 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault18 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault19 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault20 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault21 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault22 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault23 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault24 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault25 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault26 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault27 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault28 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault29 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault30 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault31 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault32 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault33 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault34 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault35 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault36 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault37 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault38 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault39 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault40 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault41 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault42 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault43 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault44 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault45 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault46 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault47 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault48 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault49 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault50 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault51 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault52 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault53 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault54 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault55 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault56 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault57 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault58 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault59 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault60 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault61 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault62 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault63 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault64 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault65 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault66 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault67 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault68 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault69 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault70 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault71 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault72 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault73 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault74 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault75 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault76 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault77 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault79 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault80 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault81 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault82 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault83 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault84 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault85 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault86 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault87 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault88 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault89 | Single Phase Fault with Stuck Breaker on STHLND 3 345.00 (635016) 345 kV Bus a. Apply Fault at the STHLND 3 345.00 (635016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHLND 3 (635016) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. STHLND 3 (635016) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault90 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault91 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault92 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault93 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault94 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault95 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault96 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault98 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault99 | Single Phase Fault with Stuck Breaker on G16-050-TAP (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault100 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault102 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault103 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault104 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault105 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault106 | Single Phase Fault with Stuck Breaker on G17-183-TAP (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault107 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault108 | Single Phase Fault with Stuck Breaker on STHLND 3 (635016) 345 kV Bus a. Apply Fault at the STHLND 3 (635016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHLND 3 (635016) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault109 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault110 | Single Phase Fault with Stuck Breaker on ST JOE 5 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault111 | Single Phase Fault with Stuck Breaker on CBLUFFS5 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault113 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault114 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault115 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault116 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault117 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault118 | Single Phase Fault with Stuck Breaker on RLHILLS3 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RLHILLS3 (635100) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault119 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault120 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault121 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault122 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault123 | Single Phase Fault with Stuck Breaker on S1280 5 (646280) 161 kV Bus a. Apply Fault at the S1280 5 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1280 5 (646280) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault124 | Single Phase Fault with Stuck Breaker on N.PLATT4 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.PLATT4 (640286) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault125 | Single Phase Fault with Stuck Breaker on BEVERLY7 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault126 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault127 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault128 | Single Phase Fault with Stuck Breaker on IDA CO 3 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault129 | Single Phase Fault with Stuck Breaker on 7FAIRPT (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_REGIONAL_P4_Fault130 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault1 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault2 | 3 Phase fault on NW70FAIRFD7 115.00 (650210) 115 kV Bus a. Apply fault at the NW70FAIRFD7 115.00 (650210) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault3 | 3 Phase fault on NW68HOLDRG7 115.00 (650214) 115 kV Bus a. Apply fault at the NW68HOLDRG7 115.00 (650214) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault4 | 3 Phase fault on 27&PLR 7 115.00 (650229) 115 kV Bus a. Apply fault at the 27&PLR 7 115.00 (650229) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault5 | 3 Phase fault on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault6 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault7 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault8 | 3 Phase fault on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault9 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault10 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault11 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault12 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault13 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault14 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault15 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault16 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault17 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault18 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault19 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault20 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault21 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault22 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault23 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault24 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault25 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault26 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault28 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault29 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault30 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault31 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault32 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault33 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault34 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault35 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault36 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault37 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault38 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault39 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault40 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault42 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault44 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault45 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault46 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault47 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault48 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault49 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault50 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault51 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault52 | 3 Phase fault on PLYMOTH5 161.00 (635223) 161 kV Bus a. Apply fault at the PLYMOTH5 161.00 (635223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault53 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault54 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault55 | 3 Phase fault on VICTORY5 161.00 (635310) 161 kV Bus a. Apply fault at the VICTORY5 161.00 (635310) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault56 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault57 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault59 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault60 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault61 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault62 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault64 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault65 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault66 | 3 Phase fault on MANAWA 5 161.00 (635010) 161 kV Bus a. Apply fault at the MANAWA 5 161.00 (635010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 b.2. MANAWA 5 (635010) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault67 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault68 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault69 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault70 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault71 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault72 | 3 Phase fault on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault73 | 3 Phase fault on NW56&MORTN7 115.00 (650207) 115 kV Bus a. Apply fault at the NW56&MORTN7 115.00 (650207) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW56&MORTN7 (650207) 115.0 kV to NW70FAIRFD7 (650210) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault74 | 3 Phase fault on 2&N 7 115.00 (650230) 115 kV Bus a. Apply fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.6. 2&N 7 (650230) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault75 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault76 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault77 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault78 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault168 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault80 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault81 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault82 | 3 Phase fault on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST.LIB 7 (640353) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault83 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault84 | 3 Phase fault on SUB-C 7 115.00 (642070) 115 kV Bus a. Apply fault at the SUB-C 7 115.00 (642070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-C 7 (642070) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault85 | 3 Phase fault on SUB-B 7 115.00 (642069) 115 kV Bus a. Apply fault at the SUB-B 7 115.00 (642069) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB-B 7 (642069) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault86 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault87 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to S. 281 7 (641090) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault88 | 3 Phase fault on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault89 | 3 Phase fault on E7THST 7 115.00 (641085) 115 kV Bus a. Apply fault at the E7THST 7 115.00 (641085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYPASS 7 (641082) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. E7THST 9 (641095) 13.8 kV to E7THST 7 (641085) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault90 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault91 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault92 | 3 Phase fault on CAMBRIG7 115.00 (640100) 115 kV Bus a. Apply fault at the CAMBRIG7 115.00 (640100) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAMBRIG7 (640100) 115.0 kV to GOSPER 7 (640194) 115.0 kV Transmission Circuit #1 b.2. CAMBRIG7 (640100) 115.0 kV to MCCOOK 7 (640269) 115.0 kV Transmission Circuit #1 b.3. GOSPER 7 (640194) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault93 | 3 Phase fault on JOHN.LK7 115.00 (640244) 115 kV Bus a. Apply fault at the JOHN.LK7 115.00 (640244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHN.1 7 (640240) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to JOHN.LK7 (640244) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault94 | 3 Phase fault on WESTMIN7 115.00 (640407) 115 kV Bus a. Apply fault at the WESTMIN7 115.00 (640407) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COZAD 7 (640144) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 b.2. JOHN.2 7 (640242) 115.0 kV to WESTMIN7 (640407) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault95 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault96 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault97 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault98 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault99 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault100 | 3 Phase fault on TAMORA 7 115.00 (640375) 115 kV Bus a. Apply fault at the TAMORA 7 115.00 (640375) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEWARD 7 (640340) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault101 | 3 Phase fault on PAWNEEL7 115.00 (640316) 115 kV Bus a. Apply fault at the PAWNEEL7 115.00 (640316) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAWNEEL7 (640316) 115.0 kV to SEWARD 7 (640340) 115.0 kV Transmission Circuit #1 b.2. PAWNEEL7 (640316) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault102 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault103 | 3 Phase fault on SILVRCK7 115.00 (640345) 115 kV Bus a. Apply fault at the SILVRCK7 115.00 (640345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault104 | 3 Phase fault on N.BEND 7 115.00 (640281) 115 kV Bus a. Apply fault at the N.BEND 7 115.00 (640281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to N.BEND 7 (640281) 115.0 kV Transmission Circuit #1 b.2. N.BEND 7 (640281) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault105 | 3 Phase fault on WINSLOW7 115.00 (640409) 115 kV Bus a. Apply fault at the WINSLOW7 115.00 (640409) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREMONT7 (640173) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault106 | 3 Phase fault on W.POINT7 115.00 (640400) 115 kV Bus a. Apply fault at the W.POINT7 115.00 (640400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault107 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault108 | 3 Phase fault on BANCRFT7 115.00 (640070) 115 kV Bus a. Apply fault at the BANCRFT7 115.00 (640070) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault109 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault110 | 3 Phase fault on PETRSBG7 115.00 (640318) 115 kV Bus a. Apply fault at the PETRSBG7 115.00 (640318) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault111 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault112 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault113 | 3 Phase fault on CANADAY4 230.00 (640102) 230 kV Bus a. Apply fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to CANADAY4 (640102) 230.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault114 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault115 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault116 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault117 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault118 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault119 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault120 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault121 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault122 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault123 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault124 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault125 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault126 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault127 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT8 9 (640290) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault128 | 3 Phase fault on N.PLATT4 230.00 (640286) 230 kV Bus a. Apply fault at the N.PLATT4 230.00 (640286) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.PLATT7 (640287) 115.0 kV to N.PLATT4 (640286) 230.0 kV to N.PT9 9 (640291) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault129 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault130 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault131 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault132 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault133 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault134 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault135 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault136 | 3 Phase fault on HASTING4 230.00 (640214) 230 kV Bus a. Apply fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault137 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault138 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALANPPD7 (640304) 115.0 kV to OGALALA4 (640302) 230.0 kV to OGALLALA T19 (643115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault139 | 3 Phase fault on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault140 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault141 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault142 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault143 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault144 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault145 | 3 Phase fault on BELDEN 8 69.000 (640081) 69 kV Bus a. Apply fault at the BELDEN 8 69.000 (640081) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault146 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault147 | 3 Phase fault on BROKENBG 69.000 (640090) 69 kV Bus a. Apply fault at the BROKENBG 69.000 (640090) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault148 | 3 Phase fault on CALAWAY8 69.000 (640099) 69 kV Bus a. Apply fault at the CALAWAY8 69.000 (640099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAWAY8 (640099) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault149 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault150 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault151 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault152 | 3 Phase fault on CREITON8 69.000 (640150) 69 kV Bus a. Apply fault at the CREITON8 69.000 (640150) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault153 | 3 Phase fault on GENEVA 8 69.000 (640179) 69 kV Bus a. Apply fault at the GENEVA 8 69.000 (640179) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault154 | 3 Phase fault on GENOA 7 115.00 (640181) 115 kV Bus a. Apply fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENOA 7 (640181) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault155 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault156 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault157 | 3 Phase fault on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOUPCTY7 (640259) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault158 | 3 Phase fault on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.LOUP 7 (640284) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault159 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault160 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault161 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault162 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault163 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault164 | 3 Phase fault on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETERSBRG.N7 (640444) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault165 | 3 Phase fault on HILDRTH8 69.000 (640223) 69 kV Bus a. Apply fault at the HILDRTH8 69.000 (640223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault166 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault167 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault168 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load #N2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault169 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault170 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault171 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault172 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault173 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault174 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault175 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault176 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault177 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault178 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault179 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault180 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault181 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault182 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault183 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault184 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault185 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault186 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault187 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault188 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault189 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault190 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault191 | 3 Phase fault on S1250 5 161 (646250) 161 kV Bus a. Apply fault at the S1250 5 161 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault192 | 3 Phase fault on S1211 5 161 (646211) 161 kV Bus a. Apply fault at the S1211 5 161 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault193 | 3 Phase fault on S1299 5 161 (646299) 161 kV Bus a. Apply fault at the S1299 5 161 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault194 | 3 Phase fault on S1222 5 161.00 (646222) 161 kV Bus a. Apply fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault195 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault196 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault197 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault198 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault199 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault200 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault201 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault202 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault203 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault204 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault205 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault206 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault207 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault208 | 3 Phase fault on S1256 5 161.0 (646256) 161 kV Bus a. Apply fault at the S1256 5 161.0 (646256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault209 | 3 Phase fault on S1286 5 161.00 (646286) 161 kV Bus a. Apply fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault210 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault211 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault212 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault213 | 3 Phase fault on S1367 5 161.0 (646367) 161 kV Bus a. Apply fault at the S1367 5 161.0 (646367) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault214 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault215 | 3 Phase fault on JCT205 8 69.000 (647105) 69 kV Bus a. Apply fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault216 | 3 Phase fault on S901 8 69.000 (647901) 69 kV Bus a. Apply fault at the S901 8 69.000 (647901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault217 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault218 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault219 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault220 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault221 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault222 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault223 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault224 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault225 | 3 Phase fault on S910 8 69.000 (647910) 69 kV Bus a. Apply fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault226 | 3 Phase fault on S911 8 69.000 (647911) 69 kV Bus a. Apply fault at the S911 8 69.000 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault227 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault228 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault229 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault230 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault231 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault232 | 3 Phase fault on FREM A 8 69.000 (647421) 69 kV Bus a. Apply fault at the FREM A 8 69.000 (647421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM A 8 (647421) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault233 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM C 8 (647423) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault234 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM D 8 (647424) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault235 | 3 Phase fault on FREM B 8 69.000 (647422) 69 kV Bus a. Apply fault at the FREM B 8 69.000 (647422) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREM B 8 (647422) 69.0 kV to FREM G 8 (647427) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault236 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S991 E 8 (647291) 69.0 kV to FREM B 8 (647422) 69.0 kV Transmission Circuit #1 b.2. S991 E 8 (647291) 69.0 kV to S1291 5 (646291) 161.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault237 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault238 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault239 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault240 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault241 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault242 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault243 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault244 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault245 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault246 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault247 | 3 Phase fault on S1210 5 161.00 (646210) 161 kV Bus a. Apply fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault248 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault249 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault250 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault251 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault252 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault253 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T1 9 (643058) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault254 | 3 Phase fault on FREMONT7 115.00 (640173) 115 kV Bus a. Apply fault at the FREMONT7 115.00 (640173) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S976 8 (647976) 69.0 kV to FREMONT7 (640173) 115.0 kV to FREMONT T4 9 (643059) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault255 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault256 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault257 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault258 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault259 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault260 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault261 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault262 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault263 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault264 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault265 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault266 | 3 Phase fault on OGALALA4 230.00 (640302) 230 kV Bus a. Apply fault at the OGALALA4 230.00 (640302) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGALALA4 (640302) 230.0 kV to SIDNEY___TS4 (659134) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault267 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault270 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault271 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault272 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault273 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault274 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault275 | 3 Phase fault on CBLUFFS8 69.000 (635002) 69 kV Bus a. Apply fault at the CBLUFFS8 69.000 (635002) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to SUB701 8 (635004) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault276 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB703 8 (635006) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault277 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB704 8 (635007) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault278 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to HONEYCK8 (635080) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault280 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault281 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault282 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault283 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault286 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault287 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to SC WTRWRKS 8 (635242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault288 | 3 Phase fault on KELLOGG8 69.000 (635222) 69 kV Bus a. Apply fault at the KELLOGG8 69.000 (635222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG8 (635222) 69.0 kV to DIVISON8 (635246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault289 | 3 Phase fault on SBRIDGE T8 69.000 (635227) 69 kV Bus a. Apply fault at the SBRIDGE T8 69.000 (635227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SBRIDGE T8 (635227) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault290 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to SLOAN 8 (635237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault291 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault292 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10215A_-NI8 (659922) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault293 | 3 Phase fault on SALIX 8 69.000 (635236) 69 kV Bus a. Apply fault at the SALIX 8 69.000 (635236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 8 (635236) 69.0 kV to K10225A_-NI8 (659923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault294 | 3 Phase fault on STSTEEL8 69.000 (635240) 69 kV Bus a. Apply fault at the STSTEEL8 69.000 (635240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STSTEEL8 (635240) 69.0 kV to KNOX 8 (635243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault295 | 3 Phase fault on SC WEST8 69.000 (635241) 69 kV Bus a. Apply fault at the SC WEST8 69.000 (635241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SC WEST8 (635241) 69.0 kV to SC WTRWRKS 8 (635242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault296 | 3 Phase fault on DIVISON8 69.000 (635246) 69 kV Bus a. Apply fault at the DIVISON8 69.000 (635246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIVISON8 (635246) 69.0 kV to EASTSID8 (635247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault297 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to JAMES 8 (635248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault298 | 3 Phase fault on EASTSID8 69.000 (635247) 69 kV Bus a. Apply fault at the EASTSID8 69.000 (635247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTSID8 (635247) 69.0 kV to LAWTON8 (635249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault299 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to MAPLTN 8 (635302) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault300 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to SMITHLD8 (635303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault301 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to DANBURY8 (635304) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault302 | 3 Phase fault on MONONA 8 69.000 (635301) 69 kV Bus a. Apply fault at the MONONA 8 69.000 (635301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONONA 8 (635301) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault303 | 3 Phase fault on DANBURY8 69.000 (635304) 69 kV Bus a. Apply fault at the DANBURY8 69.000 (635304) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANBURY8 (635304) 69.0 kV to MAPCO 8 (635305) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault305 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault306 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault307 | 3 Phase fault on ALBION 7 115.00 (640054) 115 kV Bus a. Apply fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault308 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault309 | 3 Phase fault on AURORA_7 115.00 (640063) 115 kV Bus a. Apply fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault310 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault311 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault312 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault313 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault314 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault315 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault316 | 3 Phase fault on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault317 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault318 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault319 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault320 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault321 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault322 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault323 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault324 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault325 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault326 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault327 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault328 | 3 Phase fault on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault329 | 3 Phase fault on CALAWAY7 115.00 (640098) 115 kV Bus a. Apply fault at the CALAWAY7 115.00 (640098) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAWAY7 (640098) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault330 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to ELMCRK_7 (640161) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault331 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault332 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault333 | 3 Phase fault on CANADAY7 115.00 (640103) 115 kV Bus a. Apply fault at the CANADAY7 115.00 (640103) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADAY7 (640103) 115.0 kV to LXNGTN 7 (640256) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault334 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault335 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault336 | 3 Phase fault on CENCITY7 115.00 (640107) 115 kV Bus a. Apply fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault337 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault338 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.DRY7 (640122) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault339 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COL.SE 7 (640124) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault340 | 3 Phase fault on COL.COG7 115.00 (640119) 115 kV Bus a. Apply fault at the COL.COG7 115.00 (640119) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault341 | 3 Phase fault on COL.SE 7 115.00 (640124) 115 kV Bus a. Apply fault at the COL.SE 7 115.00 (640124) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault342 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault343 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault344 | 3 Phase fault on COLMB.E7 115.00 (640127) 115 kV Bus a. Apply fault at the COLMB.E7 115.00 (640127) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault345 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault346 | 3 Phase fault on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault347 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault348 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault349 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault350 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault351 | 3 Phase fault on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault352 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault353 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault354 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault355 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault356 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK_7 (640161) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault357 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault358 | 3 Phase fault on FRIEND 7 115.00 (640174) 115 kV Bus a. Apply fault at the FRIEND 7 115.00 (640174) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault359 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault360 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault361 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault362 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault363 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault364 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault365 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault366 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault367 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault368 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault369 | 3 Phase fault on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault370 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault371 | 3 Phase fault on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault372 | 3 Phase fault on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault373 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault374 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault375 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault376 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault377 | 3 Phase fault on HASTING7 115.00 (640215) 115 kV Bus a. Apply fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault378 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault379 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault380 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault381 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault382 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault383 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault384 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault385 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault386 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault387 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to LOWELL 7 (640261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault388 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV to TOWER 7 (640383) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault389 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LXNGTN 7 (640256) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault390 | 3 Phase fault on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault391 | 3 Phase fault on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault392 | 3 Phase fault on LOWELL 7 115.00 (640261) 115 kV Bus a. Apply fault at the LOWELL 7 115.00 (640261) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOWELL 7 (640261) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault393 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault394 | 3 Phase fault on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault395 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault396 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault397 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault398 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault399 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault195 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault401 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault402 | 3 Phase fault on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault403 | 3 Phase fault on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.LOUP 7 (640284) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault404 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault405 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault406 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault407 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault408 | 3 Phase fault on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault409 | 3 Phase fault on ORD 7 115.00 (640308) 115 kV Bus a. Apply fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORD 7 (640308) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault410 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault411 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault412 | 3 Phase fault on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault413 | 3 Phase fault on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST.LIB 7 (640353) 115.0 kV to ST.PAUL7 (640355) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault414 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault415 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault416 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault417 | 3 Phase fault on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault418 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault419 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH7 (640387) 115.0 kV to S.SIOUXCITY7 (640424) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault420 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault421 | 3 Phase fault on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHERRYC3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault422 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault423 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault424 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault425 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault426 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault427 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault428 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault429 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault430 | 3 Phase fault on SIOUXCY2 230.00 (652552) 230 kV Bus a. Apply fault at the SIOUXCY2 230.00 (652552) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault431 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault432 | 3 Phase fault on K10215A_-NI869.000 (659922) 69 kV Bus a. Apply fault at the K10215A_-NI869.000 (659922) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10215A_-NI8 (659922) 69.0 kV to K144LWTN-NI8 (659979) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault433 | 3 Phase fault on K10225A_-NI869.000 (659923) 69 kV Bus a. Apply fault at the K10225A_-NI869.000 (659923) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K10225A_-NI8 (659923) 69.0 kV to K127WHTG-NI8 (659981) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault434 | 3 Phase fault on K136MAPL-NI869.000 (659989) 69 kV Bus a. Apply fault at the K136MAPL-NI869.000 (659989) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. K136MAPL-NI8 (659989) 69.0 kV to K121MPLM-NI8 (659990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault435 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault436 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault437 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault438 | 3 Phase fault on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLMFLD 8 (640085) 69.0 kV to BLMFLD 7 (640084) 115.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault439 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault440 | 3 Phase fault on BROKENB7 115.00 (640089) 115 kV Bus a. Apply fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROKENBG (640090) 69.0 kV to BROKENB7 (640089) 115.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault441 | 3 Phase fault on CALAWAY7 115.00 (640098) 115 kV Bus a. Apply fault at the CALAWAY7 115.00 (640098) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALAWAY8 (640099) 69.0 kV to CALAWAY7 (640098) 115.0 kV to CALLAWAY T19 (643027) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault442 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault443 | 3 Phase fault on ELMCRK_7 115.00 (640161) 115 kV Bus a. Apply fault at the ELMCRK_7 115.00 (640161) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCRK 8 (640162) 69.0 kV to ELMCRK_7 (640161) 115.0 kV to ELMCREEK T19 (643053) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault444 | 3 Phase fault on EMERSON7 115.00 (640163) 115 kV Bus a. Apply fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMERSONG (640164) 69.0 kV to EMERSON7 (640163) 115.0 kV to EMERSON T1 9 (643054) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault445 | 3 Phase fault on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GENEVA 8 (640179) 69.0 kV to GENEVA 7 (640178) 115.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault446 | 3 Phase fault on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GUIDE R8 (640207) 69.0 kV to GUIDE R7 (640206) 115.0 kV to GUIDEROCKT19 (643073) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault447 | 3 Phase fault on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTGTN8 (640213) 69.0 kV to HARTGTN7 (640212) 115.0 kV to HARTINGTNT19 (643074) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault448 | 3 Phase fault on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILDRTH8 (640223) 69.0 kV to HILDRTH7 (640222) 115.0 kV to HILDRETH T19 (643079) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault449 | 3 Phase fault on LXNGTN 7 115.00 (640256) 115 kV Bus a. Apply fault at the LXNGTN 7 115.00 (640256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEXNGTN8 (640257) 69.0 kV to LXNGTN 7 (640256) 115.0 kV to LEXINGTONT29 (643093) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault450 | 3 Phase fault on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCOOL 8 (640273) 69.0 kV to MCCOOL 7 (640272) 115.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault451 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault452 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault453 | 3 Phase fault on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault454 | 3 Phase fault on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STAPLETON 8 (640360) 69.0 kV to STAPLETON 7 (640359) 115.0 kV to STAPLETONT19 (643175) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault455 | 3 Phase fault on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUTTON 8 (640373) 69.0 kV to SUTTON 7 (640372) 115.0 kV to SUTTON T1 9 (643149) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault456 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T1 9 (643157) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault457 | 3 Phase fault on TWIN CH7 115.00 (640387) 115 kV Bus a. Apply fault at the TWIN CH7 115.00 (640387) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWIN CH8 (640388) 69.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T2 9 (643158) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault458 | 3 Phase fault on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLJCT8 (640415) 69.0 kV to CARLJCT7 (640105) 115.0 kV to CARLTNJCTT29 (643031) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault459 | 3 Phase fault on YORK 7 115.00 (640411) 115 kV Bus a. Apply fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK 8 (640443) 69.0 kV to YORK 7 (640411) 115.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault460 | 3 Phase fault on YORK SW7 115.00 (640413) 115 kV Bus a. Apply fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YORK.SW T2 8 (640447) 69.0 kV to YORK SW7 (640413) 115.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault461 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault462 | 3 Phase fault on ORD 7 115.00 (640308) 115 kV Bus a. Apply fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORD 8 (640475) 69.0 kV to ORD 7 (640308) 115.0 kV to ORD T2 9 (643179) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault463 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault464 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault465 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault466 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault467 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault468 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault469 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault470 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault471 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault472 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault473 | 3 Phase fault on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault474 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault475 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault476 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P1_Fault477 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault1 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault2 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault3 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault4 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault5 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault6 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault7 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault8 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault9 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault10 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault11 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault12 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault14 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault16 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault18 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault19 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault21 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault22 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault23 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault24 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault25 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault26 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault27 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault28 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault29 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault30 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault31 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault32 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault33 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault35 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault36 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault37 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault38 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault40 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault41 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault42 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault43 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault44 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault45 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault46 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault47 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault48 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P1_Fault49 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #z | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault1 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault2 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault3 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault4 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault5 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault6 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault7 | Single Phase Fault with Stuck Breaker on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 b.2. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault8 | Single Phase Fault with Stuck Breaker on BUNGE 5 161.00 (635031) 161 kV Bus a. Apply Fault at the BUNGE 5 161.00 (635031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 b.3. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 b.4. BUNGE 5 (635031) 161.0 kV to HASTING5 (635032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault9 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. SUB701 5 (635003) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault10 | Single Phase Fault with Stuck Breaker on OVRLND 5 161.00 (635015) 161 kV Bus a. Apply Fault at the OVRLND 5 161.00 (635015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault11 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault12 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault13 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault14 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault15 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault16 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.2. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault17 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault18 | Single Phase Fault with Stuck Breaker on RAUN 5 161.00 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault19 | Single Phase Fault with Stuck Breaker on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply Fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 b.2. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault20 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (635226) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (635226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.2. PLYMOTH5 (635223) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault21 | Single Phase Fault with Stuck Breaker on SALIX 5 161.00 (635235) 161 kV Bus a. Apply Fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.3. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault22 | Single Phase Fault with Stuck Breaker on MONONA 5 161.00 (635300) 161 kV Bus a. Apply Fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault23 | Single Phase Fault with Stuck Breaker on CRWFRD 5 161.00 (635330) 161 kV Bus a. Apply Fault at the CRWFRD 5 161.00 (635330) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.2. VICTORY5 (635310) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 b.3. CRWFRD 5 (635330) 161.0 kV to NEWHRVST 9 (635331) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault24 | Single Phase Fault with Stuck Breaker on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply Fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.3. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 b.4. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault25 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.2. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 b.3. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 b.4. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault26 | Single Phase Fault with Stuck Breaker on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply Fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 b.2. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.3. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 b.4. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault27 | Single Phase Fault with Stuck Breaker on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply Fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to MORNSD 5 (635225) 161.0 kV Transmission Circuit #1 b.2. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault28 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 b.3. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.4. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault29 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault30 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault31 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault32 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER5 (652563) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY8 (652574) 69.0 kV Two Winding #1 b.3. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault33 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLYMOTH5 (635223) 161.0 kV to SIOUXCY5 (652566) 161.0 kV Transmission Circuit #1 b.2. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault34 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault35 | Single Phase Fault with Stuck Breaker on SUB-D 7 115.00 (642071) 115 kV Bus a. Apply Fault at the SUB-D 7 115.00 (642071) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DONIPHAN_7 (640159) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault36 | Single Phase Fault with Stuck Breaker on SUB-E 7 115.0 (642072) 115 kV Bus a. Apply Fault at the SUB-E 7 115.0 (642072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.2. SUB-E 7 (642072) 115.0 kV to Load #F0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault37 | Single Phase Fault with Stuck Breaker on SUB-F 7 115.0 (642073) 115 kV Bus a. Apply Fault at the SUB-F 7 115.0 (642073) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to SUB-F 7 (642073) 115.0 kV Transmission Circuit #1 b.2. SUB-F 7 (642073) 115.0 kV to Load #F0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault38 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to EGY CTRG (641086) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault39 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.6. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.7. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 b.9. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault40 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. HOSK.T89 (640230) 34.5 kV to HOSKINS4 (640227) 230.0 kV Two Winding #1 b.3. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.4. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault41 | Single Phase Fault with Stuck Breaker on COLMB.W4 230.00 (640131) 230 kV Bus a. Apply Fault at the COLMB.W4 230.00 (640131) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.3. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT19 (643039) 13.8 kV Three Winding #1 b.4. COLMB.W4 (640131) 230.0 kV to COLMB.W9 (640132) 34.5 kV to COLMB.WSTT29 (643040) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault42 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. COLMB.W4 (640131) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.3. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.4. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.5. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault43 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.4. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault44 | Single Phase Fault with Stuck Breaker on AINSWND7 115.00 (640050) 115 kV Bus a. Apply Fault at the AINSWND7 115.00 (640050) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AINSWND7 (640050) 115.0 kV to AINSWND.PLTD (640025) 34.5 kV Two Winding #1 b.2. AINSWND7 (640050) 115.0 kV to AINSWRT7 (640051) 115.0 kV Transmission Circuit #1 b.3. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault45 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to FULERTN7 (640176) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.4. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.5. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T1 9 (643004) 13.8 kV Three Winding #1 b.6. ALBION 7 (640054) 115.0 kV to ALBION 9 (640055) 34.5 kV to ALBION T2 9 (643005) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault46 | Single Phase Fault with Stuck Breaker on AURORA_7 115.00 (640063) 115 kV Bus a. Apply Fault at the AURORA_7 115.00 (640063) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. AURORA_7 (640063) 115.0 kV to AURORA 9 (640064) 34.5 kV to AURORA T1 9 (643008) 13.8 kV Three Winding #1 b.4. AURORA_7 (640063) 115.0 kV to AURORA_8 (640416) 69.0 kV to AURORA T2 9 (643009) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault47 | Single Phase Fault with Stuck Breaker on BEEMER 7 115.00 (640078) 115 kV Bus a. Apply Fault at the BEEMER 7 115.00 (640078) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. BEEMER 7 (640078) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.3. BEEMER 7 (640078) 115.0 kV to BEEMER G (640079) 34.5 kV to BEEMER T1 9 (643015) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault48 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.3. BELDEN 7 (640080) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.4. BELDEN 7 (640080) 115.0 kV to BELDEN 8 (640081) 69.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault49 | Single Phase Fault with Stuck Breaker on BROKENB7 115.00 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 b.2. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 b.3. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.4. BROKENB7 (640089) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 b.5. BROKENB7 (640089) 115.0 kV to BROKENBG (640090) 69.0 kV to BROKENBOWT19 (643023) 13.8 kV Three Winding #1 b.6. BROKENB7 (640089) 115.0 kV to BROKENBG (640090) 69.0 kV to BROKENBOWT29 (643024) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault50 | Single Phase Fault with Stuck Breaker on CALAWAY7 115.00 (640098) 115 kV Bus a. Apply Fault at the CALAWAY7 115.00 (640098) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 b.2. CALAWAY7 (640098) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 b.3. CALAWAY7 (640098) 115.0 kV to CALAWAY8 (640099) 69.0 kV to CALLAWAY T19 (643027) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault51 | Single Phase Fault with Stuck Breaker on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply Fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.3. CARLJCT7 (640105) 115.0 kV to CARLJCT9 (640106) 34.5 kV to CARLTNJCTT19 (643030) 13.8 kV Three Winding #1 b.4. CARLJCT7 (640105) 115.0 kV to CARLJCT8 (640415) 69.0 kV to CARLTNJCTT29 (643031) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault52 | Single Phase Fault with Stuck Breaker on CENCITY7 115.00 (640107) 115 kV Bus a. Apply Fault at the CENCITY7 115.00 (640107) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.3. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT19 (643032) 13.8 kV Three Winding #1 b.4. CENCITY7 (640107) 115.0 kV to CENCITY9 (640108) 34.5 kV to CENTRLCTYT29 (643033) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault53 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.3. CREITON7 (640149) 115.0 kV to CREITON8 (640150) 69.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault54 | Single Phase Fault with Stuck Breaker on CRESTON7 115.00 (640151) 115 kV Bus a. Apply Fault at the CRESTON7 115.00 (640151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.2. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.3. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T1 9 (643046) 4.2 kV Three Winding #1 b.4. CRESTON7 (640151) 115.0 kV to CRESTON9 (640152) 34.5 kV to CRESTON T2 9 (643047) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault55 | Single Phase Fault with Stuck Breaker on CRETE__7 115.00 (640153) 115 kV Bus a. Apply Fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRETE__7 (640153) 115.0 kV to FRIEND 7 (640174) 115.0 kV Transmission Circuit #1 b.2. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 b.3. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T1 9 (643048) 13.8 kV Three Winding #1 b.4. CRETE__7 (640153) 115.0 kV to CRETE G (640154) 34.5 kV to CRETE T2 9 (643049) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault56 | Single Phase Fault with Stuck Breaker on EMERSON7 115.00 (640163) 115 kV Bus a. Apply Fault at the EMERSON7 115.00 (640163) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to EMERSON7 (640163) 115.0 kV Transmission Circuit #1 b.2. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.3. EMERSON7 (640163) 115.0 kV to EMERSONG (640164) 69.0 kV to EMERSON T1 9 (643054) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault57 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.2. FRIEND 7 (640174) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 b.3. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.4. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.5. GENEVA 7 (640178) 115.0 kV to GENEVA 8 (640179) 69.0 kV to GENEVA T2 9 (643062) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault58 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.2. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.3. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T1 9 (643064) 13.8 kV Three Winding #1 b.4. GENOA 7 (640181) 115.0 kV to GENOA G (640182) 34.5 kV to GENOA T2 9 (643065) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault59 | Single Phase Fault with Stuck Breaker on HEBRN N7 115.00 (640218) 115 kV Bus a. Apply Fault at the HEBRN N7 115.00 (640218) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.2. FAIRBRY7 (640169) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.3. HEBRN N7 (640218) 115.0 kV to HEBRON G (640012) 13.8 kV Two Winding #1 b.4. HEBRN N7 (640218) 115.0 kV to HEBRON 7 (640220) 115.0 kV Transmission Circuit #1 b.5. HEBRON G (640012) Machine #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault60 | Single Phase Fault with Stuck Breaker on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.2. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.3. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. LOUPCTY7 (640259) 115.0 kV to LOUPCTY9 (640260) 34.5 kV to LOUP CITYT19 (643095) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault61 | Single Phase Fault with Stuck Breaker on MAXWELS7 115.00 (640267) 115 kV Bus a. Apply Fault at the MAXWELS7 115.00 (640267) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAWAY7 (640098) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 b.2. MAXWELS7 (640267) 115.0 kV to N.PLATT7 (640287) 115.0 kV Transmission Circuit #1 b.3. MAXWELS7 (640267) 115.0 kV to STAPLETON 7 (640359) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault62 | Single Phase Fault with Stuck Breaker on MCCOOL 7 115.00 (640272) 115 kV Bus a. Apply Fault at the MCCOOL 7 115.00 (640272) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.4. MCCOOL 7 (640272) 115.0 kV to MCCOOL 8 (640273) 69.0 kV to MCCOOL T1 9 (643171) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault63 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.3. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.4. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.5. NELIGH 7 (640293) 115.0 kV to NELIGH 8 (640294) 69.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 b.6. NELIGH 7 (640293) 115.0 kV to NELIGH 9 (640295) 34.5 kV to NELIGH T1 9 (643109) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault64 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T1 9 (643112) 13.8 kV Three Winding #1 b.5. NORFOLK7 (640298) 115.0 kV to NORFOLK9 (640299) 34.5 kV to NORFOLK T2 9 (643113) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault65 | Single Phase Fault with Stuck Breaker on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply Fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT19 (643110) 13.8 kV Three Winding #1 b.5. NORFK.N7 (640296) 115.0 kV to NORFK.N9 (640297) 34.5 kV to NORFOLK.NT29 (643111) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault66 | Single Phase Fault with Stuck Breaker on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply Fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.2. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 b.3. N.LOUP 7 (640284) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.4. N.LOUP 7 (640284) 115.0 kV to N.LOUP 9 (640285) 34.5 kV to NORTHLOUPT19 (643105) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault67 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BANCRFT7 (640070) 115.0 kV to OAKLAND7 (640300) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.3. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 b.4. OAKLAND7 (640300) 115.0 kV to WINSLOW7 (640409) 115.0 kV Transmission Circuit #1 b.5. OAKLAND7 (640300) 115.0 kV to OAKLAND9 (640301) 34.5 kV to OAKLAND T1 9 (643114) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault68 | Single Phase Fault with Stuck Breaker on PAULINE7 115.00 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.4. PAULINE7 (640313) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.5. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.6. PAULINE7 (640313) 115.0 kV to PAULINE8 (640314) 69.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault69 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to SPALDNG7 (640347) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.3. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T19 (643139) 13.8 kV Three Winding #1 b.4. SPALDNG7 (640347) 115.0 kV to SPALDNG9 (640348) 34.5 kV to SPALDING T29 (643169) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault70 | Single Phase Fault with Stuck Breaker on STNTN.N7 115.00 (640363) 115 kV Bus a. Apply Fault at the STNTN.N7 115.00 (640363) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.3. STNTN.N7 (640363) 115.0 kV to STNTN.N9 (640364) 34.5 kV to STANTN.N T19 (643145) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault71 | Single Phase Fault with Stuck Breaker on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply Fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 b.2. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.3. SUTTON 7 (640372) 115.0 kV to SUTTON 8 (640373) 69.0 kV to SUTTON T1 9 (643149) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault72 | Single Phase Fault with Stuck Breaker on TEKAMAH7 115.00 (640378) 115 kV Bus a. Apply Fault at the TEKAMAH7 115.00 (640378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH9 (640379) 34.5 kV to TEKAMAH T2 9 (643152) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault73 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.3. THEDFRD7 (640381) 115.0 kV to THEDFRD9 (640382) 34.5 kV to THEDFORD T19 (643153) 13.8 kV Three Winding #1 b.4. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault74 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.2. TAMORA 7 (640375) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 b.3. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.4. YORK 7 (640411) 115.0 kV to YORK 9 (640412) 34.5 kV to YORK T1 9 (643166) 13.8 kV Three Winding #1 b.5. YORK 7 (640411) 115.0 kV to YORK 8 (640443) 69.0 kV to YORK T2 9 (643167) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault75 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.3. YORK SW7 (640413) 115.0 kV to YORK SW9 (640414) 34.5 kV to YORK.SW T1 9 (643168) 13.8 kV Three Winding #1 b.4. YORK SW7 (640413) 115.0 kV to YORK.SW T2 8 (640447) 69.0 kV to YORK.SW T2 9 (643176) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault76 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault77 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault78 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault79 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to BEATRCE7 (640076) 115.0 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.4. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.7. BEATRCE9 (640077) 34.5 kV to Load #NW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault80 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEATRCE9 (640077) 34.5 kV to BEATRCE7 (640076) 115.0 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 b.4. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE9 (640077) 34.5 kV to Load #NW | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault81 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.COG7 (640119) 115.0 kV to COLMB.E7 (640127) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault82 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.2. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.3. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.5. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault83 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault84 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.4. HOSKINS9 (640229) 34.5 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.7. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.8. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.9. HOSKINS9 (640229) 34.5 kV to Load #N2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault85 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS9 (640229) 34.5 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 b.4. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.8. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.9. HOSKINS9 (640229) 34.5 kV to Load #N2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault86 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault87 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.2. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.3. PETERSBRG.N7 (640444) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault88 | Single Phase Fault with Stuck Breaker on BEATRCE7 115.00 (640076) 115 kV Bus a. Apply Fault at the BEATRCE7 115.00 (640076) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEAT. S7 (640074) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 b.2. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.3. BEATRCE7 (640076) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #2 b.4. BEATRCE7 (640076) 115.0 kV to HARBINE7 (640208) 115.0 kV Transmission Circuit #1 b.5. BEATRCE7 (640076) 115.0 kV to STEINER7 (640361) 115.0 kV Transmission Circuit #1 b.6. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T19 (643013) 13.8 kV Three Winding #1 b.7. BEATRCE7 (640076) 115.0 kV to BEATRCE9 (640077) 34.5 kV to BEATRICE T29 (643014) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault89 | Single Phase Fault with Stuck Breaker on BLMFLD 7 115.00 (640084) 115 kV Bus a. Apply Fault at the BLMFLD 7 115.00 (640084) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 b.2. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. ELKRDG.PLT D (640419) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.4. CROFTN.PLT D (640423) 34.5 kV to BLMFLD 7 (640084) 115.0 kV Two Winding #1 b.5. BLMFLD 7 (640084) 115.0 kV to BLMFLD 8 (640085) 69.0 kV to BLOMFIELDT19 (643019) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault90 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS7 (640136) 115.0 kV to COLMBS1G (640006) 13.8 kV Two Winding #1 b.2. COLMBUS7 (640136) 115.0 kV to COLMBS2G (640007) 13.8 kV Two Winding #1 b.3. COLMBUS7 (640136) 115.0 kV to CRESTON7 (640151) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to SCHUYLR7 (640336) 115.0 kV Transmission Circuit #1 b.5. COLMBUS9 (640137) 34.5 kV to COLMBUS7 (640136) 115.0 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.9. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.10. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.11. COLMBUS7 (640136) 115.0 kV to Switched Shunt Device # b.12. COLMBUS9 (640137) 34.5 kV to Load #N0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault91 | Single Phase Fault with Stuck Breaker on COLMBUS7 115.00 (640136) 115 kV Bus a. Apply Fault at the COLMBUS7 115.00 (640136) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL.SE 7 (640124) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.3. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.4. COLMBUS7 (640136) 115.0 kV to COLMBS3G (640008) 13.8 kV Two Winding #1 b.5. COLMBUS7 (640136) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 b.6. COLMBUS7 (640136) 115.0 kV to SILVRCK7 (640345) 115.0 kV Transmission Circuit #1 b.7. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T59 (643041) 13.8 kV Three Winding #1 b.8. COLMBUS7 (640136) 115.0 kV to COLMBUS9 (640137) 34.5 kV to COLUMBUS T69 (643042) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault92 | Single Phase Fault with Stuck Breaker on GR ISLD7 115.00 (640201) 115 kV Bus a. Apply Fault at the GR ISLD7 115.00 (640201) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AURORA_7 (640063) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. CENCITY7 (640107) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.3. GR ISLD7 (640201) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 b.4. GR ISLD7 (640201) 115.0 kV to SUB-D 7 (642071) 115.0 kV Transmission Circuit #1 b.5. GR ISLD7 (640201) 115.0 kV to SUB-E 7 (642072) 115.0 kV Transmission Circuit #1 b.6. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.7. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.8. GR ISLD7 (640201) 115.0 kV to GR ISLD9 (640202) 34.5 kV to GR ISLD T1 9 (643072) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault93 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG9 (640225) 34.5 kV to Load #N0 b.2. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.3. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 b.4. HOLDREG7 (640224) 115.0 kV to HOLDREG9 (640225) 34.5 kV to HOLDREDGET19 (643080) 13.8 kV Three Winding #1 b.5. HOLDREG7 (640224) 115.0 kV to HOLDREGE 8 (640448) 69.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 b.10. HOLDREG7 (640224) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault94 | Single Phase Fault with Stuck Breaker on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.4. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.5. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.6. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.7. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T3 9 (643085) 13.8 kV Three Winding #1 b.8. HOSKINS7 (640228) 115.0 kV to HOSKINS9 (640229) 34.5 kV to HOSKINS T6 9 (643086) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault95 | Single Phase Fault with Stuck Breaker on PETERSBRG.N7115.00 (640444) 115 kV Bus a. Apply Fault at the PETERSBRG.N7115.00 (640444) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 b.2. PETRSBG7 (640318) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #z1 b.3. LAREDO.PLT 9 (640433) 34.5 kV to PETERSBRG.N7 (640444) 115.0 kV Two Winding #1 b.4. PETERSBRG.N7 (640444) 115.0 kV to WHTHRSX9 (648503) 34.5 kV to WHTHRSY9 (648504) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault96 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to Load #O0 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.3. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault97 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to Load #O0 b.2. S1210 5 (646210) 161.0 kV to Load #O0 b.3. S1217 5 (646217) 161.0 kV to Load #O0 b.4. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.5. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.7. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault98 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault99 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault100 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault101 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault102 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault103 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.4. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault104 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault105 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault106 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault107 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault108 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault109 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault110 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault111 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault112 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault113 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault114 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.2. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault115 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault116 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to Load #O0 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault117 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault118 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault119 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.3. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault120 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211T39 (645127) 13.8 kV to Load #S4 b.2. S1211 5 (646211) 161.0 kV to S1211T39 (645127) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault121 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault122 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault123 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.4. NO4 AUX9 (645124) 2.4 kV to Load #S1 b.5. S1299 5 (646299) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault124 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.4. NO5 AUX9 (645125) 4.2 kV to Load #S1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault125 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1211T49 (645128) 13.8 kV Two Winding #1 b.3. S1211T39 (645127) 13.8 kV to Load #S4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault126 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1216 5 (646216) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault127 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.7. S1216 5 (646216) 161.0 kV to Load #O0 b.8. S1217 5 (646217) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault128 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.7. S1216 5 (646216) 161.0 kV to Load #O0 b.8. S1210 5 (646210) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault129 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.7. S1217 5 (646217) 161.0 kV to Load #O0 b.8. S1210 5 (646210) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault130 | Single Phase Fault with Stuck Breaker on S1220 5 161.00 (646220) 161 kV Bus a. Apply Fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault131 | Single Phase Fault with Stuck Breaker on S1222 5 161.00 (646222) 161 kV Bus a. Apply Fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault132 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault133 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault134 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault135 | Single Phase Fault with Stuck Breaker on S1229 5 161.00 (646229) 161 kV Bus a. Apply Fault at the S1229 5 161.00 (646229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault136 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault137 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault138 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault139 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault140 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault141 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault142 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1211 5 (646211) 161.0 kV to Load #O0 b.4. S1250 5 (646250) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault143 | Single Phase Fault with Stuck Breaker on S1250 5 161.0 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.0 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault144 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1341 5 (646341) 161.0 kV to Load #O0 b.2. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.3. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault145 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault146 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FC1A 5 (645100) 161.0 kV to FC1A3 9 (645103) 4.2 kV Two Winding #1 b.2. FC1A 5 (645100) 161.0 kV to FC1A4 9 (645104) 4.2 kV Two Winding #1 b.3. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 b.4. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.5. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.6. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault147 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault148 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault149 | Single Phase Fault with Stuck Breaker on S1286 5 161.00 (646286) 161 kV Bus a. Apply Fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault150 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault151 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load #O0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault152 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault153 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 b.2. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault154 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault155 | Single Phase Fault with Stuck Breaker on S1291 5 161.00 (646291) 161 kV Bus a. Apply Fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault156 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault157 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault158 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault159 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.4. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.5. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault160 | Single Phase Fault with Stuck Breaker on GAVINS 7 115.00 (652511) 115 kV Bus a. Apply Fault at the GAVINS 7 115.00 (652511) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLMFLD 7 (640084) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.2. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.3. GAVINS 7 (652511) 115.0 kV to GAVINS1G (652575) 13.2 kV Two Winding #1 b.4. GAVINS 7 (652511) 115.0 kV to GAVINS2G (652576) 13.2 kV Two Winding #1 b.5. GAVINS 7 (652511) 115.0 kV to GAVINS3G (652577) 13.2 kV Two Winding #1 b.6. GAVINS 7 (652511) 115.0 kV to SPIRIT_M-BE7 (659121) 115.0 kV Transmission Circuit #1 b.7. GAVINS 7 (652511) 115.0 kV to YANKTON JCT7 (660006) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault161 | Single Phase Fault with Stuck Breaker on DENISON4 230.00 (652567) 230 kV Bus a. Apply Fault at the DENISON4 230.00 (652567) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.2. DENISON4 (652567) 230.0 kV to DENISON8 (652583) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault162 | Single Phase Fault with Stuck Breaker on EAGLE___-NI4230.00 (659900) 230 kV Bus a. Apply Fault at the EAGLE___-NI4230.00 (659900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.2. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.3. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #1 b.4. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #2 b.5. EAGLE___-NI4 (659900) 230.0 kV to EAGLE___-NI8 (659901) 69.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault163 | Single Phase Fault with Stuck Breaker on RASMUSN-ER4 230.00 (655484) 230 kV Bus a. Apply Fault at the RASMUSN-ER4 230.00 (655484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.3. RASMUSN-ER4 (655484) 230.0 kV to RASMUSN-ER8 (655485) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault164 | Single Phase Fault with Stuck Breaker on CLEVELND-LO4230.00 (659735) 230 kV Bus a. Apply Fault at the CLEVELND-LO4230.00 (659735) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.2. ROCKRPDMUNI8 (658122) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.3. PAHOJA__-BE4 (659311) 230.0 kV to CLEVELND-LO4 (659735) 230.0 kV Transmission Circuit #1 b.4. PAHOJA__-BE4 (659311) 230.0 kV to EAGLE___-NI4 (659900) 230.0 kV Transmission Circuit #1 b.5. RKRPDTAP-LO8 (659714) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.6. LESTERSS-LO8 (659722) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.7. STEEN -LO8 (659726) 69.0 kV to CLEVELND-LO8 (659736) 69.0 kV Transmission Circuit #1 b.8. CLEVELND-LO4 (659735) 230.0 kV to CLEVELND-LO8 (659736) 69.0 kV to CLEVELND-LO9 (659737) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault165 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault195 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault167 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault302 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault169 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.0 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.0 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load #M0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault170 | Single Phase Fault with Stuck Breaker on 6815TP38 69.000 (647016) 69 kV Bus a. Apply Fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault171 | Single Phase Fault with Stuck Breaker on 6815TP98 69.000 (647017) 69 kV Bus a. Apply Fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.6. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.8. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault172 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.4. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.5. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault173 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault174 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault175 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault176 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault177 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault178 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault179 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault180 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault181 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault182 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault183 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault184 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault185 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault186 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault187 | Single Phase Fault with Stuck Breaker on 20PIONEERS7 115.00 (650238) 115 kV Bus a. Apply Fault at the 20PIONEERS7 115.00 (650238) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2&N 7 (650230) 115.0 kV to 20PIONEERS7 (650238) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault188 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault189 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 20PIONEERS7 (650238) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault190 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault191 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault192 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. ROKEBY 7 (650290) 115.0 kV to ROKEBY 2G (650092) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault193 | Single Phase Fault with Stuck Breaker on ROKEBY 7 115.00 (650290) 115 kV Bus a. Apply Fault at the ROKEBY 7 115.00 (650290) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27&PLR 7 (650229) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault194 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault302 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault196 | Single Phase Fault with Stuck Breaker on FOLSM&PHIL7 115.00 (650242) 115 kV Bus a. Apply Fault at the FOLSM&PHIL7 115.00 (650242) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. FOLSM&PHIL7 (650242) 115.0 kV to ROKEBY 7 (650290) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault197 | Single Phase Fault with Stuck Breaker on 76&ROKEBY 7 115.00 (650276) 115 kV Bus a. Apply Fault at the 76&ROKEBY 7 115.00 (650276) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.3. 91&HWY2 7 (650274) 115.0 kV to 76&ROKEBY 7 (650276) 115.0 kV Transmission Circuit #1 b.4. 76&ROKEBY 7 (650276) 115.0 kV to 76&ROKEBY 9 (650376) 12.5 kV to 761TERTIARY (650576) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault198 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault199 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOLSM&PHIL7 (650242) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault200 | Single Phase Fault with Stuck Breaker on SW7&BENNET7 115.00 (650246) 115 kV Bus a. Apply Fault at the SW7&BENNET7 115.00 (650246) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault201 | Single Phase Fault with Stuck Breaker on 40&BENNET 7 115.00 (650247) 115 kV Bus a. Apply Fault at the 40&BENNET 7 115.00 (650247) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SW7&BENNET7 (650246) 115.0 kV to 40&BENNET 7 (650247) 115.0 kV Transmission Circuit #1 b.2. 40&BENNET 7 (650247) 115.0 kV to 40&ROKEBY 7 (650250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault202 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.2. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.3. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.5. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault203 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault204 | Single Phase Fault with Stuck Breaker on EGYCNTR7 115.00 (641087) 115 kV Bus a. Apply Fault at the EGYCNTR7 115.00 (641087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. EGYCNTR7 (641087) 115.0 kV to EGYCTR2G (641089) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault205 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault206 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault207 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault208 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault209 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault210 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault211 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault212 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault213 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault214 | Single Phase Fault with Stuck Breaker on C.CREEK4 230.00 (640093) 230 kV Bus a. Apply Fault at the C.CREEK4 230.00 (640093) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to C.CREEK7 (640094) 115.0 kV to CRKDCREEKT19 (643026) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault215 | Single Phase Fault with Stuck Breaker on CANADAY4 230.00 (640102) 230 kV Bus a. Apply Fault at the CANADAY4 230.00 (640102) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. C.CREEK4 (640093) 230.0 kV to CANADAY4 (640102) 230.0 kV Transmission Circuit #1 b.2. C.CREEK4 (640093) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. CANADAY4 (640102) 230.0 kV to CANADAY7 (640103) 115.0 kV to CANADAY T4 9 (643029) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault216 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault217 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault218 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault219 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to RIVERDL4 (640330) 230.0 kV Transmission Circuit #1 b.3. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault220 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to HASTING4 (640214) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 b.4. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault221 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault222 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault223 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault224 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault225 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault226 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault227 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault228 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault229 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault230 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault231 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault232 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault233 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault234 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault235 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault236 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault237 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.3. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault238 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMERSON7 (640163) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to TWIN CH7 (640387) 115.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault239 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault240 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault241 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.5. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault242 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault243 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault244 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault245 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.2. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.3. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 b.4. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.5. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.6. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault246 | Single Phase Fault with Stuck Breaker on S985 8 69.000 (647985) 69 kV Bus a. Apply Fault at the S985 8 69.000 (647985) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTSMTH8 (640320) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.2. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.3. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault247 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.5. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault248 | Single Phase Fault with Stuck Breaker on 6815TP38 69.000 (647016) 69 kV Bus a. Apply Fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.8. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.9. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault249 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault250 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 b.2. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.6. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault251 | Single Phase Fault with Stuck Breaker on S912 8 69.000 (647912) 69 kV Bus a. Apply Fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault252 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault253 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.5. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault254 | Single Phase Fault with Stuck Breaker on S923 8 69.000 (647923) 69 kV Bus a. Apply Fault at the S923 8 69.000 (647923) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 b.3. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault255 | Single Phase Fault with Stuck Breaker on S924 8 69.000 (647924) 69 kV Bus a. Apply Fault at the S924 8 69.000 (647924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault256 | Single Phase Fault with Stuck Breaker on S928 8 69.000 (647928) 69 kV Bus a. Apply Fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault257 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T3 8 (647815) 69.0 kV to Load #O0 b.2. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.3. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.6. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault258 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.5. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.9. S906 N 8 (647006) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault259 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.3. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.4. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault260 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6815T1&T2 8 (647015) 69.0 kV to Load #O0 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.4. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.5. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.9. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault261 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.4. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.5. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.6. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.7. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault262 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault263 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault264 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to J748POI (87487) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault265 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault266 | Single Phase Fault with Stuck Breaker on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply Fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #2 b.2. BPS SUB7 (640088) 115.0 kV to BEATRCE7 (640076) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault267 | Single Phase Fault with Stuck Breaker on CLATONA7 115.00 (640111) 115 kV Bus a. Apply Fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLATONA7 (640111) 115.0 kV to BPS SUB7 (640088) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault268 | Single Phase Fault with Stuck Breaker on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply Fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault269 | Single Phase Fault with Stuck Breaker on GUIDE R7 115.00 (640206) 115 kV Bus a. Apply Fault at the GUIDE R7 115.00 (640206) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GUIDE R7 (640206) 115.0 kV to ROSEMONT 7 (640583) 115.0 kV Transmission Circuit #1 b.2. GUIDE R7 (640206) 115.0 kV to SUPEROR7 (640368) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault270 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault271 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault272 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault273 | Single Phase Fault with Stuck Breaker on ORD 7 115.00 (640308) 115 kV Bus a. Apply Fault at the ORD 7 115.00 (640308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORD 7 (640308) 115.0 kV to MUDDY CREEK7 (640455) 115.0 kV Transmission Circuit #1 b.2. ORD 7 (640308) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault274 | Single Phase Fault with Stuck Breaker on ST.LIB 7 115.00 (640353) 115 kV Bus a. Apply Fault at the ST.LIB 7 115.00 (640353) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to GR ISLD7 (640201) 115.0 kV Transmission Circuit #1 b.2. ST.LIB 7 (640353) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault275 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T4 9 (643155) 13.8 kV Three Winding #1 b.2. TWIN CH7 (640387) 115.0 kV to TWIN CH4 (640386) 230.0 kV to TWIN CH T6 9 (643156) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault276 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERRYC3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. CHERRYC3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault277 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault278 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault279 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to RTLSNAKE.W 4 (640561) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault280 | Single Phase Fault with Stuck Breaker on ROSEMONT 7115.00 (640583) 115 kV Bus a. Apply Fault at the ROSEMONT 7115.00 (640583) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEMONT 7 (640583) 115.0 kV to GUIDE R7 (640206) 115.0 kV Transmission Circuit #1 b.2. ROSEMONT 7 (640583) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault281 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault282 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault283 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault284 | Single Phase Fault with Stuck Breaker on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #2 b.2. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault285 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault286 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault287 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault288 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.2. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T5 9 (643070) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault289 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault290 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault291 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 7 (640272) 115.0 kV to MCCOOL 3 (640271) 345.0 kV to MCCOOL19 (640274) 13.8 kV Three Winding #1 b.2. MCCOOL 7 (640272) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault292 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 b.2. PAULINE7 (640313) 115.0 kV to HILDRTH7 (640222) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault293 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 b.2. RIVERDL7 (640331) 115.0 kV to RIVERDL4 (640330) 230.0 kV to RIVERDALET39 (643184) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault294 | Single Phase Fault with Stuck Breaker on CHERRYC3 345.00 (640500) 345 kV Bus a. Apply Fault at the CHERRYC3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to CHERRYC3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault295 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault296 | Single Phase Fault with Stuck Breaker on HASTCTY7 115.00 (641088) 115 kV Bus a. Apply Fault at the HASTCTY7 115.00 (641088) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTCTY7 (641088) 115.0 kV to E7THST 7 (641085) 115.0 kV Transmission Circuit #1 b.2. HASTCTY7 (641088) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault297 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S3456 3 (645456) 345.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault298 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault299 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault300 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault301 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY4 (652565) 230.0 kV to SIOUXCY2 (652552) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Transfer | GROUP2_LOCAL_P4_Fault360 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault303 | Single Phase Fault with Stuck Breaker on ALBION 7 115.00 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 115.00 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to PETRSBG7 (640318) 115.0 kV Transmission Circuit #1 b.2. ALBION 7 (640054) 115.0 kV to GENOA 7 (640181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault304 | Single Phase Fault with Stuck Breaker on BROKENB7 115.00 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 115.00 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to C.CREEK7 (640094) 115.0 kV Transmission Circuit #1 b.2. BROKENB7 (640089) 115.0 kV to CALAWAY7 (640098) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault305 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault306 | Single Phase Fault with Stuck Breaker on GENOA 7 115.00 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 115.00 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. GENOA 7 (640181) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault307 | Single Phase Fault with Stuck Breaker on LOUPCTY7 115.00 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 115.00 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to N.LOUP 7 (640284) 115.0 kV Transmission Circuit #1 b.2. LOUPCTY7 (640259) 115.0 kV to ST.LIB 7 (640353) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault308 | Single Phase Fault with Stuck Breaker on N.LOUP 7 115.00 (640284) 115 kV Bus a. Apply Fault at the N.LOUP 7 115.00 (640284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.LOUP 7 (640284) 115.0 kV to LOUPCTY7 (640259) 115.0 kV Transmission Circuit #1 b.2. N.LOUP 7 (640284) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault309 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault310 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault311 | Single Phase Fault with Stuck Breaker on OAKLAND7 115.00 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 115.00 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to TEKAMAH7 (640378) 115.0 kV Transmission Circuit #1 b.2. OAKLAND7 (640300) 115.0 kV to W.POINT7 (640400) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault312 | Single Phase Fault with Stuck Breaker on SPALDNG7 115.00 (640347) 115 kV Bus a. Apply Fault at the SPALDNG7 115.00 (640347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPALDNG7 (640347) 115.0 kV to G17-234-TAP (761695) 115.0 kV Transmission Circuit #1 b.2. SPALDNG7 (640347) 115.0 kV to ALBION 7 (640054) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault313 | Single Phase Fault with Stuck Breaker on YORK 7 115.00 (640411) 115 kV Bus a. Apply Fault at the YORK 7 115.00 (640411) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YORK 7 (640411) 115.0 kV to YORK SW7 (640413) 115.0 kV Transmission Circuit #1 b.2. YORK 7 (640411) 115.0 kV to TAMORA 7 (640375) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault314 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault315 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault316 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARD AVE 3 (635219) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault317 | Single Phase Fault with Stuck Breaker on KNOX 8 69.000 (635243) 69 kV Bus a. Apply Fault at the KNOX 8 69.000 (635243) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOX 8 (635243) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 b.2. KNOX 8 (635243) 69.0 kV to STSTEEL8 (635240) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault318 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLND 3 (635400) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. HIGHLND 3 (635400) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault319 | Single Phase Fault with Stuck Breaker on MUDDY CREEK7115.00 (640455) 115 kV Bus a. Apply Fault at the MUDDY CREEK7115.00 (640455) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUDDY CREEK7 (640455) 115.0 kV to ORD 7 (640308) 115.0 kV Transmission Circuit #1 b.2. MUDDY CREEK7 (640455) 115.0 kV to BROKENB7 (640089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault320 | Single Phase Fault with Stuck Breaker on S.SIOUXCITY7115.00 (640424) 115 kV Bus a. Apply Fault at the S.SIOUXCITY7115.00 (640424) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.SIOUXCITY7 (640424) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #1 b.2. S.SIOUXCITY7 (640424) 115.0 kV to TWIN CH7 (640387) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault321 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault322 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault323 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault324 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault325 | Single Phase Fault with Stuck Breaker on GRPR2 3 345.00 (648520) 345 kV Bus a. Apply Fault at the GRPR2 3 345.00 (648520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR2 3 (648520) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #1 b.2. GRPR2 3 (648520) 345.0 kV to GRPR21X9 (648521) 34.5 kV to GRPR21Y9 (648522) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault326 | Single Phase Fault with Stuck Breaker on GRPR_DMY_BUS345.00 (648527) 345 kV Bus a. Apply Fault at the GRPR_DMY_BUS345.00 (648527) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPR_DMY_BUS (648527) 345.0 kV to GRPR1 3 (648513) 345.0 kV Transmission Circuit #z1 b.2. GRPR_DMY_BUS (648527) 345.0 kV to GRPR12X9 (648517) 34.5 kV to GRPR12Y9 (648518) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault327 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault328 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault329 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault330 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault331 | Single Phase Fault with Stuck Breaker on GENEVA 7 115.00 (640178) 115 kV Bus a. Apply Fault at the GENEVA 7 115.00 (640178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENEVA 7 (640178) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. GENEVA 7 (640178) 115.0 kV to SUTTON 7 (640372) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault332 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault333 | Single Phase Fault with Stuck Breaker on HARTGTN7 115.00 (640212) 115 kV Bus a. Apply Fault at the HARTGTN7 115.00 (640212) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARTGTN7 (640212) 115.0 kV to GAVINS 7 (652511) 115.0 kV Transmission Circuit #1 b.2. HARTGTN7 (640212) 115.0 kV to BELDEN 7 (640080) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault334 | Single Phase Fault with Stuck Breaker on HILDRTH7 115.00 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 115.00 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HILDRTH7 (640222) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault335 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault336 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault337 | Single Phase Fault with Stuck Breaker on RIVERDL4 230.00 (640330) 230 kV Bus a. Apply Fault at the RIVERDL4 230.00 (640330) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVERDL4 (640330) 230.0 kV to C.CREEK4 (640093) 230.0 kV Transmission Circuit #1 b.2. RIVERDL4 (640330) 230.0 kV to RIVERDL7 (640331) 115.0 kV to RIVERDALET19 (643128) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault338 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to SHELCRK4 (640343) 230.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 b.2. SHELCRK3 (640342) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault339 | Single Phase Fault with Stuck Breaker on STAPLETON 7115.00 (640359) 115 kV Bus a. Apply Fault at the STAPLETON 7115.00 (640359) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STAPLETON 7 (640359) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 b.2. STAPLETON 7 (640359) 115.0 kV to MAXWELS7 (640267) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault340 | Single Phase Fault with Stuck Breaker on SUTTON 7 115.00 (640372) 115 kV Bus a. Apply Fault at the SUTTON 7 115.00 (640372) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUTTON 7 (640372) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.2. SUTTON 7 (640372) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault341 | Single Phase Fault with Stuck Breaker on TWIN CH4 230.00 (640386) 230 kV Bus a. Apply Fault at the TWIN CH4 230.00 (640386) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. TWIN CH4 (640386) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault342 | Single Phase Fault with Stuck Breaker on CARLJCT7 115.00 (640105) 115 kV Bus a. Apply Fault at the CARLJCT7 115.00 (640105) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARLJCT7 (640105) 115.0 kV to HEBRN N7 (640218) 115.0 kV Transmission Circuit #1 b.2. CARLJCT7 (640105) 115.0 kV to GENEVA 7 (640178) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault343 | Single Phase Fault with Stuck Breaker on YORK SW7 115.00 (640413) 115 kV Bus a. Apply Fault at the YORK SW7 115.00 (640413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. YORK SW7 (640413) 115.0 kV to MCCOOL 7 (640272) 115.0 kV Transmission Circuit #1 b.2. YORK SW7 (640413) 115.0 kV to YORK 7 (640411) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault344 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault345 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault346 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING4 (640214) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. HASTING4 (640214) 230.0 kV to HASTCTY7 (641088) 115.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault347 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.2. S1254 5 (646254) 161.0 kV to S1249 5 (646249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault348 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S906 S 8 (647906) 69.0 kV to S904 8 (647904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault349 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault350 | Single Phase Fault with Stuck Breaker on S910 8 69.000 (647910) 69 kV Bus a. Apply Fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to S908 8 (647908) 69.0 kV Transmission Circuit #1 b.2. S910 8 (647910) 69.0 kV to JCT205 8 (647105) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault351 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault352 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault353 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY5 (652566) 161.0 kV to PLYMOTH5 (635223) 161.0 kV Transmission Circuit #1 b.2. SIOUXCY5 (652566) 161.0 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault354 | Single Phase Fault with Stuck Breaker on OAKLAND7 (640300) 115 kV Bus a. Apply Fault at the OAKLAND7 (640300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKLAND7 (640300) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault355 | Single Phase Fault with Stuck Breaker on RAUN 5 (635201) 161 kV Bus a. Apply Fault at the RAUN 5 (635201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault356 | Single Phase Fault with Stuck Breaker on SIOUXCY3 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault357 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault358 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault359 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault360 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-144 : PTDF of 0.67744 | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault361 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault362 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault363 | Single Phase Fault with Stuck Breaker on MONOLITH 7 (640591) 115 kV Bus a. Apply Fault at the MONOLITH 7 (640591) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault364 | Single Phase Fault with Stuck Breaker on TOBIAS 3 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault365 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault366 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault367 | Single Phase Fault with Stuck Breaker on MOORE 3 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault368 | Single Phase Fault with Stuck Breaker on MCCOOL 3 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault369 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault370 | Single Phase Fault with Stuck Breaker on PAULINE3 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault371 | Single Phase Fault with Stuck Breaker on PAULINE7 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault372 | Single Phase Fault with Stuck Breaker on HILDRTH7 (640222) 115 kV Bus a. Apply Fault at the HILDRTH7 (640222) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HILDRTH7 (640222) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault374 | Single Phase Fault with Stuck Breaker on S910 8 (647910) 69 kV Bus a. Apply Fault at the S910 8 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault375 | Single Phase Fault with Stuck Breaker on HOSKINS4 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault376 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault377 | Single Phase Fault with Stuck Breaker on HOSKINS7 (640228) 115 kV Bus a. Apply Fault at the HOSKINS7 (640228) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault378 | Single Phase Fault with Stuck Breaker on NORFOLK7 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault379 | Single Phase Fault with Stuck Breaker on BELDEN 7 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault380 | Single Phase Fault with Stuck Breaker on ANTELOPE 7 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault381 | Single Phase Fault with Stuck Breaker on SHELCRK3 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault382 | Single Phase Fault with Stuck Breaker on ORD 7 (640308) 115 kV Bus a. Apply Fault at the ORD 7 (640308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORD 7 (640308) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault383 | Single Phase Fault with Stuck Breaker on BROKENB7 (640089) 115 kV Bus a. Apply Fault at the BROKENB7 (640089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROKENB7 (640089) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault384 | Single Phase Fault with Stuck Breaker on LOUPCTY7 (640259) 115 kV Bus a. Apply Fault at the LOUPCTY7 (640259) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOUPCTY7 (640259) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault385 | Single Phase Fault with Stuck Breaker on ST.LIB 7 (640353) 115 kV Bus a. Apply Fault at the ST.LIB 7 (640353) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST.LIB 7 (640353) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault386 | Single Phase Fault with Stuck Breaker on ALBION 7 (640054) 115 kV Bus a. Apply Fault at the ALBION 7 (640054) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALBION 7 (640054) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_LOCAL_P4_Fault387 | Single Phase Fault with Stuck Breaker on GENOA 7 (640181) 115 kV Bus a. Apply Fault at the GENOA 7 (640181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENOA 7 (640181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault1 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 4G (635024) 26.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault2 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to WSEC 3G (635023) 24.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault3 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault4 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B1 9 (635101) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault5 | Single Phase Fault with Stuck Breaker on RLHILLS3 345.00 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 345.00 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 b.2. RLHILLS3 (635100) 345.0 kV to RLHILLS B3 9 (635105) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault6 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault7 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault8 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault9 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault10 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault11 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault12 | Single Phase Fault with Stuck Breaker on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 b.2. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault13 | Single Phase Fault with Stuck Breaker on FALLOW 3 345.00 (635590) 345 kV Bus a. Apply Fault at the FALLOW 3 345.00 (635590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 b.2. FALLOW 3 (635590) 345.0 kV to MRNLGHT B1 9 (635595) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault14 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 3 (635200) 345.0 kV to NEAL 3G (635213) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault15 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to NEAL 4G (635214) 24.0 kV Two Winding #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault16 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault17 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault18 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault19 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault20 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault21 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault22 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault23 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault24 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault25 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault26 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault27 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault28 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault29 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault30 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault31 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault32 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault33 | Single Phase Fault with Stuck Breaker on LAKPLAT-ER4 230.00 (655475) 230 kV Bus a. Apply Fault at the LAKPLAT-ER4 230.00 (655475) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. LAKPLAT-ER4 (655475) 230.0 kV to LAKPLAT-ER8 (655476) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault34 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault35 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault36 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault37 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.4. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.5. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault38 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP8 (652276) 69.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.3. FTTHOMP9 (652277) 13.8 kV to FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault39 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.2. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault40 | Single Phase Fault with Stuck Breaker on FTRANDL7 115.00 (652510) 115 kV Bus a. Apply Fault at the FTRANDL7 115.00 (652510) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault41 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.2. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.3. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.5. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault42 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault43 | Single Phase Fault with Stuck Breaker on WHTSWAN-ER7 115.00 (655490) 115 kV Bus a. Apply Fault at the WHTSWAN-ER7 115.00 (655490) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault44 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault45 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault46 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault47 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault48 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault49 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault50 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault51 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 b.3. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault52 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault53 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to CHERRYC3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault54 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.5. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.6. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.7. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.8. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.9. SIOUXC39 (652308) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.10. SIOUXC49 (652310) 13.8 kV to SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV Three Winding #1 b.11. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.12. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault55 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault56 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault57 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault58 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to GENTLMN4 (640184) 230.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault59 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault60 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON3 (640252) 345.0 kV to KEYSTON7 (640253) 115.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault61 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault62 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault63 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault64 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault65 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault66 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault67 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault68 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault69 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault70 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault71 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault72 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault73 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault74 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault75 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault76 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault77 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault79 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault80 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault81 | Single Phase Fault with Stuck Breaker on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault82 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault83 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault84 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault85 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault86 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault87 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault88 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault89 | Single Phase Fault with Stuck Breaker on STHLND 3 345.00 (635016) 345 kV Bus a. Apply Fault at the STHLND 3 345.00 (635016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHLND 3 (635016) 345.0 kV to CBLUFFS3 (635000) 345.0 kV Transmission Circuit #1 b.2. STHLND 3 (635016) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault90 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault91 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault92 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault93 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault94 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault95 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault96 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault98 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault99 | Single Phase Fault with Stuck Breaker on G16-050-TAP (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault100 | Single Phase Fault with Stuck Breaker on PNYCRK 3 (635013) 345 kV Bus a. Apply Fault at the PNYCRK 3 (635013) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PNYCRK 3 (635013) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault102 | Single Phase Fault with Stuck Breaker on CBLUFFS3 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault103 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault104 | Single Phase Fault with Stuck Breaker on GENTLMN4 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault105 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault106 | Single Phase Fault with Stuck Breaker on G17-183-TAP (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault107 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault108 | Single Phase Fault with Stuck Breaker on STHLND 3 (635016) 345 kV Bus a. Apply Fault at the STHLND 3 (635016) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHLND 3 (635016) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault109 | Single Phase Fault with Stuck Breaker on J412 POI 3 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault110 | Single Phase Fault with Stuck Breaker on ST JOE 5 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault111 | Single Phase Fault with Stuck Breaker on CBLUFFS5 (635001) 161 kV Bus a. Apply Fault at the CBLUFFS5 (635001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault113 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault114 | Single Phase Fault with Stuck Breaker on GENTLMN3 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault115 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault116 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault117 | Single Phase Fault with Stuck Breaker on POSTROCK7 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault118 | Single Phase Fault with Stuck Breaker on RLHILLS3 (635100) 345 kV Bus a. Apply Fault at the RLHILLS3 (635100) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RLHILLS3 (635100) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault119 | Single Phase Fault with Stuck Breaker on HOSKINS3 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault120 | Single Phase Fault with Stuck Breaker on S3451 3 (645451) 345 kV Bus a. Apply Fault at the S3451 3 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault121 | Single Phase Fault with Stuck Breaker on S3456 3 (645456) 345 kV Bus a. Apply Fault at the S3456 3 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault122 | Single Phase Fault with Stuck Breaker on OVRLND 3 (635014) 345 kV Bus a. Apply Fault at the OVRLND 3 (635014) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVRLND 3 (635014) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault123 | Single Phase Fault with Stuck Breaker on S1280 5 (646280) 161 kV Bus a. Apply Fault at the S1280 5 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1280 5 (646280) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault124 | Single Phase Fault with Stuck Breaker on N.PLATT4 (640286) 230 kV Bus a. Apply Fault at the N.PLATT4 (640286) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.PLATT4 (640286) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault125 | Single Phase Fault with Stuck Breaker on BEVERLY7 (640082) 115 kV Bus a. Apply Fault at the BEVERLY7 (640082) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEVERLY7 (640082) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault126 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault127 | Single Phase Fault with Stuck Breaker on SWEET W3 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault128 | Single Phase Fault with Stuck Breaker on IDA CO 3 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault129 | Single Phase Fault with Stuck Breaker on 7FAIRPT (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25W | Transfer | GROUP2_REGIONAL_P4_Fault130 | Single Phase Fault with Stuck Breaker on MINGO 7 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 NEBRASKA | DISIS-2017-002 CF | 25S | Base | GROUP2_LOCAL_P1_Fault79 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25S | Base | GROUP2_LOCAL_P1_Fault400 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Oscillatory response due to non-convergence following the event. | Contingent on the queued Multi - Sheldon - Monolith 115 kV upgrade. Stable response observed after the upgrade is in-service.
02 NEBRASKA | DISIS-2017-002 CF | 25S | Base | GROUP2_LOCAL_P4_Fault166 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25S | Base | GROUP2_LOCAL_P4_Fault168 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25S | Base | GROUP2_LOCAL_P4_Fault195 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25S | Base | GROUP2_LOCAL_P4_Fault302 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25S | Base | GROUP2_LOCAL_P4_Fault360 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Base | GROUP2_LOCAL_P1_Fault79 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Base | GROUP2_LOCAL_P1_Fault400 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Oscillatory response due to non-convergence following the event. | Contingent on the queued Multi - Sheldon - Monolith 115 kV upgrade. Stable response observed after the upgrade is in-service.
02 NEBRASKA | DISIS-2017-002 CF | 25W | Base | GROUP2_LOCAL_P4_Fault166 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Base | GROUP2_LOCAL_P4_Fault168 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.3. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Base | GROUP2_LOCAL_P4_Fault195 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.8. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.9. GR ISL29 (653316) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Base | GROUP2_LOCAL_P4_Fault302 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
02 NEBRASKA | DISIS-2017-002 CF | 25W | Base | GROUP2_LOCAL_P4_Fault360 | Single Phase Fault with Stuck Breaker on GR ISLD3 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at several nearby generating sites following the event. | Multi - Gentleman - Cherry Co. - Holt Co. 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT2 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.3. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT3 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT4 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT5 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.2. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.3. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.4. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding #1 b.5. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT6 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT7 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT8 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT9 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT10 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT11 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT12 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT13 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT14 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT15 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT16 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT17 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT18 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT19 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT20 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT21 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT22 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT23 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT24 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT25 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT26 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT27 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT28 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT29 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT30 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT31 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT32 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT33 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT34 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT35 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT36 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT37 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT38 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT39 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT40 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT41 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT42 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT43 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT44 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT45 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT46 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT47 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT48 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT49 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT50 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT51 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT52 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT53 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT54 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT55 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT56 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT57 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT58 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT59 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT60 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT61 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT62 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT63 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT64 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT65 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT66 | 3 Phase fault on QUINTON3 115.00 (533172) 115 kV Bus a. Apply fault at the QUINTON3 115.00 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT67 | 3 Phase fault on 6 GOLDN3 115.00 (533177) 115 kV Bus a. Apply fault at the 6 GOLDN3 115.00 (533177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT68 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT69 | 3 Phase fault on INDIANH3 115.00 (533166) 115 kV Bus a. Apply fault at the INDIANH3 115.00 (533166) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT70 | 3 Phase fault on 17&FAIR3 115.00 (533175) 115 kV Bus a. Apply fault at the 17&FAIR3 115.00 (533175) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17&FAIR3 (533175) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT71 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT72 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT73 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT74 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT75 | 3 Phase fault on BONITA 3 115.00 (533262) 115 kV Bus a. Apply fault at the BONITA 3 115.00 (533262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONITA 3 (533262) 115.0 kV to SPRINGH3 (533267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT76 | 3 Phase fault on GEARY 3 115.00 (533336) 115 kV Bus a. Apply fault at the GEARY 3 115.00 (533336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT77 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT78 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT79 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT80 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT81 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT82 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT83 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT84 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT85 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT86 | 3 Phase fault on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT87 | 3 Phase fault on EMANHAT3 115.00 (533326) 115 kV Bus a. Apply fault at the EMANHAT3 115.00 (533326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT3 (533326) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT88 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to MANVILE3 (533426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT89 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT90 | 3 Phase fault on FAIRGDS3 115.00 (533236) 115 kV Bus a. Apply fault at the FAIRGDS3 115.00 (533236) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT91 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT92 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT93 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT94 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT95 | 3 Phase fault on WM BROS3 115.00 (533183) 115 kV Bus a. Apply fault at the WM BROS3 115.00 (533183) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WM BROS3 (533183) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT96 | 3 Phase fault on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT97 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT98 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT99 | 3 Phase fault on KERFORD3 115.00 (533216) 115 kV Bus a. Apply fault at the KERFORD3 115.00 (533216) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERFORD3 (533216) 115.0 kV to NW LEAV3 (533259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT100 | 3 Phase fault on KSU W 3 115.00 (533333) 115 kV Bus a. Apply fault at the KSU W 3 115.00 (533333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT101 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT102 | 3 Phase fault on MANVILE3 115.00 (533426) 115 kV Bus a. Apply fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT103 | 3 Phase fault on REFINRY3 115.00 (533427) 115 kV Bus a. Apply fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT104 | 3 Phase fault on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT105 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT106 | 3 Phase fault on MORRIS 3 115.00 (533305) 115 kV Bus a. Apply fault at the MORRIS 3 115.00 (533305) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT107 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT108 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT109 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT110 | 3 Phase fault on STRANGR3 115.00 (533268) 115 kV Bus a. Apply fault at the STRANGR3 115.00 (533268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT111 | 3 Phase fault on UNIONRG3 115.00 (533359) 115 kV Bus a. Apply fault at the UNIONRG3 115.00 (533359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG3 (533359) 115.0 kV to TCHOPE 3 (533360) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT112 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT113 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT114 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to RA5HIPR2 (533706) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT115 | 3 Phase fault on FRNTR N2 69.000 (533593) 69 kV Bus a. Apply fault at the FRNTR N2 69.000 (533593) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNTR N2 (533593) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT116 | 3 Phase fault on BUTLERN2 69.000 (533583) 69 kV Bus a. Apply fault at the BUTLERN2 69.000 (533583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERN2 (533583) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT117 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT118 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT119 | 3 Phase fault on DAVIS 2 69.000 (533506) 69 kV Bus a. Apply fault at the DAVIS 2 69.000 (533506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 2 (533506) 69.0 kV to MWIRNJ22 (533529) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT120 | 3 Phase fault on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT121 | 3 Phase fault on INDEPEN2 69.000 (533694) 69 kV Bus a. Apply fault at the INDEPEN2 69.000 (533694) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT122 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT123 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCAN 2 (533850) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT124 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT125 | 3 Phase fault on STROTHR2 69.000 (533556) 69 kV Bus a. Apply fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT126 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT127 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT128 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT129 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT130 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT131 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT132 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT133 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT134 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT135 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT136 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT137 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT138 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT139 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT140 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT141 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT142 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT143 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT144 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT145 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT146 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT147 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT148 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT149 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT150 | 3 Phase fault on 5WEDK 1 161.00 (345975) 161 kV Bus a. Apply fault at the 5WEDK 1 161.00 (345975) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAPE GIR1 (344280) 161.0 kV to 5CAPE GIR2 (344282) 161.0 kV Transmission Circuit #z b.2. 5CAPE GIR1 (344280) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #1 b.3. 5CAPE GIR1 (344280) 161.0 kV to 5WEDK 1 (345975) 161.0 kV Transmission Circuit #1 b.4. 5CHARMN 1 (344338) 161.0 kV to 5TRAIL_TR TP (345824) 161.0 kV Transmission Circuit #1 b.5. 5TRAIL TR (345823) 161.0 kV to 5TRAIL_TR TP (345824) 161.0 kV Transmission Circuit #z b.6. 5WEDK 1 (345975) 161.0 kV to 5WEDK 2 (345984) 161.0 kV Transmission Circuit #z b.7. 1CHARMIN (346035) 13.2 kV to 5CHARMN 1 (344338) 161.0 kV Two Winding #1 b.8. 1CHARMIN (346035) 13.2 kV to 5CHARMN 1 (344338) 161.0 kV Two Winding #2 b.9. 2TRAIL TR (346144) 69.0 kV to 5TRAIL TR (345823) 161.0 kV Two Winding #1 b.10. 1WEDEKIND (346157) 34.5 kV to 5WEDK 1 (345975) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT151 | 3 Phase fault on 5ORAN 161.00 (345375) 161 kV Bus a. Apply fault at the 5ORAN 161.00 (345375) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORLEY (300121) 161.0 kV to 5ORAN (345375) 161.0 kV Transmission Circuit #1 b.2. 5KELSO 2 (344850) 161.0 kV to 5ORAN (345375) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT152 | 3 Phase fault on 7KELSO 2 345.00 (344849) 345 kV Bus a. Apply fault at the 7KELSO 2 345.00 (344849) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 2 (344849) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT153 | 3 Phase fault on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7LUTESVIL (344974) 345.0 kV to 7ST FRANC (345773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT154 | 3 Phase fault on 7HERITAGE 345.00 (345434) 345 kV Bus a. Apply fault at the 7HERITAGE 345.00 (345434) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7LUTESVIL (344974) 345.0 kV to 7HERITAGE (345434) 345.0 kV Transmission Circuit #1 b.2. 7HERITAGE (345434) 345.0 kV to 5HERITAGE 1 (345976) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT155 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT156 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT157 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT158 | 3 Phase fault on 7KELSO 2 345.00 (344849) 345 kV Bus a. Apply fault at the 7KELSO 2 345.00 (344849) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 2 (344849) 345.0 kV to 5KELSO 2 (344850) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT159 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT160 | 3 Phase fault on 5CAPE GIR2 161.00 (344282) 161 kV Bus a. Apply fault at the 5CAPE GIR2 161.00 (344282) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAPE GIR1 (344280) 161.0 kV to 5CAPE GIR2 (344282) 161.0 kV Transmission Circuit #z b.2. 5CAPE GIR2 (344282) 161.0 kV to 5CAPE GIR3 (344286) 161.0 kV Transmission Circuit #z b.3. 5CAPE GIR2 (344282) 161.0 kV to 5VIADUCT 1 (345894) 161.0 kV Transmission Circuit #z b.4. 5CAPE GIR2 (344282) 161.0 kV to 5JOPPA SR (351006) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT161 | 3 Phase fault on 5CAPE GIR3 161.00 (344286) 161 kV Bus a. Apply fault at the 5CAPE GIR3 161.00 (344286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAPE GIR2 (344282) 161.0 kV to 5CAPE GIR3 (344286) 161.0 kV Transmission Circuit #z b.2. 5CAPE GIR3 (344286) 161.0 kV to 5VIAD_TP (345891) 161.0 kV Transmission Circuit #2 b.3. 5CAPE GIR3 (344286) 161.0 kV to 5VIADUCT 2 (345893) 161.0 kV Transmission Circuit #z b.4. 5CAPE GIR3 (344286) 161.0 kV to 5HERITAGE 1 (345976) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT162 | 3 Phase fault on 8NEWMAD 500.00 (300035) 500 kV Bus a. Apply fault at the 8NEWMAD 500.00 (300035) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8NEWMAD (300035) 500.0 kV to 8WNEWMADRID (301406) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT163 | 3 Phase fault on 7STFRAN 345.00 (300048) 345 kV Bus a. Apply fault at the 7STFRAN 345.00 (300048) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7STFRAN (300048) 345.0 kV to 7GOBKNOB (300054) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT164 | 3 Phase fault on 5ESSEX 161.00 (300075) 161 kV Bus a. Apply fault at the 5ESSEX 161.00 (300075) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ESSEX (300075) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT165 | 3 Phase fault on 5GRNFRT 161.00 (300084) 161 kV Bus a. Apply fault at the 5GRNFRT 161.00 (300084) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRNFRT (300084) 161.0 kV to POP BLF5 (505438) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT166 | 3 Phase fault on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 b.3. 2GIBSON (301291) 69.0 kV to 5GIBSON (300083) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT167 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT168 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to N MADRD5 (505400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT169 | 3 Phase fault on 2CAMBEL 69.000 (301196) 69 kV Bus a. Apply fault at the 2CAMBEL 69.000 (301196) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CAMBEL (301196) 69.0 kV to 2GIBSON (301291) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT170 | 3 Phase fault on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT171 | 3 Phase fault on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT172 | 3 Phase fault on 2GIBSON 69.000 (301291) 69 kV Bus a. Apply fault at the 2GIBSON 69.000 (301291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GIBSON (301291) 69.0 kV to 2KENNET (301294) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT173 | 3 Phase fault on 2GIBSON 69.000 (301291) 69 kV Bus a. Apply fault at the 2GIBSON 69.000 (301291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GIBSON (301291) 69.0 kV to 2CLARKTON (301432) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT174 | 3 Phase fault on 8POWERLN_RD%500.00 (338156) 500 kV Bus a. Apply fault at the 8POWERLN_RD%500.00 (338156) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8POWERLN_RD% (338156) 500.0 kV to 8DELL% (338187) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT175 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 5DELL# (338596) 161.0 kV to 1DELL T1 (338597) 13.8 kV Three Winding #1 b.2. 8DELL% (338187) 500.0 kV to 5DELL# (338596) 161.0 kV to 1DELL T2 (338598) 13.8 kV Three Winding #1 b.3. 8DELL% (338187) 500.0 kV to 5DELL# (338596) 161.0 kV to 1DELL T3 (338599) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT176 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 8SANS SOUCI% (338188) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT177 | 3 Phase fault on 5STEELE! 161.00 (338194) 161 kV Bus a. Apply fault at the 5STEELE! 161.00 (338194) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STEELE! (338194) 161.0 kV to 5HAYTI.S% (338200) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT178 | 3 Phase fault on 5HAYTI.S% 161.00 (338200) 161 kV Bus a. Apply fault at the 5HAYTI.S% 161.00 (338200) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HAYTI.S% (338200) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT179 | 3 Phase fault on 5JIM HILL% 161.00 (338202) 161 kV Bus a. Apply fault at the 5JIM HILL% 161.00 (338202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JIM HILL% (338202) 161.0 kV to 5RECTOR.N# (338689) 161.0 kV Transmission Circuit #1 b.2. 5PARAGOULD% (338204) 161.0 kV to 5HALLIDAY# (338709) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT180 | 3 Phase fault on N MADRD5 161.00 (505400) 161 kV Bus a. Apply fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X1 1 (505401) 13.8 kV Three Winding #1 b.2. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X2 1 (505403) 13.8 kV Three Winding #1 b.3. NMA X1 1 (505401) 13.8 kV to N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV Three Winding #1 b.6. NMA X2 1 (505403) 13.8 kV to N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT181 | 3 Phase fault on N MADRD5 161.00 (505400) 161 kV Bus a. Apply fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD5 (505400) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT182 | 3 Phase fault on KENNETT5 161.00 (505410) 161 kV Bus a. Apply fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEN X1 1 (505407) 13.8 kV to KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV Three Winding #1 b.3. KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV to KEN X2 1 (505409) 13.8 kV Three Winding #1 b.5. KENNETT5 (505410) 161.0 kV to KENNETT2 (505408) 69.0 kV to KEN X1 1 (505407) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT183 | 3 Phase fault on KENNETT5 161.00 (505410) 161 kV Bus a. Apply fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENNETT5 (505410) 161.0 kV to PARAGLD5 (505412) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT184 | 3 Phase fault on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRG X1 1 (505411) 13.8 kV to PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV Three Winding #1 b.2. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X1 1 (505411) 13.8 kV Three Winding #1 b.3. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X2 1 (505413) 13.8 kV Three Winding #1 b.4. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X3 1 (505415) 13.8 kV Three Winding #1 b.5. PRG X2 1 (505413) 13.8 kV to PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV Three Winding #1 b.9. PRG X3 1 (505415) 13.8 kV to PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT185 | 3 Phase fault on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT186 | 3 Phase fault on CENTR H5 161.00 (505416) 161 kV Bus a. Apply fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTR H5 (505416) 161.0 kV to JONESBO5 (505418) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT187 | 3 Phase fault on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKESTN5 (505428) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT188 | 3 Phase fault on POP BLF5 161.00 (505438) 161 kV Bus a. Apply fault at the POP BLF5 161.00 (505438) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PBL X1 1 (505435) 13.8 kV to POP BLF2 (505436) 69.0 kV to POP BLF5 (505438) 161.0 kV Three Winding #1 b.3. POP BLF2 (505436) 69.0 kV to POP BLF5 (505438) 161.0 kV to PBL X2 1 (505437) 13.8 kV Three Winding #1 b.4. POP BLF2 (505436) 69.0 kV to POP BLF5 (505438) 161.0 kV to PBL X3 1 (505439) 13.8 kV Three Winding #1 b.6. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X1 1 (505435) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT189 | 3 Phase fault on KENNETT5 161.00 (505410) 161 kV Bus a. Apply fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENNETT5 (505410) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT190 | 3 Phase fault on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGLD5 (505412) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT191 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT192 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT193 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT194 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT195 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT196 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT197 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT198 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT199 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT200 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT201 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT202 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT203 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT204 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT205 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT206 | 3 Phase fault on 5STFRANB2 161.00 (300115) 161 kV Bus a. Apply fault at the 5STFRANB2 161.00 (300115) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STFRANB2 (300115) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT207 | 3 Phase fault on 8WNEWMADRID 500.00 (301406) 500 kV Bus a. Apply fault at the 8WNEWMADRID 500.00 (301406) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WNEWMADRID (301406) 500.0 kV to 8DELL% (338187) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT208 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT209 | 3 Phase fault on 5PORTAGEVLE 161.00 (338201) 161 kV Bus a. Apply fault at the 5PORTAGEVLE 161.00 (338201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.3. 5PORTAGEVLE (338201) 161.0 kV to 1PORTGVIL (345534) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT210 | 3 Phase fault on 5PORTAGEVLE 161.00 (338201) 161 kV Bus a. Apply fault at the 5PORTAGEVLE 161.00 (338201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 8W.MEMPHIS% (338162) 500.0 kV to 8BHAM STEEL (360075) 500.0 kV Transmission Circuit #1 b.3. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT211 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT212 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT213 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT214 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT215 | 3 Phase fault on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT216 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT217 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT218 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT219 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT220 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT221 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT222 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT223 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT224 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT225 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT226 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT227 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT228 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT229 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT230 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT231 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT232 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT233 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT234 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT235 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT236 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT237 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT238 | 3 Phase fault on 41CALIF3 115.00 (533160) 115 kV Bus a. Apply fault at the 41CALIF3 115.00 (533160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT239 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to AMELIA 3 (533215) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT240 | 3 Phase fault on S GAGEE3 115.00 (533178) 115 kV Bus a. Apply fault at the S GAGEE3 115.00 (533178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT241 | 3 Phase fault on CORONAD3 115.00 (533394) 115 kV Bus a. Apply fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT242 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT243 | 3 Phase fault on LEC U4 3 115.00 (533249) 115 kV Bus a. Apply fault at the LEC U4 3 115.00 (533249) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT244 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT245 | 3 Phase fault on MIDIANW2 69.000 (533597) 69 kV Bus a. Apply fault at the MIDIANW2 69.000 (533597) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIANW2 (533597) 69.0 kV to THUNBRD2 (533603) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT246 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT247 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT248 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT249 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT250 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT251 | 3 Phase fault on COMOTAR4 138.00 (533037) 138 kV Bus a. Apply fault at the COMOTAR4 138.00 (533037) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT252 | 3 Phase fault on INTERST4 138.00 (533051) 138 kV Bus a. Apply fault at the INTERST4 138.00 (533051) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT253 | 3 Phase fault on 43LORAN 115.00 (533440) 115 kV Bus a. Apply fault at the 43LORAN 115.00 (533440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.3. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT254 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT255 | 3 Phase fault on PEIL 3 115.00 (533343) 115 kV Bus a. Apply fault at the PEIL 3 115.00 (533343) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEIL 3 (533343) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.2. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT256 | 3 Phase fault on FRONTEN2 69.000 (533775) 69 kV Bus a. Apply fault at the FRONTEN2 69.000 (533775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.2. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT257 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 b.5. DEARING1 (533089) 13.2 kV to DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT258 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 b.4. LIBERTY1 (533090) 13.2 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT259 | 3 Phase fault on NINMLTP4 138.00 (521128) 138 kV Bus a. Apply fault at the NINMLTP4 138.00 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT260 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT261 | 3 Phase fault on CDRDLTP4 138.00 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 138.00 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT262 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT263 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT264 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT265 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT266 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT267 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT268 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT269 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT270 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT271 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT272 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT273 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT274 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT275 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT276 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT277 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT278 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT279 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT280 | 3 Phase fault on FOWLER 4 138.00 (533043) 138 kV Bus a. Apply fault at the FOWLER 4 138.00 (533043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT281 | 3 Phase fault on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT282 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT283 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT284 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT285 | 3 Phase fault on TALLGRS4 138.00 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 138.00 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT286 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT287 | 3 Phase fault on CENTENN4 138.00 (533034) 138 kV Bus a. Apply fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT288 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT289 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT290 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT291 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT292 | 3 Phase fault on BU11PON4 138.00 (533032) 138 kV Bus a. Apply fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT293 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT294 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT295 | 3 Phase fault on BEECHTP4 138.00 (533028) 138 kV Bus a. Apply fault at the BEECHTP4 138.00 (533028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.2. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.3. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.4. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT296 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT297 | 3 Phase fault on ANDOVER4 138.00 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 138.00 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT298 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT299 | 3 Phase fault on 29EVENG3 115.00 (533185) 115 kV Bus a. Apply fault at the 29EVENG3 115.00 (533185) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT300 | 3 Phase fault on SALTCRK3 115.00 (533434) 115 kV Bus a. Apply fault at the SALTCRK3 115.00 (533434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.2. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT301 | 3 Phase fault on 27CROCO3 115.00 (533187) 115 kV Bus a. Apply fault at the 27CROCO3 115.00 (533187) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT302 | 3 Phase fault on N TYLER3 115.00 (533168) 115 kV Bus a. Apply fault at the N TYLER3 115.00 (533168) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to N TYLER3 (533168) 115.0 kV Transmission Circuit #1 b.2. N TYLER3 (533168) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT303 | 3 Phase fault on FMC 3 115.00 (533241) 115 kV Bus a. Apply fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.2. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT304 | 3 Phase fault on EUDORA 3 115.00 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 115.00 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.2. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT305 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT306 | 3 Phase fault on EABILEN3 115.00 (533365) 115 kV Bus a. Apply fault at the EABILEN3 115.00 (533365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT307 | 3 Phase fault on JCTCTY 3 115.00 (533330) 115 kV Bus a. Apply fault at the JCTCTY 3 115.00 (533330) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT308 | 3 Phase fault on PARALEL3 115.00 (533218) 115 kV Bus a. Apply fault at the PARALEL3 115.00 (533218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to PARALEL3 (533218) 115.0 kV Transmission Circuit #1 b.2. PARALEL3 (533218) 115.0 kV to WALNUT 3 (533220) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT309 | 3 Phase fault on SHERWOD3 115.00 (533194) 115 kV Bus a. Apply fault at the SHERWOD3 115.00 (533194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT310 | 3 Phase fault on KEENE 3 115.00 (533167) 115 kV Bus a. Apply fault at the KEENE 3 115.00 (533167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 b.2. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT311 | 3 Phase fault on SOUTHTN3 115.00 (533265) 115 kV Bus a. Apply fault at the SOUTHTN3 115.00 (533265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.2. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT312 | 3 Phase fault on FORBES 3 115.00 (533157) 115 kV Bus a. Apply fault at the FORBES 3 115.00 (533157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORBES 3 (533157) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.2. FORBES 3 (533157) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT313 | 3 Phase fault on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT314 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT315 | 3 Phase fault on 54&MERI3 115.00 (533156) 115 kV Bus a. Apply fault at the 54&MERI3 115.00 (533156) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT316 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT317 | 3 Phase fault on LEVEE 3 115.00 (533327) 115 kV Bus a. Apply fault at the LEVEE 3 115.00 (533327) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT3 (533326) 115.0 kV to LEVEE 3 (533327) 115.0 kV Transmission Circuit #1 b.2. LEVEE 3 (533327) 115.0 kV to MATTERS3 (533334) 115.0 kV Transmission Circuit #1 b.3. MATTERS3 (533334) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT318 | 3 Phase fault on BISMARK3 115.00 (533234) 115 kV Bus a. Apply fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT319 | 3 Phase fault on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. OSAGE 3 (533170) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.3. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.4. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.5. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT320 | 3 Phase fault on NTHLAND3 115.00 (533169) 115 kV Bus a. Apply fault at the NTHLAND3 115.00 (533169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.2. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT321 | 3 Phase fault on TONGATP3 115.00 (533219) 115 kV Bus a. Apply fault at the TONGATP3 115.00 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT322 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT323 | 3 Phase fault on HALLMRK3 115.00 (533242) 115 kV Bus a. Apply fault at the HALLMRK3 115.00 (533242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.2. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT324 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT325 | 3 Phase fault on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT326 | 3 Phase fault on STULL T3 115.00 (533270) 115 kV Bus a. Apply fault at the STULL T3 115.00 (533270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.3. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.5. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT327 | 3 Phase fault on STAGGHL3 115.00 (533341) 115 kV Bus a. Apply fault at the STAGGHL3 115.00 (533341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.2. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT328 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT329 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT330 | 3 Phase fault on NORTHST3 115.00 (533370) 115 kV Bus a. Apply fault at the NORTHST3 115.00 (533370) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT331 | 3 Phase fault on FRTLEAV3 115.00 (533274) 115 kV Bus a. Apply fault at the FRTLEAV3 115.00 (533274) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 b.2. SPRUCE 3 (533266) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. SPRUCE 3 (533266) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT332 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT333 | 3 Phase fault on MAPLE J2 69.000 (533516) 69 kV Bus a. Apply fault at the MAPLE J2 69.000 (533516) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 2 (533506) 69.0 kV to MAPLE J2 (533516) 69.0 kV Transmission Circuit #1 b.2. E MADSN2 (533508) 69.0 kV to F MONRO2 (533510) 69.0 kV Transmission Circuit #1 b.3. E MADSN2 (533508) 69.0 kV to MAPLE J2 (533516) 69.0 kV Transmission Circuit #1 b.4. E MADSN2 (533508) 69.0 kV to 3 VANBU2 (533527) 69.0 kV Transmission Circuit #1 b.5. MAPLE J2 (533516) 69.0 kV to 2ND ELM2 (533520) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT334 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT335 | 3 Phase fault on ARCOTAP2 69.000 (533620) 69 kV Bus a. Apply fault at the ARCOTAP2 69.000 (533620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO 2 (533619) 69.0 kV to ARCOTAP2 (533620) 69.0 kV Transmission Circuit #1 b.2. ARCOTAP2 (533620) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.3. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.4. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.6. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT336 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT337 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.3. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT338 | 3 Phase fault on ROCKCRK2 69.000 (533458) 69 kV Bus a. Apply fault at the ROCKCRK2 69.000 (533458) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 2 (533456) 69.0 kV to ROCKCRK2 (533458) 69.0 kV Transmission Circuit #1 b.2. ROCKCRK2 (533458) 69.0 kV to VALLEY22 (533483) 69.0 kV Transmission Circuit #1 b.3. ARNOLD 2 (533471) 69.0 kV to NORTONV2 (533481) 69.0 kV Transmission Circuit #1 b.4. NORTONV2 (533481) 69.0 kV to VALLEY22 (533483) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT339 | 3 Phase fault on ORCHARD2 69.000 (533643) 69 kV Bus a. Apply fault at the ORCHARD2 69.000 (533643) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.3. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT340 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT341 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT342 | 3 Phase fault on PECK 2 69.000 (533830) 69 kV Bus a. Apply fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. GILL W 2 (533796) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.3. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT343 | 3 Phase fault on MIDIANE2 69.000 (533610) 69 kV Bus a. Apply fault at the MIDIANE2 69.000 (533610) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERN2 (533583) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #1 b.2. MIDIANE2 (533610) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT344 | 3 Phase fault on BU5FURL2 69.000 (533861) 69 kV Bus a. Apply fault at the BU5FURL2 69.000 (533861) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THUNBRD2 (533603) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 b.2. CHISHLM2 (533786) 69.0 kV to GRANT 2 (533799) 69.0 kV Transmission Circuit #1 b.3. GRANT 2 (533799) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT345 | 3 Phase fault on HYDROTP2 69.000 (533833) 69 kV Bus a. Apply fault at the HYDROTP2 69.000 (533833) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMAN2 (533787) 69.0 kV to HYDROTP2 (533833) 69.0 kV Transmission Circuit #1 b.2. RENEW 2 (533831) 69.0 kV to HYDROTP2 (533833) 69.0 kV Transmission Circuit #1 b.3. RENEW 2 (533831) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT346 | 3 Phase fault on COFFSUB2 69.000 (533683) 69 kV Bus a. Apply fault at the COFFSUB2 69.000 (533683) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFSUB2 (533683) 69.0 kV to CRA S 2 (533685) 69.0 kV Transmission Circuit #1 b.2. COFFSUB2 (533683) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT347 | 3 Phase fault on BEECRK2 69.000 (533677) 69 kV Bus a. Apply fault at the BEECRK2 69.000 (533677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEECRK2 (533677) 69.0 kV to CANEY 2 (533678) 69.0 kV Transmission Circuit #1 b.2. BEECRK2 (533677) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.3. BEECRK2 (533677) 69.0 kV to COBBTAP2 (533710) 69.0 kV Transmission Circuit #1 b.4. BEECRK2 (533677) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT348 | 3 Phase fault on ROUSE 2 69.000 (533771) 69 kV Bus a. Apply fault at the ROUSE 2 69.000 (533771) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.2. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT349 | 3 Phase fault on WILLJCT2 69.000 (533713) 69 kV Bus a. Apply fault at the WILLJCT2 69.000 (533713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.2. WILLJCT2 (533713) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT350 | 3 Phase fault on WARE 2 69.000 (533652) 69 kV Bus a. Apply fault at the WARE 2 69.000 (533652) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.2. WARE 2 (533652) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 b.3. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT351 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT352 | 3 Phase fault on PITNAC 2 69.000 (533769) 69 kV Bus a. Apply fault at the PITNAC 2 69.000 (533769) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.2. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.3. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT353 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT354 | 3 Phase fault on AQUARS 2 69.000 (533756) 69 kV Bus a. Apply fault at the AQUARS 2 69.000 (533756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AQUARS 2 (533756) 69.0 kV to HUDSJCT2 (533764) 69.0 kV Transmission Circuit #1 b.2. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.3. HUDSJCT2 (533764) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT355 | 3 Phase fault on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT356 | 3 Phase fault on ADA 2 69.000 (533581) 69 kV Bus a. Apply fault at the ADA 2 69.000 (533581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADA 2 (533581) 69.0 kV to ELDORAD2 (533590) 69.0 kV Transmission Circuit #1 b.2. ADA 2 (533581) 69.0 kV to PESTER 2 (533600) 69.0 kV Transmission Circuit #1 b.3. CHESNEY2 (533589) 69.0 kV to MIDIANW2 (533597) 69.0 kV Transmission Circuit #1 b.4. CHESNEY2 (533589) 69.0 kV to PESTER 2 (533600) 69.0 kV Transmission Circuit #1 b.5. ELDORAD2 (533590) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT357 | 3 Phase fault on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT358 | 3 Phase fault on VULCTP 2 69.000 (533851) 69 kV Bus a. Apply fault at the VULCTP 2 69.000 (533851) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.3. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 b.4. SUNSET-2 (533844) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 b.5. SG1CHEN2 (533871) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT359 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT360 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT361 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT362 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.3. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.4. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT363 | 3 Phase fault on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.2. ASHGRV22 (533658) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.3. ASHGRJ12 (533659) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #z1 b.4. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT364 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT365 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT366 | 3 Phase fault on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT367 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT368 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.3. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.4. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.5. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 b.6. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT369 | 3 Phase fault on STALEY 2 69.000 (541261) 69 kV Bus a. Apply fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT370 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT371 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT372 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT373 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT374 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT375 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT376 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT377 | 3 Phase fault on KAW W 5 161.00 (546655) 161 kV Bus a. Apply fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT378 | 3 Phase fault on MAYSOTH5 161.00 (546722) 161 kV Bus a. Apply fault at the MAYSOTH5 161.00 (546722) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT379 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT380 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT381 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT382 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT383 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT384 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT385 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.3. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT386 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT387 | 3 Phase fault on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT388 | 3 Phase fault on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT389 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT390 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.4. MONTGOM1 (533091) 13.2 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT391 | 3 Phase fault on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.3. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT392 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT393 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT394 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT395 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT396 | 3 Phase fault on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPMAN3 (533362) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT397 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT398 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT399 | 3 Phase fault on HARTLND3 115.00 (533197) 115 kV Bus a. Apply fault at the HARTLND3 115.00 (533197) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTLND3 (533197) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT400 | 3 Phase fault on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT401 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT402 | 3 Phase fault on KSU E 3 115.00 (533346) 115 kV Bus a. Apply fault at the KSU E 3 115.00 (533346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSU E 3 (533346) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT403 | 3 Phase fault on NMANHT3 115.00 (533347) 115 kV Bus a. Apply fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT3 (533347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT404 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT405 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT406 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT407 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT408 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT409 | 3 Phase fault on WILDCAT3 115.00 (533345) 115 kV Bus a. Apply fault at the WILDCAT3 115.00 (533345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILDCAT3 (533345) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT410 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT411 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT412 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT413 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT414 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT415 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT416 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT417 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT418 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT419 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT420 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT421 | 3 Phase fault on COALCRK2 69.000 (533633) 69 kV Bus a. Apply fault at the COALCRK2 69.000 (533633) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALCRK2 (533633) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT422 | 3 Phase fault on DAVIS 2 69.000 (533506) 69 kV Bus a. Apply fault at the DAVIS 2 69.000 (533506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 2 (533506) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT423 | 3 Phase fault on DEARING2 69.000 (533688) 69 kV Bus a. Apply fault at the DEARING2 69.000 (533688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT424 | 3 Phase fault on MONTGOM2 69.000 (533698) 69 kV Bus a. Apply fault at the MONTGOM2 69.000 (533698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT425 | 3 Phase fault on MULBERY2 69.000 (533767) 69 kV Bus a. Apply fault at the MULBERY2 69.000 (533767) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULBERY2 (533767) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT426 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT427 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT428 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT429 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT430 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT431 | 3 Phase fault on UDALL 2 69.000 (533559) 69 kV Bus a. Apply fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UDALL 2 (533559) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT432 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT433 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.2. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT434 | 3 Phase fault on 19THST 3 115.00 (533256) 115 kV Bus a. Apply fault at the 19THST 3 115.00 (533256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to 19THST 3 (533256) 115.0 kV Transmission Circuit #1 b.2. 19THST 3 (533256) 115.0 kV to FREESTATE3 (533257) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT435 | 3 Phase fault on CARB-KW 3 115.00 (533195) 115 kV Bus a. Apply fault at the CARB-KW 3 115.00 (533195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.2. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT436 | 3 Phase fault on FREESTATE3 115.00 (533257) 115 kV Bus a. Apply fault at the FREESTATE3 115.00 (533257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT437 | 3 Phase fault on SHAWNEE3 115.00 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 115.00 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT438 | 3 Phase fault on CRAWFRD3 115.00 (533364) 115 kV Bus a. Apply fault at the CRAWFRD3 115.00 (533364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. CRAWFRD3 (533364) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 b.3. MENTOR 3 (533374) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT439 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT440 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT441 | 3 Phase fault on MOONLIT3 115.00 (533254) 115 kV Bus a. Apply fault at the MOONLIT3 115.00 (533254) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT442 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT443 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT444 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT445 | 3 Phase fault on DEERCRK2 69.000 (533457) 69 kV Bus a. Apply fault at the DEERCRK2 69.000 (533457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 2 (533456) 69.0 kV to DEERCRK2 (533457) 69.0 kV Transmission Circuit #1 b.2. DEERCRK2 (533457) 69.0 kV to SANTAFJ2 (533460) 69.0 kV Transmission Circuit #1 b.3. SANTAFJ2 (533460) 69.0 kV to 2MADISN2 (533461) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT446 | 3 Phase fault on LITCH S2 69.000 (533766) 69 kV Bus a. Apply fault at the LITCH S2 69.000 (533766) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT447 | 3 Phase fault on HUDSON-2 69.000 (533763) 69 kV Bus a. Apply fault at the HUDSON-2 69.000 (533763) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON-2 (533763) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT448 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT449 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT450 | 3 Phase fault on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRINGH3 (533267) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT451 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT452 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT453 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT454 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT455 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT456 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT457 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT458 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT459 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT460 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT461 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT462 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT463 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT464 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT465 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT466 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT467 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT468 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT469 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT470 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT471 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT472 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT473 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT474 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT475 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT476 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT477 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT478 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT479 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT480 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT481 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT482 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT483 | 3 Phase fault on S1250 5 161 (646250) 161 kV Bus a. Apply fault at the S1250 5 161 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT484 | 3 Phase fault on S1211 5 161 (646211) 161 kV Bus a. Apply fault at the S1211 5 161 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT485 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT486 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT487 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT488 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT489 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT490 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT491 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT492 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT493 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT494 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT495 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT496 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT497 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT498 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT499 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT500 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT501 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT502 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT503 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT504 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT505 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT506 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT507 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT508 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT509 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT510 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT511 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT512 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT513 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT514 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT515 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT516 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT517 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT518 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT519 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT520 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT521 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT522 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT523 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT524 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT525 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT526 | 3 Phase fault on SIKETAP5 161.00 (505427) 161 kV Bus a. Apply fault at the SIKETAP5 161.00 (505427) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to SIKETAP5 (505427) 161.0 kV Transmission Circuit #1 b.2. SIKETAP5 (505427) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT527 | 3 Phase fault on IODINE 4 138.00 (520957) 138 kV Bus a. Apply fault at the IODINE 4 138.00 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT528 | 3 Phase fault on GLASMTN4 138.00 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 138.00 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT529 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT530 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT531 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT532 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT533 | 3 Phase fault on SEILING4 138.00 (520553) 138 kV Bus a. Apply fault at the SEILING4 138.00 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT534 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT535 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT536 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT537 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT538 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT539 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT540 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT541 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT542 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT543 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT544 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT545 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT546 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT547 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT548 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT549 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT550 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT551 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT552 | 3 Phase fault on ELMCREK6 230.00 (539639) 230 kV Bus a. Apply fault at the ELMCREK6 230.00 (539639) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT553 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT554 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT555 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT556 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT557 | 3 Phase fault on JEWELL 3 115.00 (539669) 115 kV Bus a. Apply fault at the JEWELL 3 115.00 (539669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.2. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT558 | 3 Phase fault on CLIFTON3 115.00 (539656) 115 kV Bus a. Apply fault at the CLIFTON3 115.00 (539656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIFTON3 (539656) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT559 | 3 Phase fault on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT560 | 3 Phase fault on CONCRD6 230.00 (539658) 230 kV Bus a. Apply fault at the CONCRD6 230.00 (539658) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT561 | 3 Phase fault on BARBER 4 138.00 (539674) 138 kV Bus a. Apply fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT562 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT563 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT564 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT565 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT566 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT567 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT568 | 3 Phase fault on 8NEWMAD 500.00 (300035) 500 kV Bus a. Apply fault at the 8NEWMAD 500.00 (300035) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8NEWMAD (300035) 500.0 kV to 8NEWMADXF34 (301528) 500.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT569 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT570 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT571 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT572 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7NEWMADXF34 (301529) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT573 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7NEWMADXF12 (301530) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT574 | 3 Phase fault on 7STFRAN 345.00 (300048) 345 kV Bus a. Apply fault at the 7STFRAN 345.00 (300048) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7STFRAN (300048) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT575 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT576 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT577 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT578 | 3 Phase fault on 5GENTRY 161.00 (300073) 161 kV Bus a. Apply fault at the 5GENTRY 161.00 (300073) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GENTRY (300073) 161.0 kV to 5FAIRPTB2 (300076) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT579 | 3 Phase fault on 5ESSEX 161.00 (300075) 161 kV Bus a. Apply fault at the 5ESSEX 161.00 (300075) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ESSEX (300075) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT580 | 3 Phase fault on 5FAIRPTB2 161.00 (300076) 161 kV Bus a. Apply fault at the 5FAIRPTB2 161.00 (300076) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT581 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT582 | 3 Phase fault on 5MARYVB2 161.00 (300097) 161 kV Bus a. Apply fault at the 5MARYVB2 161.00 (300097) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARYVB2 (300097) 161.0 kV to MARYVLE5 (541251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT583 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M0 (301396) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT584 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M1 (301397) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT585 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M2 (301398) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT586 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M3 (301399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT587 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NEWMADCP (301405) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT588 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NEWMADXF12 (301531) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT589 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NMDSU100HS (301538) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT590 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NMDSU200HS (301539) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT591 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT592 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT593 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT594 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT595 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT596 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT597 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT598 | 3 Phase fault on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STJUDEW (300170) 69.0 kV to 2NMCOAL (300171) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT599 | 3 Phase fault on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STJUDEW (300170) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT600 | 3 Phase fault on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STJUDEW (300170) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT601 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2MAGNOL (300328) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT602 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2ROSEHL (300334) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT603 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT604 | 3 Phase fault on 2CHAPHL 69.000 (300324) 69 kV Bus a. Apply fault at the 2CHAPHL 69.000 (300324) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CHAPHL (300324) 69.0 kV to 2RT Z (300325) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT605 | 3 Phase fault on 2RT Z 69.000 (300325) 69 kV Bus a. Apply fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RT Z (300325) 69.0 kV to 2COLMBUS (300326) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT606 | 3 Phase fault on 2RT Z 69.000 (300325) 69 kV Bus a. Apply fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RT Z (300325) 69.0 kV to 2ELM (300327) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT607 | 3 Phase fault on 2ELM 69.000 (300327) 69 kV Bus a. Apply fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT608 | 3 Phase fault on 2ROSEHL 69.000 (300334) 69 kV Bus a. Apply fault at the 2ROSEHL 69.000 (300334) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROSEHL (300334) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT609 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT610 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT611 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT612 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT613 | 3 Phase fault on 5GRAVOIB1 161.00 (300555) 161 kV Bus a. Apply fault at the 5GRAVOIB1 161.00 (300555) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRAVOIB1 (300555) 161.0 kV to 5GRAVOIB2 (300574) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT614 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT615 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT616 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT617 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT618 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT619 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT620 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT621 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT622 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT623 | 3 Phase fault on 2REEDS 69.000 (300751) 69 kV Bus a. Apply fault at the 2REEDS 69.000 (300751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT624 | 3 Phase fault on 2ELKTON 69.000 (300773) 69 kV Bus a. Apply fault at the 2ELKTON 69.000 (300773) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELKTON (300773) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT625 | 3 Phase fault on 2KNOBBY 69.000 (300780) 69 kV Bus a. Apply fault at the 2KNOBBY 69.000 (300780) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KNOBBY (300780) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT626 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT627 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT628 | 3 Phase fault on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT629 | 3 Phase fault on 2ICONTP 69.000 (300809) 69 kV Bus a. Apply fault at the 2ICONTP 69.000 (300809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ICONTP (300809) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT630 | 3 Phase fault on 2OSCEOL 69.000 (300811) 69 kV Bus a. Apply fault at the 2OSCEOL 69.000 (300811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT631 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT632 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT633 | 3 Phase fault on 2AID 69.000 (301190) 69 kV Bus a. Apply fault at the 2AID 69.000 (301190) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AID (301190) 69.0 kV to 2AIDJCT (301191) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT634 | 3 Phase fault on 2AIDJCT 69.000 (301191) 69 kV Bus a. Apply fault at the 2AIDJCT 69.000 (301191) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AIDJCT (301191) 69.0 kV to 2PUXICO (301221) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT635 | 3 Phase fault on 2AIDJCT 69.000 (301191) 69 kV Bus a. Apply fault at the 2AIDJCT 69.000 (301191) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AIDJCT (301191) 69.0 kV to 2BLOOMF (301237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT636 | 3 Phase fault on 2ARAB 69.000 (301192) 69 kV Bus a. Apply fault at the 2ARAB 69.000 (301192) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ARAB (301192) 69.0 kV to 2ADVANC (301235) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT637 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2FISK (301205) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT638 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2PUXICO (301221) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT639 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2ROMBAR (301223) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT640 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2WAPELO (301226) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT641 | 3 Phase fault on 2FISK 69.000 (301205) 69 kV Bus a. Apply fault at the 2FISK 69.000 (301205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISK (301205) 69.0 kV to 2DUDLEY (301228) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT642 | 3 Phase fault on 2MALDEN 69.000 (301214) 69 kV Bus a. Apply fault at the 2MALDEN 69.000 (301214) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALDEN (301214) 69.0 kV to 2PARMA (301250) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT643 | 3 Phase fault on 2ROMBAR 69.000 (301223) 69 kV Bus a. Apply fault at the 2ROMBAR 69.000 (301223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROMBAR (301223) 69.0 kV to 2PBNORTH (301412) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT644 | 3 Phase fault on 2ADVANC 69.000 (301235) 69 kV Bus a. Apply fault at the 2ADVANC 69.000 (301235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ADVANC (301235) 69.0 kV to 2ARDEOLA (301257) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT645 | 3 Phase fault on 2ADVANC 69.000 (301235) 69 kV Bus a. Apply fault at the 2ADVANC 69.000 (301235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ADVANC (301235) 69.0 kV to 2WHTWTR (301279) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT646 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2DOGWOD (301239) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT647 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2LILBRN (301246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT648 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2WOLFIS (301252) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT649 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2WYATT (301253) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT650 | 3 Phase fault on 2BLOOMF 69.000 (301237) 69 kV Bus a. Apply fault at the 2BLOOMF 69.000 (301237) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLOOMF (301237) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT651 | 3 Phase fault on 2DOGWOD 69.000 (301239) 69 kV Bus a. Apply fault at the 2DOGWOD 69.000 (301239) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DOGWOD (301239) 69.0 kV to 2MATHWS (301247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT652 | 3 Phase fault on 2DOGWOD 69.000 (301239) 69 kV Bus a. Apply fault at the 2DOGWOD 69.000 (301239) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DOGWOD (301239) 69.0 kV to 2MINER (301254) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT653 | 3 Phase fault on 2FRISCO 69.000 (301240) 69 kV Bus a. Apply fault at the 2FRISCO 69.000 (301240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRISCO (301240) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT654 | 3 Phase fault on 2FRISCO 69.000 (301240) 69 kV Bus a. Apply fault at the 2FRISCO 69.000 (301240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRISCO (301240) 69.0 kV to 2PARMA (301250) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT655 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to 2IDALMA (301244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT656 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT657 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to 2ARDEOLA (301257) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT658 | 3 Phase fault on 2IDALMA 69.000 (301244) 69 kV Bus a. Apply fault at the 2IDALMA 69.000 (301244) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALMA (301244) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT659 | 3 Phase fault on 2KELLY 69.000 (301245) 69 kV Bus a. Apply fault at the 2KELLY 69.000 (301245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KELLY (301245) 69.0 kV to 2VANDSR (301251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT660 | 3 Phase fault on 2LILBRN 69.000 (301246) 69 kV Bus a. Apply fault at the 2LILBRN 69.000 (301246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LILBRN (301246) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT661 | 3 Phase fault on 2MATHWS 69.000 (301247) 69 kV Bus a. Apply fault at the 2MATHWS 69.000 (301247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MATHWS (301247) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT662 | 3 Phase fault on 2MOREHS 69.000 (301248) 69 kV Bus a. Apply fault at the 2MOREHS 69.000 (301248) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOREHS (301248) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT663 | 3 Phase fault on 2MOREJT 69.000 (301249) 69 kV Bus a. Apply fault at the 2MOREJT 69.000 (301249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOREJT (301249) 69.0 kV to 2VANDSR (301251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT664 | 3 Phase fault on 2PARMA 69.000 (301250) 69 kV Bus a. Apply fault at the 2PARMA 69.000 (301250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PARMA (301250) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT665 | 3 Phase fault on 2VANDSR 69.000 (301251) 69 kV Bus a. Apply fault at the 2VANDSR 69.000 (301251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VANDSR (301251) 69.0 kV to 2MORLEY (301255) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT666 | 3 Phase fault on 2AVONKN 69.000 (301285) 69 kV Bus a. Apply fault at the 2AVONKN 69.000 (301285) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AVONKN (301285) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT667 | 3 Phase fault on 2AVONKN 69.000 (301285) 69 kV Bus a. Apply fault at the 2AVONKN 69.000 (301285) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AVONKN (301285) 69.0 kV to 2GIDJCT (301293) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT668 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT669 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT670 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT671 | 3 Phase fault on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT672 | 3 Phase fault on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOKC (301522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT673 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT674 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT675 | 3 Phase fault on 5CHARLSTN 161.00 (344333) 161 kV Bus a. Apply fault at the 5CHARLSTN 161.00 (344333) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHARLSTN (344333) 161.0 kV to 5MINER 1 (345203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT676 | 3 Phase fault on 5KELSO 1 161.00 (344847) 161 kV Bus a. Apply fault at the 5KELSO 1 161.00 (344847) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KELSO 1 (344847) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT677 | 3 Phase fault on 5KELSO 1 161.00 (344847) 161 kV Bus a. Apply fault at the 5KELSO 1 161.00 (344847) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KELSO 1 (344847) 161.0 kV to 5MINER 1 (345203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT678 | 3 Phase fault on 5KELSO 1 161.00 (344847) 161 kV Bus a. Apply fault at the 5KELSO 1 161.00 (344847) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KELSO 1 (344847) 161.0 kV to 5VIAD_TP (345891) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT679 | 3 Phase fault on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 1 (344848) 345.0 kV to 7KELSO 2 (344849) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT680 | 3 Phase fault on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 1 (344848) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT681 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT682 | 3 Phase fault on 5MINER 1 161.00 (345203) 161 kV Bus a. Apply fault at the 5MINER 1 161.00 (345203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MINER 1 (345203) 161.0 kV to 5MINER 2 (345204) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT683 | 3 Phase fault on 5MINER 1 161.00 (345203) 161 kV Bus a. Apply fault at the 5MINER 1 161.00 (345203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MINER 1 (345203) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT684 | 3 Phase fault on 5RCHLND 1 161.00 (345588) 161 kV Bus a. Apply fault at the 5RCHLND 1 161.00 (345588) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RCHLND 1 (345588) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT685 | 3 Phase fault on 5STODDARD 1 161.00 (345790) 161 kV Bus a. Apply fault at the 5STODDARD 1 161.00 (345790) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STODDARD 1 (345790) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT686 | 3 Phase fault on 5VIAD_TP 161.00 (345891) 161 kV Bus a. Apply fault at the 5VIAD_TP 161.00 (345891) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5VIAD_TP (345891) 161.0 kV to 5VIADUCT 3 (345892) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT687 | 3 Phase fault on 7W_FRFT_E 345.00 (346992) 345 kV Bus a. Apply fault at the 7W_FRFT_E 345.00 (346992) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7W_FRFT_E (346992) 345.0 kV to 7SHAWNEE FP (360002) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT688 | 3 Phase fault on 7JOPPA TS 345.00 (347325) 345 kV Bus a. Apply fault at the 7JOPPA TS 345.00 (347325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JOPPA TS (347325) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT689 | 3 Phase fault on 5JOPPA S TP1161.00 (347334) 161 kV Bus a. Apply fault at the 5JOPPA S TP1161.00 (347334) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA S TP1 (347334) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at Silk (505432) and New Madrid (300006, 300007) generating sites following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT690 | 3 Phase fault on 5JOPPA T3 161.00 (347335) 161 kV Bus a. Apply fault at the 5JOPPA T3 161.00 (347335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA T3 (347335) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at Silk (505432) and New Madrid (300006, 300007) generating sites following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT691 | 3 Phase fault on 5MARION S 161.00 (347523) 161 kV Bus a. Apply fault at the 5MARION S 161.00 (347523) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARION S (347523) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT692 | 3 Phase fault on 7COMM 345.00 (348287) 345 kV Bus a. Apply fault at the 7COMM 345.00 (348287) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7COMM (348287) 345.0 kV to 7JORD (348289) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT693 | 3 Phase fault on 7JORD 345.00 (348289) 345 kV Bus a. Apply fault at the 7JORD 345.00 (348289) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JORD (348289) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT694 | 3 Phase fault on 7MASS 345.00 (348294) 345 kV Bus a. Apply fault at the 7MASS 345.00 (348294) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MASS (348294) 345.0 kV to 7SHAWNEE FP (360002) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT695 | 3 Phase fault on 5NAUVOO TN 161.00 (360479) 161 kV Bus a. Apply fault at the 5NAUVOO TN 161.00 (360479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NAUVOO TN (360479) 161.0 kV to 5RIDGELY TN (360521) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT696 | 3 Phase fault on 5RIDGELY TN 161.00 (360521) 161 kV Bus a. Apply fault at the 5RIDGELY TN 161.00 (360521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RIDGELY TN (360521) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT697 | 3 Phase fault on 5TIPTONVL TN161.00 (361261) 161 kV Bus a. Apply fault at the 5TIPTONVL TN161.00 (361261) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TIPTONVL TN (361261) 161.0 kV to 5POLK TP (361596) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT698 | 3 Phase fault on 5TROY TN 161.00 (361422) 161 kV Bus a. Apply fault at the 5TROY TN 161.00 (361422) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TROY TN (361422) 161.0 kV to 5POLK TP (361596) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT699 | 3 Phase fault on 5POLK TP 161.00 (361596) 161 kV Bus a. Apply fault at the 5POLK TP 161.00 (361596) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5POLK TP (361596) 161.0 kV to 5POLK (361597) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT700 | 3 Phase fault on N MADRD5 161.00 (505400) 161 kV Bus a. Apply fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD5 (505400) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT701 | 3 Phase fault on N MADRD2 69.000 (505402) 69 kV Bus a. Apply fault at the N MADRD2 69.000 (505402) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT702 | 3 Phase fault on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT703 | 3 Phase fault on PIGGOTT2 69.000 (505406) 69 kV Bus a. Apply fault at the PIGGOTT2 69.000 (505406) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIGGOTT2 (505406) 69.0 kV to KENNETT2 (505408) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT704 | 3 Phase fault on SIKETAP5 161.00 (505427) 161 kV Bus a. Apply fault at the SIKETAP5 161.00 (505427) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKETAP5 (505427) 161.0 kV to SIKE SW5 (505433) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT705 | 3 Phase fault on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKESTN5 (505428) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT706 | 3 Phase fault on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDALIA 5 (505434) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT707 | 3 Phase fault on POP BLF5 161.00 (505438) 161 kV Bus a. Apply fault at the POP BLF5 161.00 (505438) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POP BLF5 (505438) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT708 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT709 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT710 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT711 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT712 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT713 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT714 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT715 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT716 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT717 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT719 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT720 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT721 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT722 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT723 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT724 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT725 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT726 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT727 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT728 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT729 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT730 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT731 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT732 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT733 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT734 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT735 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT736 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT737 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT738 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT739 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT740 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT741 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT742 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT743 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT744 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT745 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT746 | 3 Phase fault on WACO S 4 138.00 (533071) 138 kV Bus a. Apply fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT747 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT748 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT749 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT750 | 3 Phase fault on FREESTATE3 115.00 (533257) 115 kV Bus a. Apply fault at the FREESTATE3 115.00 (533257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREESTATE3 (533257) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT751 | 3 Phase fault on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT752 | 3 Phase fault on KSU W 3 115.00 (533333) 115 kV Bus a. Apply fault at the KSU W 3 115.00 (533333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSU W 3 (533333) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT753 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT754 | 3 Phase fault on AEC 3 115.00 (533361) 115 kV Bus a. Apply fault at the AEC 3 115.00 (533361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT755 | 3 Phase fault on BERG 3 115.00 (533367) 115 kV Bus a. Apply fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT756 | 3 Phase fault on BERG 3 115.00 (533367) 115 kV Bus a. Apply fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT757 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT758 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT759 | 3 Phase fault on ARKVAL 3 115.00 (533411) 115 kV Bus a. Apply fault at the ARKVAL 3 115.00 (533411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT760 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT761 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT762 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT763 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT764 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT765 | 3 Phase fault on FLORAL 2 69.000 (533545) 69 kV Bus a. Apply fault at the FLORAL 2 69.000 (533545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORAL 2 (533545) 69.0 kV to FLORALJ2 (533546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT766 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT767 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to TIMBER 2 (533557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT768 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT769 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT770 | 3 Phase fault on BUTLERN2 69.000 (533583) 69 kV Bus a. Apply fault at the BUTLERN2 69.000 (533583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERN2 (533583) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT771 | 3 Phase fault on MIDIANW2 69.000 (533597) 69 kV Bus a. Apply fault at the MIDIANW2 69.000 (533597) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIANW2 (533597) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT772 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT773 | 3 Phase fault on CGENSUB2 69.000 (533662) 69 kV Bus a. Apply fault at the CGENSUB2 69.000 (533662) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CGENSUB2 (533662) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT774 | 3 Phase fault on ALTAMNT2 69.000 (533671) 69 kV Bus a. Apply fault at the ALTAMNT2 69.000 (533671) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT775 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODESH2 (533699) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT776 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT777 | 3 Phase fault on CHERRYV2 69.000 (533679) 69 kV Bus a. Apply fault at the CHERRYV2 69.000 (533679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYV2 (533679) 69.0 kV to CHRYJCT2 (533680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT778 | 3 Phase fault on YELLOWJ2 69.000 (533692) 69 kV Bus a. Apply fault at the YELLOWJ2 69.000 (533692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YELLOWJ2 (533692) 69.0 kV to NEW ALB2 (533701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT779 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT780 | 3 Phase fault on NEODJCT2 69.000 (533700) 69 kV Bus a. Apply fault at the NEODJCT2 69.000 (533700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEODJCT2 (533700) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT781 | 3 Phase fault on NEW ALB2 69.000 (533701) 69 kV Bus a. Apply fault at the NEW ALB2 69.000 (533701) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEW ALB2 (533701) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT782 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT783 | 3 Phase fault on LITCH N2 69.000 (533765) 69 kV Bus a. Apply fault at the LITCH N2 69.000 (533765) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT784 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT785 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT786 | 3 Phase fault on RIPLEYE2 69.000 (533859) 69 kV Bus a. Apply fault at the RIPLEYE2 69.000 (533859) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIPLEYE2 (533859) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT787 | 3 Phase fault on EAST SUB 2 69.000 (533990) 69 kV Bus a. Apply fault at the EAST SUB 2 69.000 (533990) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT788 | 3 Phase fault on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT789 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT790 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT791 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT792 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT793 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT794 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT795 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT796 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT797 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT798 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT799 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT800 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT801 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT802 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT803 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT804 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT805 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT806 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT807 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT808 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT809 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT810 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT811 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT812 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT813 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT814 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to POPE (541349) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT815 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT816 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT817 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT818 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT819 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT820 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT821 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT822 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT823 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT824 | 3 Phase fault on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT825 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT826 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT827 | 3 Phase fault on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT828 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT829 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT830 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT831 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT832 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT833 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT834 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT835 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to BRADDYVILLE5 (635038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT836 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT837 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT838 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT839 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT840 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT841 | 3 Phase fault on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT842 | 3 Phase fault on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to ALABAMA5 (541354) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT843 | 3 Phase fault on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT844 | 3 Phase fault on IND PRK5 161.00 (541256) 161 kV Bus a. Apply fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT845 | 3 Phase fault on COOK 5 161.00 (541257) 161 kV Bus a. Apply fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT846 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT847 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT848 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT849 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT850 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT851 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT852 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT853 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT854 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT855 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT856 | 3 Phase fault on IATAN5 161.00 (541350) 161 kV Bus a. Apply fault at the IATAN5 161.00 (541350) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT857 | 3 Phase fault on AMOIL 2 69.000 (541358) 69 kV Bus a. Apply fault at the AMOIL 2 69.000 (541358) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOIL 2 (541358) 69.0 kV to MIDWY1 2 (541368) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT858 | 3 Phase fault on MIDWY1 2 69.000 (541368) 69 kV Bus a. Apply fault at the MIDWY1 2 69.000 (541368) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWY1 2 (541368) 69.0 kV to MDWYTP 2 (541389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT859 | 3 Phase fault on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAY_5 (541369) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT860 | 3 Phase fault on SAVANAH2 69.000 (541391) 69 kV Bus a. Apply fault at the SAVANAH2 69.000 (541391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAVANAH2 (541391) 69.0 kV to EDMOND2 (541392) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT861 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT862 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT863 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT864 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT865 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT866 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT867 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM_CAP5 (542947) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT868 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT869 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN_CAP5 (542950) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT870 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT871 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT872 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT873 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT874 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT875 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT876 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT877 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT878 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT879 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT880 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT881 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT882 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT883 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT884 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT885 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT886 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT887 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT888 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT889 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT890 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT891 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT892 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT893 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT894 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT895 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT896 | 3 Phase fault on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT897 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT898 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT899 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT900 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT901 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT902 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT903 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT904 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT905 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT906 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT907 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT908 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT909 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT910 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT911 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT912 | 3 Phase fault on LVISTA 5 161.00 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 161.00 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT913 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT914 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT915 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT916 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT917 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT918 | 3 Phase fault on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT919 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT920 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT921 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT922 | 3 Phase fault on CLAYCM15 161.00 (543022) 161 kV Bus a. Apply fault at the CLAYCM15 161.00 (543022) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLAYCM15 (543022) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT923 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT924 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT925 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT926 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT927 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT928 | 3 Phase fault on BRKRIDG5 161.00 (543033) 161 kV Bus a. Apply fault at the BRKRIDG5 161.00 (543033) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKRIDG5 (543033) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT929 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT930 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT931 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT932 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT933 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT934 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT935 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT936 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT937 | 3 Phase fault on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LENEXA 5 (543038) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT938 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT939 | 3 Phase fault on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT940 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT941 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT942 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT943 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT944 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT945 | 3 Phase fault on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT946 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT947 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT948 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT949 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT950 | 3 Phase fault on WEB105 2 69.000 (547431) 69 kV Bus a. Apply fault at the WEB105 2 69.000 (547431) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB105 2 (547431) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT951 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT952 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT953 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT954 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT955 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT956 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT957 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT958 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT959 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT960 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT961 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT962 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT963 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT964 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT965 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT966 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT967 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT968 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT969 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT970 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT971 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT972 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT973 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT974 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT975 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT976 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT977 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT978 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT979 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT980 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT981 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT982 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT983 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT984 | 3 Phase fault on COOPER_602 869.000 (640143) 69 kV Bus a. Apply fault at the COOPER_602 869.000 (640143) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT985 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT986 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT987 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT988 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT562 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. Present in the base case as well. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT990 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT991 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT992 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT993 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT994 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT995 | 3 Phase fault on GI94_POI 345.00 (709400) 345 kV Bus a. Apply fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT996 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5ESSEX (300075) 161.0 kV to 7ESSEX (300038) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT997 | 3 Phase fault on 7STFRAN 345.00 (300048) 345 kV Bus a. Apply fault at the 7STFRAN 345.00 (300048) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5STFRNB3 (300116) 161.0 kV to 7STFRAN (300048) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT998 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT999 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1000 | 3 Phase fault on 5FAIRPTB2 161.00 (300076) 161 kV Bus a. Apply fault at the 5FAIRPTB2 161.00 (300076) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRPT (300249) 69.0 kV to 5FAIRPTB2 (300076) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1001 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1002 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1003 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1004 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1005 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1006 | 3 Phase fault on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 5OSCEOL (301040) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1007 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1008 | 3 Phase fault on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1009 | 3 Phase fault on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1010 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEYCRK (301401) 69.0 kV to 5TURKEYCRK (301370) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1011 | 3 Phase fault on 8WNEWMADRID 500.00 (301406) 500 kV Bus a. Apply fault at the 8WNEWMADRID 500.00 (301406) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1012 | 3 Phase fault on 8NEWMADXF34 500.00 (301528) 500 kV Bus a. Apply fault at the 8NEWMADXF34 500.00 (301528) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMADXF34 (301529) 345.0 kV to 8NEWMADXF34 (301528) 500.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1013 | 3 Phase fault on 8NEWMADXF34 500.00 (301528) 500 kV Bus a. Apply fault at the 8NEWMADXF34 500.00 (301528) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMADXF34 (301529) 345.0 kV to 8NEWMADXF34 (301528) 500.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1014 | 3 Phase fault on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5NEWMADXF12 (301531) 161.0 kV to 7NEWMADXF12 (301530) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1015 | 3 Phase fault on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5NEWMADXF12 (301531) 161.0 kV to 7NEWMADXF12 (301530) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1016 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 5DELL% (338185) 161.0 kV to 1DELL1 (338183) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1017 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 5DELL% (338185) 161.0 kV to 1DELL2 (338184) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1018 | 3 Phase fault on 5JIM HILL% 161.00 (338202) 161 kV Bus a. Apply fault at the 5JIM HILL% 161.00 (338202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JIM HILL% (338202) 161.0 kV to 3JIM HILL! (338230) 115.0 kV to 1JIM HILL (338209) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1019 | 3 Phase fault on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 1 (344848) 345.0 kV to 5KELSO 1 (344847) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1020 | 3 Phase fault on 7JOPPA TS 345.00 (347325) 345 kV Bus a. Apply fault at the 7JOPPA TS 345.00 (347325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JOPPA TS (351003) 161.0 kV to 7JOPPA TS (347325) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1021 | 3 Phase fault on 7JORD 345.00 (348289) 345 kV Bus a. Apply fault at the 7JORD 345.00 (348289) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JORD (348289) 345.0 kV to 4JORD (348292) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1022 | 3 Phase fault on 7MASS 345.00 (348294) 345 kV Bus a. Apply fault at the 7MASS 345.00 (348294) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MASS (348294) 345.0 kV to 5MASS (348295) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1023 | 3 Phase fault on 8SHAWNEE FP 500.00 (360001) 500 kV Bus a. Apply fault at the 8SHAWNEE FP 500.00 (360001) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHAWNEE FP (360001) 500.0 kV to 7SHAWNEE FP (360002) 345.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1024 | 3 Phase fault on CENTR H5 161.00 (505416) 161 kV Bus a. Apply fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X1 1 (505417) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1025 | 3 Phase fault on CENTR H5 161.00 (505416) 161 kV Bus a. Apply fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X2 1 (505419) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1026 | 3 Phase fault on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKESTN5 (505428) 161.0 kV to SIKESTN2 (505430) 69.0 kV to SIK X1 1 (505429) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1027 | 3 Phase fault on SIKE SW5 161.00 (505433) 161 kV Bus a. Apply fault at the SIKE SW5 161.00 (505433) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKE SW5 (505433) 161.0 kV to SIKE SW2 (505423) 69.0 kV to SIK X2 1 (505431) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1028 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1029 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1030 | 3 Phase fault on MOORLND4 138.00 (520999) 138 kV Bus a. Apply fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 (520999) 138.0 kV to MOORLND2 (520995) 69.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1031 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1032 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1033 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1034 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1035 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1036 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1037 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1038 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1039 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1040 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1041 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1042 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1043 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1044 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1045 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1046 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1047 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1048 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1049 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1050 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1051 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1052 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1053 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1054 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1055 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1056 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1057 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1058 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1059 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1060 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to NMANHT3 (533347) 115.0 kV to NMANHX1 (532901) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1061 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1062 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1063 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1064 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1065 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1066 | 3 Phase fault on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1067 | 3 Phase fault on TECHILL5 161.00 (532920) 161 kV Bus a. Apply fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1068 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1069 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1070 | 3 Phase fault on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1071 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1072 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1073 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1074 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1075 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1076 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1077 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1078 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1079 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1080 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1081 | 3 Phase fault on 17TH 4 138.00 (533064) 138 kV Bus a. Apply fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1082 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1083 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to ARNOLD 2 (533471) 69.0 kV to ARNOLD 1 (533449) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1084 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to NCTYSVC2 (533505) 69.0 kV to CITIES 1 (533453) 3.9 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1085 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1086 | 3 Phase fault on HEC 3 115.00 (533419) 115 kV Bus a. Apply fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1087 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1088 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1089 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1090 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1091 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1092 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1093 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1094 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1095 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1096 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1097 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 2 (533742) 69.0 kV to MOUND 4 (533013) 138.0 kV to MOUND1X1 (533095) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1098 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1099 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1100 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1101 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1102 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1103 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1104 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1105 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1106 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1107 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1108 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1109 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1110 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY2 (541287) 69.0 kV to MARTCTY5 (541210) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1111 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1112 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1113 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1114 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1115 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1116 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1117 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1118 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1119 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to MRVL#1 (541378) 69.0 kV to MARYVIL11 (541519) 13.2 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1120 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to MRVL#2 (541359) 69.0 kV to MARYVIL21 (541520) 13.2 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1121 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to BELTONS5 (541340) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1122 | 3 Phase fault on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1123 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1124 | 3 Phase fault on EDMOND5 161.00 (541355) 161 kV Bus a. Apply fault at the EDMOND5 161.00 (541355) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDMOND5 (541355) 161.0 kV to EDMOND2 (541392) 69.0 kV to EDMOND-T (541522) 13.1 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1125 | 3 Phase fault on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAY_5 (541369) 161.0 kV to MIDWY1 2 (541368) 69.0 kV to MIDWY-T1 (541521) 13.2 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1126 | 3 Phase fault on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAY_5 (541369) 161.0 kV to MIDWY2 2 (541390) 69.0 kV to MIDWY-T2 (541393) 13.2 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1127 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1128 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1129 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1130 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1131 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1132 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1133 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1134 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1135 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1136 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1137 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1138 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1139 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1140 | 3 Phase fault on IATAN 7 345.00 (542982) 345 kV Bus a. Apply fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1141 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1142 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1143 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1144 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1145 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1146 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1147 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1148 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1149 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1150 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1151 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1152 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1153 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1154 | 3 Phase fault on 5NEWMADCP 161.00 (301405) 161 kV Bus a. Apply fault at the 5NEWMADCP 161.00 (301405) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMADCP (301405) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1155 | 3 Phase fault on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALDEN 2 (505404) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1156 | 3 Phase fault on PIGGOTT2 69.000 (505406) 69 kV Bus a. Apply fault at the PIGGOTT2 69.000 (505406) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIGGOTT2 (505406) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1157 | 3 Phase fault on KENNETT2 69.000 (505408) 69 kV Bus a. Apply fault at the KENNETT2 69.000 (505408) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENNETT2 (505408) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1158 | 3 Phase fault on PARAGLD2 69.000 (505414) 69 kV Bus a. Apply fault at the PARAGLD2 69.000 (505414) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGLD2 (505414) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT1159 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT1 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT2 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT3 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT4 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT5 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT6 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT7 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT8 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT9 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT10 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT11 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT12 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT13 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT14 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT15 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT16 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT17 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT18 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT19 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT20 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT21 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT22 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT23 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT24 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT25 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT26 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT27 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT28 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT29 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT30 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT31 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT32 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT33 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT34 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT35 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT36 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT37 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT38 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT39 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT40 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT41 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT42 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT43 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT44 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT45 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT46 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT47 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT48 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT49 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT50 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_REGIONAL_FAULT51 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT1 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.4. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.5. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.6. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.7. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.8. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.9. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.10. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.11. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.12. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding #1 b.13. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 b.14. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.15. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding #1 b.16. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 b.17. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT2 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 b.3. LITCH 5 (532932) 161.0 kV to LITCH N2 (533765) 69.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 b.4. LITCH 5 (532932) 161.0 kV to LITCH S2 (533766) 69.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT3 | Single Phase Fault with Stuck Breaker on 29TH 4 138.00 (533024) 138 kV Bus a. Apply Fault at the 29TH 4 138.00 (533024) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT4 | Single Phase Fault with Stuck Breaker on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT5 | Single Phase Fault with Stuck Breaker on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply Fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT6 | Single Phase Fault with Stuck Breaker on MAIZE 4 138.00 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 138.00 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT7 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. TIOGA 4 (532996) 138.0 kV to TIOGA 2 (533646) 69.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT8 | Single Phase Fault with Stuck Breaker on 6 GOLDN3 115.00 (533177) 115 kV Bus a. Apply Fault at the 6 GOLDN3 115.00 (533177) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT9 | Single Phase Fault with Stuck Breaker on AEC 3 115.00 (533361) 115 kV Bus a. Apply Fault at the AEC 3 115.00 (533361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AEC 3 (533361) 115.0 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.2. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.4. AEC 3 (533361) 115.0 kV to AEC W1 (533887) 34.5 kV Two Winding #1 b.5. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT10 | Single Phase Fault with Stuck Breaker on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply Fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.3. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT11 | Single Phase Fault with Stuck Breaker on INDIANH3 115.00 (533166) 115 kV Bus a. Apply Fault at the INDIANH3 115.00 (533166) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.3. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT12 | Single Phase Fault with Stuck Breaker on LEC U4 3 115.00 (533249) 115 kV Bus a. Apply Fault at the LEC U4 3 115.00 (533249) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 (532662) 14.4 kV to LEC U4 3 (533249) 115.0 kV Two Winding #1 b.2. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.3. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT13 | Single Phase Fault with Stuck Breaker on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply Fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT14 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. MORRIS 3 (533305) 115.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT15 | Single Phase Fault with Stuck Breaker on SMOKYHLLS3 115.00 (533378) 115 kV Bus a. Apply Fault at the SMOKYHLLS3 115.00 (533378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 b.2. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT16 | Single Phase Fault with Stuck Breaker on S ALMA 3 115.00 (533339) 115 kV Bus a. Apply Fault at the S ALMA 3 115.00 (533339) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 b.2. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT17 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT18 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT19 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT20 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT21 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT22 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT23 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT24 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT25 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT26 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT27 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT28 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT29 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT30 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT31 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT32 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT33 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT34 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT35 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT36 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT37 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT38 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT39 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT40 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT41 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT42 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT43 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT44 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT45 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT46 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT47 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT48 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT49 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT50 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT51 | Single Phase Fault with Stuck Breaker on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.3. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT52 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT53 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT54 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT55 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT56 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U1 (532651) 26.0 kV to JEC 6 (532852) 230.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT57 | Single Phase Fault with Stuck Breaker on JEC 6 230.00 (532852) 230 kV Bus a. Apply Fault at the JEC 6 230.00 (532852) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U1 (532651) 26.0 kV to JEC 6 (532852) 230.0 kV Two Winding #1 b.2. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT58 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT59 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT60 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT61 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT62 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT63 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT64 | Single Phase Fault with Stuck Breaker on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply Fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT65 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT66 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT67 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT68 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT69 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT70 | Single Phase Fault with Stuck Breaker on NMANHT6 230.00 (532865) 230 kV Bus a. Apply Fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.2. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 b.3. NMANHT6 (532865) 230.0 kV to NMANHT3 (533347) 115.0 kV to NMANHX1 (532901) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT71 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT72 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT73 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT74 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT75 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT76 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT77 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT78 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT79 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT80 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT81 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT82 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT83 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT84 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.3. FRANKLIN5 (532938) 161.0 kV to FRANKLIN2 (533876) 69.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT85 | Single Phase Fault with Stuck Breaker on 17TH 4 138.00 (533064) 138 kV Bus a. Apply Fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.3. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT86 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.6. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.8. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT87 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.6. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT88 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT89 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT90 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT91 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT92 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT93 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT94 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT95 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.4. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT96 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT97 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT98 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESW1 1 (533080) 13.2 kV to CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.2. CRESW2 1 (533081) 13.2 kV to CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.3. CRESWLN4 (532981) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT99 | Single Phase Fault with Stuck Breaker on SLATECRK4 138.00 (533070) 138 kV Bus a. Apply Fault at the SLATECRK4 138.00 (533070) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. CRESWLN4 (532981) 138.0 kV to SLATECRK4 (533070) 138.0 kV Transmission Circuit #1 b.3. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.4. SLATEXFMR1 (533139) 34.5 kV to SLATEGSU1 (533140) 34.5 kV Transmission Circuit #1 b.5. SLATEGEN1 (533141) 0.7 kV to SLATEGSU1 (533140) 34.5 kV Two Winding #1 b.6. SLATECRK4 (533070) 138.0 kV to SLATEXFMR1 (533139) 34.5 kV to SLATETV1 (533142) 13.2 kV Three Winding #1 b.7. CRESW1 1 (533080) 13.2 kV to CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT100 | Single Phase Fault with Stuck Breaker on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply Fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.4. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.7. MIDLTNT4 (514804) 138.0 kV to GEN-2016-071 (587480) 138.0 kV Transmission Circuit #1 b.8. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.9. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT101 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.4. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.7. MIDLTNT4 (514804) 138.0 kV to GEN-2016-071 (587480) 138.0 kV Transmission Circuit #1 b.8. CRESW2 1 (533081) 13.2 kV to CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.9. CRESWLN4 (532981) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT102 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.5. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT103 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.6. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT104 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.6. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT105 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT106 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT107 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT108 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT109 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT110 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT111 | Single Phase Fault with Stuck Breaker on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEC DG 1 (532730) 4.2 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT112 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT113 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT114 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT115 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT116 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.5. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 b.6. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT117 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT118 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT119 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT120 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT121 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.6. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT122 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. NEAST3X1 (533110) 11.3 kV to NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT123 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.4. NEAST5X1 (533111) 13.2 kV to NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT124 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.8. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.10. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT125 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT126 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT127 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT128 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.3. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.4. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.5. SUMNER 4 (532984) 138.0 kV to GEN-2017-121 (761838) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT129 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT130 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT131 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT132 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT133 | Single Phase Fault with Stuck Breaker on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT134 | Single Phase Fault with Stuck Breaker on 17&FAIR3 115.00 (533175) 115 kV Bus a. Apply Fault at the 17&FAIR3 115.00 (533175) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 b.2. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.3. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 17&FAIR3 (533175) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT135 | Single Phase Fault with Stuck Breaker on FORBES 3 115.00 (533157) 115 kV Bus a. Apply Fault at the FORBES 3 115.00 (533157) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORBES 3 (533157) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.2. FORBES 3 (533157) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.3. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.4. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT136 | Single Phase Fault with Stuck Breaker on 41CALIF3 115.00 (533160) 115 kV Bus a. Apply Fault at the 41CALIF3 115.00 (533160) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.3. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT137 | Single Phase Fault with Stuck Breaker on FMC 3 115.00 (533241) 115 kV Bus a. Apply Fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.2. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 b.3. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT138 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.3. 87TH 1X1 (532818) 13.8 kV to 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT139 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT140 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 b.2. AUBURN 3 (533151) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT141 | Single Phase Fault with Stuck Breaker on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. AUBURN 1 (532880) 14.4 kV to AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT142 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 1 (532880) 14.4 kV to AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV Three Winding #1 b.2. AUBURN 3 (533151) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT143 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.3. AUBURN 3 (533151) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT144 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT145 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT146 | Single Phase Fault with Stuck Breaker on CLAYCTR3 115.00 (533323) 115 kV Bus a. Apply Fault at the CLAYCTR3 115.00 (533323) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCSS3 (533320) 115.0 kV to CLAYCTR3 (533323) 115.0 kV Transmission Circuit #1 b.2. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT147 | Single Phase Fault with Stuck Breaker on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT148 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.4. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.5. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.6. CIRCLE 3 (533413) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT149 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT150 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.2. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.5. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT151 | Single Phase Fault with Stuck Breaker on HEC GT 3 115.00 (533421) 115 kV Bus a. Apply Fault at the HEC GT 3 115.00 (533421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.5. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT152 | Single Phase Fault with Stuck Breaker on CITIES 3 115.00 (533414) 115 kV Bus a. Apply Fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.3. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.4. CITIES 3 (533414) 115.0 kV to NCTYSVC2 (533505) 69.0 kV to CITIES 1 (533453) 3.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT153 | Single Phase Fault with Stuck Breaker on MANVILE3 115.00 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to MCPHGT4 (532705) 13.8 kV Two Winding #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT154 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to MCPHGT3 (532704) 13.8 kV Two Winding #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT155 | Single Phase Fault with Stuck Breaker on COLINE 3 115.00 (533153) 115 kV Bus a. Apply Fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.3. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.5. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT156 | Single Phase Fault with Stuck Breaker on BISMARK3 115.00 (533234) 115 kV Bus a. Apply Fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.5. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT157 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.4. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT158 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT159 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.5. HOYT 3 (533163) 115.0 kV to HOYT 7 (532765) 345.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT160 | Single Phase Fault with Stuck Breaker on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT161 | Single Phase Fault with Stuck Breaker on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT162 | Single Phase Fault with Stuck Breaker on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to N TYLER3 (533168) 115.0 kV Transmission Circuit #1 b.3. N TYLER3 (533168) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT163 | Single Phase Fault with Stuck Breaker on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply Fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHAL3 (533303) 115.0 kV to KNOB HL3 (533332) 115.0 kV Transmission Circuit #1 b.2. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. KNOB HL3 (533332) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.4. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.5. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT164 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.3. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.4. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.5. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT165 | Single Phase Fault with Stuck Breaker on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply Fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT166 | Single Phase Fault with Stuck Breaker on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply Fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 b.3. FREESTATE3 (533257) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT167 | Single Phase Fault with Stuck Breaker on STULL T3 115.00 (533270) 115 kV Bus a. Apply Fault at the STULL T3 115.00 (533270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.3. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT168 | Single Phase Fault with Stuck Breaker on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply Fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT169 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LAWHILL1 (532882) 14.4 kV to LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT170 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 b.2. LAWHILL1 (532882) 14.4 kV to LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT171 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.7. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT172 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT173 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.2. NMANHT3 (533347) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT174 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.2. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT175 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.2. NMANHT3 (533347) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT176 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHX1 (532901) 14.4 kV to NMANHT6 (532865) 230.0 kV to NMANHT3 (533347) 115.0 kV Three Winding #1 b.2. NMANHT3 (533347) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT177 | Single Phase Fault with Stuck Breaker on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply Fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.3. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.4. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT178 | Single Phase Fault with Stuck Breaker on PENTAGN3 115.00 (533261) 115 kV Bus a. Apply Fault at the PENTAGN3 115.00 (533261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.2. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.3. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.4. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.5. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT179 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. RENO 1X1 (532807) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT180 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. RENO 2X1 (532810) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT181 | Single Phase Fault with Stuck Breaker on RENO 3 115.00 (533416) 115 kV Bus a. Apply Fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT182 | Single Phase Fault with Stuck Breaker on SALINA 3 115.00 (533376) 115 kV Bus a. Apply Fault at the SALINA 3 115.00 (533376) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.3. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT183 | Single Phase Fault with Stuck Breaker on 29EVENG3 115.00 (533185) 115 kV Bus a. Apply Fault at the 29EVENG3 115.00 (533185) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT184 | Single Phase Fault with Stuck Breaker on S GAGEE3 115.00 (533178) 115 kV Bus a. Apply Fault at the S GAGEE3 115.00 (533178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.4. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT185 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.3. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.4. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.5. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT186 | Single Phase Fault with Stuck Breaker on SWLWRNC3 115.00 (533271) 115 kV Bus a. Apply Fault at the SWLWRNC3 115.00 (533271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.8. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT187 | Single Phase Fault with Stuck Breaker on SWLWRNC3 115.00 (533271) 115 kV Bus a. Apply Fault at the SWLWRNC3 115.00 (533271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.5. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT188 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.8. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.9. AEC E1 (533886) 34.5 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.10. AEC E1 (533886) 34.5 kV to AEC W1 (533887) 34.5 kV Transmission Circuit #z1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT189 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.4. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.5. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.7. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.8. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.10. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.11. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT190 | Single Phase Fault with Stuck Breaker on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.5. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT191 | Single Phase Fault with Stuck Breaker on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT192 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.3. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.4. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.5. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.6. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.7. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.8. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT193 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.3. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.4. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.5. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.6. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT194 | Single Phase Fault with Stuck Breaker on WJCCTY 3 115.00 (533342) 115 kV Bus a. Apply Fault at the WJCCTY 3 115.00 (533342) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.3. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.5. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT195 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT196 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT197 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT198 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT199 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.6. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.7. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT200 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 b.6. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.8. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT201 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 b.5. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT202 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT203 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.7. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.8. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT204 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.5. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 b.6. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT205 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.7. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT206 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.7. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT207 | Single Phase Fault with Stuck Breaker on KSU W 3 115.00 (533333) 115 kV Bus a. Apply Fault at the KSU W 3 115.00 (533333) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KSU W 3 (533333) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #z1 b.2. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.3. MATTERS3 (533334) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT208 | Single Phase Fault with Stuck Breaker on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply Fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.5. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 b.6. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.7. MIDLADN3 (533252) 115.0 kV to MIDLAND6 (532855) 230.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT209 | Single Phase Fault with Stuck Breaker on TECHILL5 161.00 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 b.6. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILW3 (533181) 115.0 kV to TECHILL5 (532920) 161.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 b.13. TECHIL4X (533885) 12.5 kV to TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT210 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT211 | Single Phase Fault with Stuck Breaker on 5KELSO 2 161.00 (344850) 161 kV Bus a. Apply Fault at the 5KELSO 2 161.00 (344850) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CAPE GIR1 (344280) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #1 b.2. 5KELSO 1 (344847) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #z b.3. 7KELSO 2 (344849) 345.0 kV to 5KELSO 2 (344850) 161.0 kV Two Winding #2 b.4. 5KELSO 2 (344850) 161.0 kV to 5ORAN (345375) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT212 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 b.3. 5HAYTI.S% (338200) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT213 | Single Phase Fault with Stuck Breaker on 5PORTAGEVLE 161.00 (338201) 161 kV Bus a. Apply Fault at the 5PORTAGEVLE 161.00 (338201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 5STEELE! (338194) 161.0 kV to 5HAYTI.S% (338200) 161.0 kV Transmission Circuit #1 b.3. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.4. 5PORTAGEVLE (338201) 161.0 kV to 1PORTGVIL (345534) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT214 | Single Phase Fault with Stuck Breaker on 5HAYTI.S% 161.00 (338200) 161 kV Bus a. Apply Fault at the 5HAYTI.S% 161.00 (338200) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.3. 5PORTAGEVLE (338201) 161.0 kV to 1PORTGVIL (345534) 34.5 kV Two Winding #1 b.4. 1HAYTI N (344720) 34.5 kV to 5HAYTI.S% (338200) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT215 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 b.3. 5JIM HILL% (338202) 161.0 kV to 5RECTOR.N# (338689) 161.0 kV Transmission Circuit #1 b.4. 5PARAGOULD% (338204) 161.0 kV to 5HALLIDAY# (338709) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT216 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT217 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT218 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT219 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT220 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT221 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT222 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT223 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT224 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT225 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT226 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT227 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT228 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT229 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT230 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT231 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT232 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT233 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT234 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT235 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT236 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT237 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT238 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT239 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT240 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT241 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT242 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT243 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT244 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT245 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT246 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT247 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT248 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT249 | Single Phase Fault with Stuck Breaker on CAR395 5 161.00 (547485) 161 kV Bus a. Apply Fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.4. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.5. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT250 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT251 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT252 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT253 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT254 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT255 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT256 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT257 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT258 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT259 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT260 | Single Phase Fault with Stuck Breaker on CAR395 5 161.00 (547485) 161 kV Bus a. Apply Fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.3. ASB349 5 (547476) 161.0 kV to A1G349 1 (547649) 13.8 kV Two Winding #1 b.4. ASB349 5 (547476) 161.0 kV to A2G349 1 (547650) 13.8 kV Two Winding #1 b.5. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT261 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT262 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT263 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT264 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT265 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT266 | Single Phase Fault with Stuck Breaker on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply Fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT7 1 (542963) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.2. HAWCT8 1 (542964) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.3. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT267 | Single Phase Fault with Stuck Breaker on NEASTN5 161.0 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.0 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.5. NEASTN5 (543666) 161.0 kV to Load #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT268 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT269 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT270 | Single Phase Fault with Stuck Breaker on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 b.2. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.3. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT271 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT272 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT273 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT274 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT275 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT276 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT277 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT278 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT279 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 b.2. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.3. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.4. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.5. MARMTNW5 (532935) 161.0 kV to MARMATN2 (533639) 69.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT280 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.5. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.6. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.9. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT281 | Single Phase Fault with Stuck Breaker on CORONAD3 115.00 (533394) 115 kV Bus a. Apply Fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT282 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT283 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT284 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT285 | Single Phase Fault with Stuck Breaker on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply Fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 b.2. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT286 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 b.2. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 b.3. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT287 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT288 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT289 | Single Phase Fault with Stuck Breaker on CGENSUB2 69.000 (533662) 69 kV Bus a. Apply Fault at the CGENSUB2 69.000 (533662) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 b.2. CGENTAP2 (533661) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 b.3. CGENSUB2 (533662) 69.0 kV to CHANP2 2 (533664) 69.0 kV Transmission Circuit #1 b.4. CGENSUB2 (533662) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT290 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT291 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT292 | Single Phase Fault with Stuck Breaker on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT293 | Single Phase Fault with Stuck Breaker on STAGGHL3 115.00 (533341) 115 kV Bus a. Apply Fault at the STAGGHL3 115.00 (533341) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.2. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.3. PEIL 3 (533343) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT294 | Single Phase Fault with Stuck Breaker on WILDCAT3 115.00 (533345) 115 kV Bus a. Apply Fault at the WILDCAT3 115.00 (533345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.2. PEIL 3 (533343) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.3. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT295 | Single Phase Fault with Stuck Breaker on ALLEN 2 69.000 (533621) 69 kV Bus a. Apply Fault at the ALLEN 2 69.000 (533621) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.5. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT296 | Single Phase Fault with Stuck Breaker on ALLEN 2 69.000 (533621) 69 kV Bus a. Apply Fault at the ALLEN 2 69.000 (533621) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT297 | Single Phase Fault with Stuck Breaker on ATHENS 2 69.000 (533623) 69 kV Bus a. Apply Fault at the ATHENS 2 69.000 (533623) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. ATHENS 2 (533623) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.3. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.4. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.5. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT298 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLERN2 (533583) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 b.3. BUTLERN2 (533583) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #z1 b.4. BUTLERN2 (533583) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #1 b.5. FRNTR N2 (533593) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #1 b.6. BUTLERS2 (533609) 69.0 kV to BUTLERS4 (532989) 138.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT299 | Single Phase Fault with Stuck Breaker on CHRYJCT2 69.000 (533680) 69 kV Bus a. Apply Fault at the CHRYJCT2 69.000 (533680) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERRYV2 (533679) 69.0 kV to CHRYJCT2 (533680) 69.0 kV Transmission Circuit #1 b.2. CHERRYV2 (533679) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 b.3. CHRYJCT2 (533680) 69.0 kV to INDEPEN2 (533694) 69.0 kV Transmission Circuit #1 b.4. CHRYJCT2 (533680) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT300 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.4. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.5. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.6. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT301 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 b.3. CRESW2 1 (533081) 13.2 kV to CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.5. CRESWLN4 (532981) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT302 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.2. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT303 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT304 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.2. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT305 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. BEECRK2 (533677) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.5. COFFSUB2 (533683) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT306 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASO 2 (533793) 69.0 kV to MULVANE2 (533821) 69.0 kV Transmission Circuit #1 b.6. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.7. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT307 | Single Phase Fault with Stuck Breaker on FTSCOTT2 69.000 (533635) 69 kV Bus a. Apply Fault at the FTSCOTT2 69.000 (533635) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.4. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.5. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT308 | Single Phase Fault with Stuck Breaker on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT309 | Single Phase Fault with Stuck Breaker on WARE 2 69.000 (533652) 69 kV Bus a. Apply Fault at the WARE 2 69.000 (533652) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.2. WARE 2 (533652) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.4. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.5. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT310 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.4. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.5. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.6. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT311 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. SUNFLRS2 (533670) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.4. CHRYJCT2 (533680) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.5. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT312 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to HUDSJCT2 (533764) 69.0 kV Transmission Circuit #1 b.2. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.3. HUDSJCT2 (533764) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.5. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.6. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT313 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.2. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.4. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.5. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT314 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.2. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.3. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.4. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT315 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.6. LITCH1 1 (532952) 13.2 kV to LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT316 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT317 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.4. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.5. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.6. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT318 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 b.4. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.5. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT319 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT320 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT321 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.3. NEC U3 (532711) 12.0 kV to NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV Three Winding #1 b.4. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT322 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.3. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT323 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. GIRARD 2 (533761) 69.0 kV to GIR JCT2 (533762) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.6. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.7. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.8. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT324 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 b.5. NOEASTW2 (533822) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #z1 b.6. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT325 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.3. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.4. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.5. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT326 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT327 | Single Phase Fault with Stuck Breaker on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT328 | Single Phase Fault with Stuck Breaker on PITTSBG2 69.000 (533770) 69 kV Bus a. Apply Fault at the PITTSBG2 69.000 (533770) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to HUDSJCT2 (533764) 69.0 kV Transmission Circuit #1 b.2. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. HUDSON-2 (533763) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.5. HUDSJCT2 (533764) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT329 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.3. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.4. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.5. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT330 | Single Phase Fault with Stuck Breaker on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.3. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.5. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT331 | Single Phase Fault with Stuck Breaker on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT2 (533558) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT332 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT333 | Single Phase Fault with Stuck Breaker on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT2 (533558) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT334 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 b.3. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.4. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.5. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.6. TIOGA 2 (533646) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 b.7. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT335 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 b.4. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.5. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.6. TIOGA 2 (533646) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 b.7. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT336 | Single Phase Fault with Stuck Breaker on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.3. BU10BEN2 (533585) 69.0 kV to WEAVER 2 (533604) 69.0 kV Transmission Circuit #1 b.4. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.5. WEAVER 2 (533604) 69.0 kV to WEAVER 4 (532991) 138.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT337 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.2. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.6. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 b.7. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT338 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT339 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT340 | Single Phase Fault with Stuck Breaker on BAX488 5 161.00 (547729) 161 kV Bus a. Apply Fault at the BAX488 5 161.00 (547729) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT341 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.4. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT342 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.6. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT343 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT344 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT345 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT346 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT347 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT348 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT349 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT350 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT351 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT352 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT353 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT354 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT355 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT356 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT357 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT358 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT359 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT360 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT361 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT362 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT363 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT364 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT365 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT366 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT367 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.3. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT368 | Single Phase Fault with Stuck Breaker on SUB N-161 161.00 (548820) 161 kV Bus a. Apply Fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT369 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT370 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT371 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT372 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT373 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT374 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT375 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT376 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT377 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT378 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT379 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT380 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT381 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT382 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT383 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT384 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT385 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT386 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT387 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT388 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT389 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT390 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT391 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT392 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT393 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT394 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT395 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT396 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT397 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT398 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT399 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT400 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT401 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT402 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT403 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to Load #O0 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT404 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.5. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT405 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT406 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.3. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT407 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT408 | Single Phase Fault with Stuck Breaker on N MADRD5 161.00 (505400) 161 kV Bus a. Apply Fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to N MADRD5 (505400) 161.0 kV Transmission Circuit #1 b.2. N MADRD5 (505400) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 b.3. N MADRD5 (505400) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 b.4. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X1 1 (505401) 13.8 kV Three Winding #1 b.5. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X2 1 (505403) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT409 | Single Phase Fault with Stuck Breaker on N MADRD5 161.00 (505400) 161 kV Bus a. Apply Fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STJUDEW (300170) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.2. 2LILBRN (301246) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.3. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 b.4. N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV to NMA X1 1 (505401) 13.8 kV Three Winding #1 b.5. N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV to NMA X2 1 (505403) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT410 | Single Phase Fault with Stuck Breaker on KENNETT5 161.00 (505410) 161 kV Bus a. Apply Fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIGGOTT2 (505406) 69.0 kV to KENNETT2 (505408) 69.0 kV Transmission Circuit #1 b.2. KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV to KEN X1 1 (505407) 13.8 kV Three Winding #1 b.3. KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV to KEN X2 1 (505409) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT411 | Single Phase Fault with Stuck Breaker on KENNETT5 161.00 (505410) 161 kV Bus a. Apply Fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD5 (505400) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 b.2. KENNETT5 (505410) 161.0 kV to PARAGLD5 (505412) 161.0 kV Transmission Circuit #1 b.3. KENNETT5 (505410) 161.0 kV to KENNETT2 (505408) 69.0 kV to KEN X1 1 (505407) 13.8 kV Three Winding #1 b.4. KENNETT5 (505410) 161.0 kV to KENNETT2 (505408) 69.0 kV to KEN X2 1 (505409) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT412 | Single Phase Fault with Stuck Breaker on PIGGOTT2 69.000 (505406) 69 kV Bus a. Apply Fault at the PIGGOTT2 69.000 (505406) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 b.2. PIGGOTT2 (505406) 69.0 kV to KENNETT2 (505408) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT413 | Single Phase Fault with Stuck Breaker on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENNETT5 (505410) 161.0 kV to PARAGLD5 (505412) 161.0 kV Transmission Circuit #1 b.2. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 b.3. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X1 1 (505411) 13.8 kV Three Winding #1 b.4. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X2 1 (505413) 13.8 kV Three Winding #1 b.5. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X3 1 (505415) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT414 | Single Phase Fault with Stuck Breaker on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply Fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MINER 1 (345203) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 b.2. SIKETAP5 (505427) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 b.3. SIKESTN5 (505428) 161.0 kV to SIKGEN 1 (505432) 13.8 kV Two Winding #1 b.4. SIKESTN5 (505428) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.5. SIKESTN5 (505428) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 b.6. SIKESTN5 (505428) 161.0 kV to SIKESTN2 (505430) 69.0 kV to SIK X1 1 (505429) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT415 | Single Phase Fault with Stuck Breaker on POP BLF5 161.00 (505438) 161 kV Bus a. Apply Fault at the POP BLF5 161.00 (505438) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GRNFRT (300084) 161.0 kV to POP BLF5 (505438) 161.0 kV Transmission Circuit #1 b.2. POP BLF5 (505438) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 b.3. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X1 1 (505435) 13.8 kV Three Winding #1 b.4. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X2 1 (505437) 13.8 kV Three Winding #1 b.5. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X3 1 (505439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT416 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT417 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT418 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT419 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT420 | Single Phase Fault with Stuck Breaker on CENTR H5 161.00 (505416) 161 kV Bus a. Apply Fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 b.2. CENTR H5 (505416) 161.0 kV to JONESBO5 (505418) 161.0 kV Transmission Circuit #1 b.3. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X1 1 (505417) 13.8 kV Three Winding #1 b.4. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X2 1 (505419) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT421 | Single Phase Fault with Stuck Breaker on 5ESSEX 161.00 (300075) 161 kV Bus a. Apply Fault at the 5ESSEX 161.00 (300075) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5ESSEX (300075) 161.0 kV to 7ESSEX (300038) 345.0 kV Two Winding #1 b.2. 5ESSEX (300075) 161.0 kV to 5ESSEXGSU1 (301533) 161.0 kV Transmission Circuit #1 b.3. 5ESSEX (300075) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #1 b.4. 5ESSEX (300075) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.5. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #1 b.6. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #2 b.7. SIKESTN5 (505428) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.8. IDALIA 5 (505434) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT422 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.3. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.5. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.6. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.7. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.8. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT423 | Single Phase Fault with Stuck Breaker on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT424 | Single Phase Fault with Stuck Breaker on STROTHR2 69.000 (533556) 69 kV Bus a. Apply Fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.2. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT425 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.0 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.0 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.3. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.4. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.5. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT426 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT427 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT428 | Single Phase Fault with Stuck Breaker on CONCRD6 230.00 (539658) 230 kV Bus a. Apply Fault at the CONCRD6 230.00 (539658) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT429 | Single Phase Fault with Stuck Breaker on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply Fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON1 (539655) 13.8 kV to CLIFTON3 (539656) 115.0 kV Two Winding #1 b.3. CLIFTON3 (539656) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.4. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.5. CLIFTON3 (539656) 115.0 kV to CLIFSUB1 (539704) 34.5 kV to CLIFTN-T (539903) 13.8 kV Three Winding #1 b.6. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT430 | Single Phase Fault with Stuck Breaker on CLIFTON3 115.00 (539656) 115 kV Bus a. Apply Fault at the CLIFTON3 115.00 (539656) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 b.4. CLIFTN-T (539903) 13.8 kV to CLIFSUB1 (539704) 34.5 kV to CLIFTON3 (539656) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT431 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT432 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT433 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT434 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT435 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT436 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP#1 (541165) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.2. S.HARP#2 (541166) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.3. S.HARP#3 (541167) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.4. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT437 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT438 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT439 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT440 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT441 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT442 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT443 | Single Phase Fault with Stuck Breaker on METRO 5 161.00 (546742) 161 kV Bus a. Apply Fault at the METRO 5 161.00 (546742) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.4. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT444 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 b.4. FARML 4 (512734) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT445 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT446 | Single Phase Fault with Stuck Breaker on PAWN-ED3 115.00 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 115.00 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.4. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.6. KINSLEY3 (530619) 115.0 kV to GEN-2016-016 (587120) 115.0 kV Transmission Circuit #1 b.7. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.8. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.9. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.10. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.11. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT447 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT448 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT449 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT450 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT451 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT452 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT453 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT454 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT455 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT456 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT457 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT458 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT459 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER_602 8 (640143) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #z1 b.2. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT460 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.3. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.5. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.7. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.8. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT461 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT462 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT463 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT464 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT465 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT466 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT467 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT468 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT469 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT470 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT471 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT472 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT473 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT474 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT475 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT476 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT477 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT478 | Single Phase Fault with Stuck Breaker on 5GENTRY 161.00 (300073) 161 kV Bus a. Apply Fault at the 5GENTRY 161.00 (300073) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GENTRY (300073) 161.0 kV to 5NODWAY (300104) 161.0 kV Transmission Circuit #1 b.2. 5GENTRY (300073) 161.0 kV to 5FAIRPTB2 (300076) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT479 | Single Phase Fault with Stuck Breaker on 5FAIRPTB2 161.00 (300076) 161 kV Bus a. Apply Fault at the 5FAIRPTB2 161.00 (300076) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.2. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT480 | Single Phase Fault with Stuck Breaker on 5HICKCK 161.00 (300087) 161 kV Bus a. Apply Fault at the 5HICKCK 161.00 (300087) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HICKCK (300087) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #1 b.2. 5HICKCK (300087) 161.0 kV to 5LOCUST (300094) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT481 | Single Phase Fault with Stuck Breaker on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply Fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 b.2. 5NEWMAD (300103) 161.0 kV to 5NEWMADCP (301405) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT482 | Single Phase Fault with Stuck Breaker on 5OSBORN 161.00 (300107) 161 kV Bus a. Apply Fault at the 5OSBORN 161.00 (300107) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSBORN (300107) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #1 b.2. 5OSBORN (300107) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT483 | Single Phase Fault with Stuck Breaker on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply Fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT484 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT485 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT486 | Single Phase Fault with Stuck Breaker on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply Fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT487 | Single Phase Fault with Stuck Breaker on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply Fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STJUDEW (300170) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.2. 2STJUDEW (300170) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT488 | Single Phase Fault with Stuck Breaker on 2JAMESN 69.000 (300202) 69 kV Bus a. Apply Fault at the 2JAMESN 69.000 (300202) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JAMESN (300202) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2JAMESN (300202) 69.0 kV to 2GALLTN (300198) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT489 | Single Phase Fault with Stuck Breaker on 2KIDDER 69.000 (300203) 69 kV Bus a. Apply Fault at the 2KIDDER 69.000 (300203) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2KIDDER (300203) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2KIDDER (300203) 69.0 kV to 2MABELTP (300215) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT490 | Single Phase Fault with Stuck Breaker on 2PATBRG 69.000 (300209) 69 kV Bus a. Apply Fault at the 2PATBRG 69.000 (300209) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PATBRG (300209) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2PATBRG (300209) 69.0 kV to 2BETHNY (300220) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT491 | Single Phase Fault with Stuck Breaker on 2DRLNGT 69.000 (300248) 69 kV Bus a. Apply Fault at the 2DRLNGT 69.000 (300248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DRLNGT (300248) 69.0 kV to 2ALBNYTP (300245) 69.0 kV Transmission Circuit #1 b.2. 2DRLNGT (300248) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT492 | Single Phase Fault with Stuck Breaker on 5FAIRPTB1 161.00 (301564) 161 kV Bus a. Apply Fault at the 5FAIRPTB1 161.00 (301564) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FAIRPT (300249) 69.0 kV to 5FAIRPTB2 (300076) 161.0 kV Two Winding #2 b.2. 2FAIRPT (300249) 69.0 kV to 5FAIRPTB1 (301564) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT493 | Single Phase Fault with Stuck Breaker on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply Fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 b.2. 2CENTRV (300323) 69.0 kV to 2ROSEHL (300334) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT494 | Single Phase Fault with Stuck Breaker on 2RT Z 69.000 (300325) 69 kV Bus a. Apply Fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2RT Z (300325) 69.0 kV to 2ELM (300327) 69.0 kV Transmission Circuit #1 b.2. 2RT Z (300325) 69.0 kV to 2COLMBUS (300326) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT495 | Single Phase Fault with Stuck Breaker on 2ELM 69.000 (300327) 69 kV Bus a. Apply Fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ELM (300327) 69.0 kV to 2RT Z (300325) 69.0 kV Transmission Circuit #1 b.2. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT496 | Single Phase Fault with Stuck Breaker on 2ROSEHL 69.000 (300334) 69 kV Bus a. Apply Fault at the 2ROSEHL 69.000 (300334) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ROSEHL (300334) 69.0 kV to 2CENTRV (300323) 69.0 kV Transmission Circuit #1 b.2. 2ROSEHL (300334) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT497 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT498 | Single Phase Fault with Stuck Breaker on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply Fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT499 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 b.2. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT500 | Single Phase Fault with Stuck Breaker on 2IVYBND 69.000 (300557) 69 kV Bus a. Apply Fault at the 2IVYBND 69.000 (300557) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2IVYBND (300557) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 b.2. 2IVYBND (300557) 69.0 kV to 2VERSAL (300565) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT501 | Single Phase Fault with Stuck Breaker on 2MTHULD 69.000 (300558) 69 kV Bus a. Apply Fault at the 2MTHULD 69.000 (300558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTHULD (300558) 69.0 kV to 2LINCLN (300534) 69.0 kV Transmission Circuit #1 b.2. 2MTHULD (300558) 69.0 kV to 2IVYBND (300557) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT502 | Single Phase Fault with Stuck Breaker on 2APPLTN 69.000 (300687) 69 kV Bus a. Apply Fault at the 2APPLTN 69.000 (300687) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2APPLTN (300687) 69.0 kV to 2LADUE (300702) 69.0 kV Transmission Circuit #1 b.2. 2APPLTN (300687) 69.0 kV to 2TABORVL (300813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT503 | Single Phase Fault with Stuck Breaker on 2AUSTIN 69.000 (300688) 69 kV Bus a. Apply Fault at the 2AUSTIN 69.000 (300688) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AUSTIN (300688) 69.0 kV to 2ELYNTP (300699) 69.0 kV Transmission Circuit #1 b.2. 2AUSTIN (300688) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT504 | Single Phase Fault with Stuck Breaker on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply Fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV Two Winding #1 b.2. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT505 | Single Phase Fault with Stuck Breaker on 2BUTLERE 69.000 (300690) 69 kV Bus a. Apply Fault at the 2BUTLERE 69.000 (300690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BUTLERE (300690) 69.0 kV to 2BUTLER (300689) 69.0 kV Transmission Circuit #1 b.2. 2BUTLERE (300690) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT506 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 b.2. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT507 | Single Phase Fault with Stuck Breaker on 2CREIGH 69.000 (300696) 69 kV Bus a. Apply Fault at the 2CREIGH 69.000 (300696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CREIGH (300696) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 b.2. 2CREIGH (300696) 69.0 kV to 2AUSTIN (300688) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT508 | Single Phase Fault with Stuck Breaker on 2GAINES 69.000 (300701) 69 kV Bus a. Apply Fault at the 2GAINES 69.000 (300701) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GAINES (300701) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2GAINES (300701) 69.0 kV to 2MTZION (300810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT509 | Single Phase Fault with Stuck Breaker on 2LADUE 69.000 (300702) 69 kV Bus a. Apply Fault at the 2LADUE 69.000 (300702) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LADUE (300702) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 b.2. 2LADUE (300702) 69.0 kV to 2APPLTN (300687) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT510 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT511 | Single Phase Fault with Stuck Breaker on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply Fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2MTZION (300810) 69.0 kV Transmission Circuit #1 b.2. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT512 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT513 | Single Phase Fault with Stuck Breaker on 2AIDJCT 69.000 (301191) 69 kV Bus a. Apply Fault at the 2AIDJCT 69.000 (301191) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AIDJCT (301191) 69.0 kV to 2BLOOMF (301237) 69.0 kV Transmission Circuit #1 b.2. 2AIDJCT (301191) 69.0 kV to 2PUXICO (301221) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT514 | Single Phase Fault with Stuck Breaker on 2ADVANC 69.000 (301235) 69 kV Bus a. Apply Fault at the 2ADVANC 69.000 (301235) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ADVANC (301235) 69.0 kV to 2ARDEOLA (301257) 69.0 kV Transmission Circuit #1 b.2. 2ADVANC (301235) 69.0 kV to 2WHTWTR (301279) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT515 | Single Phase Fault with Stuck Breaker on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply Fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ANNSTN (301236) 69.0 kV to 2LILBRN (301246) 69.0 kV Transmission Circuit #1 b.2. 2ANNSTN (301236) 69.0 kV to 2DOGWOD (301239) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT516 | Single Phase Fault with Stuck Breaker on 2BLOOMF 69.000 (301237) 69 kV Bus a. Apply Fault at the 2BLOOMF 69.000 (301237) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BLOOMF (301237) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2BLOOMF (301237) 69.0 kV to 2AIDJCT (301191) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT517 | Single Phase Fault with Stuck Breaker on 2FRISCO 69.000 (301240) 69 kV Bus a. Apply Fault at the 2FRISCO 69.000 (301240) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FRISCO (301240) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2FRISCO (301240) 69.0 kV to 2PARMA (301250) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT518 | Single Phase Fault with Stuck Breaker on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply Fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #1 b.2. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT519 | Single Phase Fault with Stuck Breaker on 2IDALMA 69.000 (301244) 69 kV Bus a. Apply Fault at the 2IDALMA 69.000 (301244) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2IDALMA (301244) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2IDALMA (301244) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT520 | Single Phase Fault with Stuck Breaker on 2MOREHS 69.000 (301248) 69 kV Bus a. Apply Fault at the 2MOREHS 69.000 (301248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOREHS (301248) 69.0 kV to 2MATHWS (301247) 69.0 kV Transmission Circuit #1 b.2. 2MOREHS (301248) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT521 | Single Phase Fault with Stuck Breaker on 2MOREJT 69.000 (301249) 69 kV Bus a. Apply Fault at the 2MOREJT 69.000 (301249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOREJT (301249) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 b.2. 2MOREJT (301249) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT522 | Single Phase Fault with Stuck Breaker on 2PARMA 69.000 (301250) 69 kV Bus a. Apply Fault at the 2PARMA 69.000 (301250) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PARMA (301250) 69.0 kV to 2FRISCO (301240) 69.0 kV Transmission Circuit #1 b.2. 2PARMA (301250) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT523 | Single Phase Fault with Stuck Breaker on 2AVONKN 69.000 (301285) 69 kV Bus a. Apply Fault at the 2AVONKN 69.000 (301285) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AVONKN (301285) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 b.2. 2AVONKN (301285) 69.0 kV to 2GIDJCT (301293) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT524 | Single Phase Fault with Stuck Breaker on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply Fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT525 | Single Phase Fault with Stuck Breaker on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply Fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KELSO 1 (344847) 161.0 kV to 7KELSO 1 (344848) 345.0 kV Two Winding #1 b.2. 5KELSO 1 (344847) 161.0 kV to 5MINER 1 (345203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT526 | Single Phase Fault with Stuck Breaker on 5MINER 1 161.00 (345203) 161 kV Bus a. Apply Fault at the 5MINER 1 161.00 (345203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MINER 1 (345203) 161.0 kV to 5KELSO 1 (344847) 161.0 kV Transmission Circuit #1 b.2. 5MINER 1 (345203) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT527 | Single Phase Fault with Stuck Breaker on 5RIDGELY TN 161.00 (360521) 161 kV Bus a. Apply Fault at the 5RIDGELY TN 161.00 (360521) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RIDGELY TN (360521) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 b.2. 5RIDGELY TN (360521) 161.0 kV to 5NAUVOO TN (360479) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT528 | Single Phase Fault with Stuck Breaker on 5TIPTONVL TN161.00 (361261) 161 kV Bus a. Apply Fault at the 5TIPTONVL TN161.00 (361261) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5TIPTONVL TN (361261) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5TIPTONVL TN (361261) 161.0 kV to 5RIDGELY TN (360521) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT529 | Single Phase Fault with Stuck Breaker on SIKETAP5 161.00 (505427) 161 kV Bus a. Apply Fault at the SIKETAP5 161.00 (505427) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIKETAP5 (505427) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 b.2. SIKETAP5 (505427) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT530 | Single Phase Fault with Stuck Breaker on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply Fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT531 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT532 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT533 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT534 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT535 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT536 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT537 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to GEN-2017-125 (761901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT538 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT539 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT540 | Single Phase Fault with Stuck Breaker on EXPED WF7 345.00 (532790) 345 kV Bus a. Apply Fault at the EXPED WF7 345.00 (532790) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPED WF7 (532790) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 b.2. EXPED WF7 (532790) 345.0 kV to E1 TX1 (534048) 34.5 kV to E1 TERT1 (534049) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT541 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT542 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT543 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT544 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT545 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT546 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT547 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT548 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT549 | Single Phase Fault with Stuck Breaker on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply Fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT550 | Single Phase Fault with Stuck Breaker on BERG 3 115.00 (533367) 115 kV Bus a. Apply Fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 b.2. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT551 | Single Phase Fault with Stuck Breaker on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply Fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT552 | Single Phase Fault with Stuck Breaker on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply Fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUNDRG3 (533429) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. MOUNDRG3 (533429) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT553 | Single Phase Fault with Stuck Breaker on CLDWELL4 138.00 (539003) 138 kV Bus a. Apply Fault at the CLDWELL4 138.00 (539003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLDWELL4 (539003) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT554 | Single Phase Fault with Stuck Breaker on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.2. MILAN_GOAB (539008) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT555 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT556 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT557 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT558 | Single Phase Fault with Stuck Breaker on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply Fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT559 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT560 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT561 | Single Phase Fault with Stuck Breaker on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 b.2. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT562 | Single Phase Fault with Stuck Breaker on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. SMTHVL 5 (541204) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT563 | Single Phase Fault with Stuck Breaker on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply Fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT564 | Single Phase Fault with Stuck Breaker on TWA 5 161.00 (541214) 161 kV Bus a. Apply Fault at the TWA 5 161.00 (541214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 b.2. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT565 | Single Phase Fault with Stuck Breaker on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply Fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 b.2. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT566 | Single Phase Fault with Stuck Breaker on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. PLTCTY 5 (541221) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT567 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT568 | Single Phase Fault with Stuck Breaker on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply Fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARYVLE5 (541251) 161.0 kV to 5MARYVB2 (300097) 161.0 kV Transmission Circuit #1 b.2. MARYVLE5 (541251) 161.0 kV to BRADDYVILLE5 (635038) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT569 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT570 | Single Phase Fault with Stuck Breaker on EAST 5 161.00 (541254) 161 kV Bus a. Apply Fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT571 | Single Phase Fault with Stuck Breaker on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply Fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 b.2. LAKE RD5 (541255) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT572 | Single Phase Fault with Stuck Breaker on IND PRK5 161.00 (541256) 161 kV Bus a. Apply Fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 b.2. IND PRK5 (541256) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT573 | Single Phase Fault with Stuck Breaker on COOK 5 161.00 (541257) 161 kV Bus a. Apply Fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOK 5 (541257) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT574 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 b.2. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT575 | Single Phase Fault with Stuck Breaker on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply Fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT576 | Single Phase Fault with Stuck Breaker on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply Fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT577 | Single Phase Fault with Stuck Breaker on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply Fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 b.2. CLNTPLT2 (541301) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT578 | Single Phase Fault with Stuck Breaker on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply Fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT579 | Single Phase Fault with Stuck Breaker on BELTONS5 161.00 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 b.2. BELTONS5 (541340) 161.0 kV to TURNER_RD5 (541259) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT580 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 b.2. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT581 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT582 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT583 | Single Phase Fault with Stuck Breaker on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply Fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDWAY_5 (541369) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 b.2. MIDWAY_5 (541369) 161.0 kV to MARYVLE5 (541251) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT584 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT585 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT586 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT587 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT588 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 b.2. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT589 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT590 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT591 | Single Phase Fault with Stuck Breaker on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply Fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PFLUMM 5 (542979) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT592 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT593 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT594 | Single Phase Fault with Stuck Breaker on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply Fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT595 | Single Phase Fault with Stuck Breaker on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply Fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHTOWN5 (542993) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 b.2. STHTOWN5 (542993) 161.0 kV to BENDIX 5 (542992) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT596 | Single Phase Fault with Stuck Breaker on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply Fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT597 | Single Phase Fault with Stuck Breaker on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT598 | Single Phase Fault with Stuck Breaker on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 b.2. GLADSTN5 (543016) 161.0 kV to GLADSTN_CAP5 (542946) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT599 | Single Phase Fault with Stuck Breaker on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply Fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 b.2. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT600 | Single Phase Fault with Stuck Breaker on BARRY 5 161.00 (543019) 161 kV Bus a. Apply Fault at the BARRY 5 161.00 (543019) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRY 5 (543019) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. BARRY 5 (543019) 161.0 kV to BARRY_CAP 5 (542944) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT601 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.2. NASHUA-5 (543028) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT602 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT603 | Single Phase Fault with Stuck Breaker on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply Fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 b.2. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT604 | Single Phase Fault with Stuck Breaker on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply Fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 b.2. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT605 | Single Phase Fault with Stuck Breaker on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. LENEXA 5 (543038) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT606 | Single Phase Fault with Stuck Breaker on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply Fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. MOONLT 5 (543044) 161.0 kV to QUARRY 5 (543037) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT607 | Single Phase Fault with Stuck Breaker on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply Fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 b.2. OXFORD 5 (543046) 161.0 kV to OLATHE 5 (543036) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT608 | Single Phase Fault with Stuck Breaker on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply Fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEOTTWA5 (543055) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 b.2. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT609 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT610 | Single Phase Fault with Stuck Breaker on CENTENL5 161.00 (543067) 161 kV Bus a. Apply Fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 b.2. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT611 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT612 | Single Phase Fault with Stuck Breaker on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 b.2. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT613 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT614 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT615 | Single Phase Fault with Stuck Breaker on G14-001-TAP 345.00 (562476) 345 kV Bus a. Apply Fault at the G14-001-TAP 345.00 (562476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G14-001-TAP (562476) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. G14-001-TAP (562476) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT616 | Single Phase Fault with Stuck Breaker on GEN-2016-111345.00 (587880) 345 kV Bus a. Apply Fault at the GEN-2016-111345.00 (587880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-111 (587880) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-111 (587880) 345.0 kV to G16-111XFMR1 (587881) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT617 | Single Phase Fault with Stuck Breaker on GEN-2017-004345.00 (588490) 345 kV Bus a. Apply Fault at the GEN-2017-004345.00 (588490) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-004 (588490) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-004 (588490) 345.0 kV to G17-004XFMR1 (588491) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT618 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT619 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT620 | Single Phase Fault with Stuck Breaker on GEN-2017-202161.00 (761418) 161 kV Bus a. Apply Fault at the GEN-2017-202161.00 (761418) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-202 (761418) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 b.2. GEN-2017-202 (761418) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT621 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GIBSON (301291) 69.0 kV to 5GIBSON (300083) 161.0 kV Two Winding #1 b.2. 2GIBSON (301291) 69.0 kV to 2CAMBEL (301196) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT622 | Single Phase Fault with Stuck Breaker on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply Fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 b.2. 2HOLDEN (300336) 69.0 kV to 2CENTRV (300323) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT623 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT624 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 b.2. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT625 | Single Phase Fault with Stuck Breaker on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply Fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #1 b.2. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT626 | Single Phase Fault with Stuck Breaker on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply Fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMADXF12 (301531) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #z1 b.2. 5NEWMADXF12 (301531) 161.0 kV to 7NEWMADXF12 (301530) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT627 | Single Phase Fault with Stuck Breaker on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply Fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7KELSO 1 (344848) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 b.2. 7KELSO 1 (344848) 345.0 kV to 7KELSO 2 (344849) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT628 | Single Phase Fault with Stuck Breaker on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV to PRG X1 1 (505411) 13.8 kV Three Winding #1 b.2. PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV to PRG X2 1 (505413) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT629 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to DELWARE4 (510379) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to SCOFCTY4 (510378) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT630 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILL6 (532857) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT631 | Single Phase Fault with Stuck Breaker on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply Fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT6 (532861) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT632 | Single Phase Fault with Stuck Breaker on TECHILL5 161.00 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILL5 (532920) 161.0 kV to KELLY 5 (532913) 161.0 kV Transmission Circuit #1 b.2. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT633 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 b.2. OTTRCRK4 (532997) 138.0 kV to BUTLER 4 (532987) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT634 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUND 4 (533013) 138.0 kV to MOUND 2 (533742) 69.0 kV to MOUND1X1 (533095) 13.2 kV Three Winding #1 b.2. MOUND 4 (533013) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT635 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 b.2. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT636 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 b.2. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT637 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 b.2. FRANKLIN2 (533876) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT638 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTN N2 (541303) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT639 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 b.2. CLNTN S2 (541320) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT640 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.2. S.HARP 2 (541343) 69.0 kV to FREEMAN2 (541291) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT641 | Single Phase Fault with Stuck Breaker on EDMOND5 161.00 (541355) 161 kV Bus a. Apply Fault at the EDMOND5 161.00 (541355) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDMOND5 (541355) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. EDMOND5 (541355) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT642 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT643 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to 5SEDALA (300117) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT644 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTON5 (541242) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #z1 b.2. CLINTON5 (541242) 161.0 kV to CLNTN N2 (541303) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT645 | Single Phase Fault with Stuck Breaker on G17-108-TAP 161.00 (761278) 161 kV Bus a. Apply Fault at the G17-108-TAP 161.00 (761278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-108-TAP (761278) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. G17-108-TAP (761278) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT646 | Single Phase Fault with Stuck Breaker on 5NODWAY 161.00 (300104) 161 kV Bus a. Apply Fault at the 5NODWAY 161.00 (300104) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NODWAY (300104) 161.0 kV to 5GENTRY (300073) 161.0 kV Transmission Circuit #1 b.2. 5NODWAY (300104) 161.0 kV to 5MARYVLB1 (301592) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT647 | Single Phase Fault with Stuck Breaker on 5WINSLOW 161.00 (301347) 161 kV Bus a. Apply Fault at the 5WINSLOW 161.00 (301347) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5WINSLOW (301347) 161.0 kV to 1WINSLOW (301356) 34.5 kV Two Winding #1 b.2. 5WINSLOW (301347) 161.0 kV to 1WINSLOW (301356) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT648 | Single Phase Fault with Stuck Breaker on 5FAIRPTB1 161.00 (301564) 161 kV Bus a. Apply Fault at the 5FAIRPTB1 161.00 (301564) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5FAIRPTB1 (301564) 161.0 kV to 5FAIRPTB2 (300076) 161.0 kV Transmission Circuit #z1 b.2. 5FAIRPTB1 (301564) 161.0 kV to 5OSBORN (300107) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT649 | Single Phase Fault with Stuck Breaker on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply Fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5COLLINS (300816) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 b.2. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT650 | Single Phase Fault with Stuck Breaker on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply Fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOL (301040) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOL (301040) 161.0 kV to 2OSCEOL (300811) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT651 | Single Phase Fault with Stuck Breaker on 5HOLDENB1 161.00 (301561) 161 kV Bus a. Apply Fault at the 5HOLDENB1 161.00 (301561) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HOLDENB1 (301561) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #z1 b.2. 5HOLDENB1 (301561) 161.0 kV to 5PITTSV (300110) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT652 | Single Phase Fault with Stuck Breaker on 2BAELLS 69.000 (301286) 69 kV Bus a. Apply Fault at the 2BAELLS 69.000 (301286) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BAELLS (301286) 69.0 kV to 2STJUDEW (300170) 69.0 kV Transmission Circuit #1 b.2. 2BAELLS (301286) 69.0 kV to 2AVONKN (301285) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT653 | Single Phase Fault with Stuck Breaker on 2KINGCT 69.000 (300257) 69 kV Bus a. Apply Fault at the 2KINGCT 69.000 (300257) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2KINGCT (300257) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2KINGCT (300257) 69.0 kV to 2FLGGSP (300251) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT654 | Single Phase Fault with Stuck Breaker on 2MAYSVL 69.000 (300259) 69 kV Bus a. Apply Fault at the 2MAYSVL 69.000 (300259) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MAYSVL (300259) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2MAYSVL (300259) 69.0 kV to 2STEWRV (300268) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT655 | Single Phase Fault with Stuck Breaker on 2SYLVAN 69.000 (300545) 69 kV Bus a. Apply Fault at the 2SYLVAN 69.000 (300545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SYLVAN (300545) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2SYLVAN (300545) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT656 | Single Phase Fault with Stuck Breaker on 2PIPER 69.000 (300706) 69 kV Bus a. Apply Fault at the 2PIPER 69.000 (300706) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PIPER (300706) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2PIPER (300706) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT657 | Single Phase Fault with Stuck Breaker on 2LEETON 69.000 (300703) 69 kV Bus a. Apply Fault at the 2LEETON 69.000 (300703) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LEETON (300703) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 b.2. 2LEETON (300703) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT658 | Single Phase Fault with Stuck Breaker on 2CLINTNLD 69.000 (301626) 69 kV Bus a. Apply Fault at the 2CLINTNLD 69.000 (301626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLINTNLD (301626) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2CLINTNLD (301626) 69.0 kV to 2LADUE (300702) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT659 | Single Phase Fault with Stuck Breaker on 2MTZION 69.000 (300810) 69 kV Bus a. Apply Fault at the 2MTZION 69.000 (300810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTZION (300810) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 b.2. 2MTZION (300810) 69.0 kV to 2DAMSCUS (300804) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT660 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT661 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT662 | Single Phase Fault with Stuck Breaker on GI94_POI 345.00 (709400) 345 kV Bus a. Apply Fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 b.2. GI94_POI (709400) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT663 | Single Phase Fault with Stuck Breaker on 2ARDEOLA 69.000 (301257) 69 kV Bus a. Apply Fault at the 2ARDEOLA 69.000 (301257) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ARDEOLA (301257) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2ARDEOLA (301257) 69.0 kV to 2ADVANC (301235) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT664 | Single Phase Fault with Stuck Breaker on 2DOGWOD 69.000 (301239) 69 kV Bus a. Apply Fault at the 2DOGWOD 69.000 (301239) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DOGWOD (301239) 69.0 kV to 2MATHWS (301247) 69.0 kV Transmission Circuit #1 b.2. 2DOGWOD (301239) 69.0 kV to 2ANNSTN (301236) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT665 | Single Phase Fault with Stuck Breaker on 2LILBRN 69.000 (301246) 69 kV Bus a. Apply Fault at the 2LILBRN 69.000 (301246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LILBRN (301246) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.2. 2LILBRN (301246) 69.0 kV to 2ANNSTN (301236) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT666 | Single Phase Fault with Stuck Breaker on 2VANDSR 69.000 (301251) 69 kV Bus a. Apply Fault at the 2VANDSR 69.000 (301251) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2VANDSR (301251) 69.0 kV to 2MORLEY (301255) 69.0 kV Transmission Circuit #1 b.2. 2VANDSR (301251) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT667 | Single Phase Fault with Stuck Breaker on 5VIAD_TP 161.00 (345891) 161 kV Bus a. Apply Fault at the 5VIAD_TP 161.00 (345891) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5VIAD_TP (345891) 161.0 kV to 5VIADUCT 3 (345892) 161.0 kV Transmission Circuit #1 b.2. 5VIAD_TP (345891) 161.0 kV to 5CAPE GIR3 (344286) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT668 | Single Phase Fault with Stuck Breaker on 5POLK TP 161.00 (361596) 161 kV Bus a. Apply Fault at the 5POLK TP 161.00 (361596) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5POLK TP (361596) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 b.2. 5POLK TP (361596) 161.0 kV to 5TROY TN (361422) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT669 | Single Phase Fault with Stuck Breaker on EXPEDITION7 345.00 (532803) 345 kV Bus a. Apply Fault at the EXPEDITION7 345.00 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPEDITION7 (532803) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. EXPEDITION7 (532803) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT670 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT671 | Single Phase Fault with Stuck Breaker on G17-004-TAP 345.00 (588494) 345 kV Bus a. Apply Fault at the G17-004-TAP 345.00 (588494) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-004-TAP (588494) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. G17-004-TAP (588494) 345.0 kV to ELMCREEK7 (539805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT672 | Single Phase Fault with Stuck Breaker on GEN-2017-125345.00 (761901) 345 kV Bus a. Apply Fault at the GEN-2017-125345.00 (761901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-125 (761901) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-125 (761901) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT673 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G17-086XFMR (589241) 34.5 kV Two Winding #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT674 | Single Phase Fault with Stuck Breaker on G17-209-TAP 345.00 (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP 345.00 (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT675 | Single Phase Fault with Stuck Breaker on G15-052T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15-052T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15-052T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT676 | Single Phase Fault with Stuck Breaker on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply Fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACKMAN5 (543126) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. LACKMAN5 (543126) 161.0 kV to SPRGHL 5 (532914) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT677 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT678 | Single Phase Fault with Stuck Breaker on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply Fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT679 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK3 (533315) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #2 b.2. OTTRCRK3 (533315) 115.0 kV to OTTRCRK4 (532997) 138.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT680 | Single Phase Fault with Stuck Breaker on SCHILNG3 115.00 (533377) 115 kV Bus a. Apply Fault at the SCHILNG3 115.00 (533377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCHILNG3 (533377) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 b.2. SCHILNG3 (533377) 115.0 kV to CRAWFRD3 (533364) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT681 | Single Phase Fault with Stuck Breaker on CHANTAP2 69.000 (533666) 69 kV Bus a. Apply Fault at the CHANTAP2 69.000 (533666) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHANTAP2 (533666) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 b.2. CHANTAP2 (533666) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT682 | Single Phase Fault with Stuck Breaker on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply Fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASHGRJ22 (533660) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 b.2. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT683 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT684 | Single Phase Fault with Stuck Breaker on SOPITT 2 69.000 (533773) 69 kV Bus a. Apply Fault at the SOPITT 2 69.000 (533773) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOPITT 2 (533773) 69.0 kV to BAKER 2 (532926) 69.0 kV Transmission Circuit #1 b.2. SOPITT 2 (533773) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT685 | Single Phase Fault with Stuck Breaker on ELMCREK6 230.00 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 230.00 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. ELMCREK6 (539639) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT686 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 4 (539674) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT687 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT688 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT689 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT690 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT691 | Single Phase Fault with Stuck Breaker on LBRTYWT5 161.00 (541247) 161 kV Bus a. Apply Fault at the LBRTYWT5 161.00 (541247) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYWT5 (541247) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 b.2. LBRTYWT5 (541247) 161.0 kV to HLLMRK 5 (541215) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT692 | Single Phase Fault with Stuck Breaker on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply Fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCONGRS5 (541318) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 b.2. NCONGRS5 (541318) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT693 | Single Phase Fault with Stuck Breaker on WESTON 5 161.00 (541351) 161 kV Bus a. Apply Fault at the WESTON 5 161.00 (541351) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTON 5 (541351) 161.0 kV to IATAN5 (541350) 161.0 kV Transmission Circuit #1 b.2. WESTON 5 (541351) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT694 | Single Phase Fault with Stuck Breaker on TIFFANY5 161.00 (543026) 161 kV Bus a. Apply Fault at the TIFFANY5 161.00 (543026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIFFANY5 (543026) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. TIFFANY5 (543026) 161.0 kV to WETHRBY5 (543017) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT695 | Single Phase Fault with Stuck Breaker on WOODBIN5 161.00 (541258) 161 kV Bus a. Apply Fault at the WOODBIN5 161.00 (541258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODBIN5 (541258) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. WOODBIN5 (541258) 161.0 kV to EAST 5 (541254) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT696 | Single Phase Fault with Stuck Breaker on AVENUECTY 5 161.00 (541394) 161 kV Bus a. Apply Fault at the AVENUECTY 5 161.00 (541394) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVENUECTY 5 (541394) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. AVENUECTY 5 (541394) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT697 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT698 | Single Phase Fault with Stuck Breaker on STALEY 2 69.000 (541261) 69 kV Bus a. Apply Fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STALEY 2 (541261) 69.0 kV to RNRDGE 2 (541260) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT699 | Single Phase Fault with Stuck Breaker on URICHTP2 69.000 (541304) 69 kV Bus a. Apply Fault at the URICHTP2 69.000 (541304) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. URICHTP2 (541304) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. URICHTP2 (541304) 69.0 kV to APCITY 2 (541306) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT700 | Single Phase Fault with Stuck Breaker on PECULRS5 161.00 (541344) 161 kV Bus a. Apply Fault at the PECULRS5 161.00 (541344) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULRS5 (541344) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 b.2. PECULRS5 (541344) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT701 | Single Phase Fault with Stuck Breaker on CEDRCRK5 161.00 (543049) 161 kV Bus a. Apply Fault at the CEDRCRK5 161.00 (543049) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDRCRK5 (543049) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. CEDRCRK5 (543049) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT702 | Single Phase Fault with Stuck Breaker on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply Fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSTVAL5 (543077) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. PLSTVAL5 (543077) 161.0 kV to SEOTTWA5 (543055) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT703 | Single Phase Fault with Stuck Breaker on BNSF 5 161.00 (543132) 161 kV Bus a. Apply Fault at the BNSF 5 161.00 (543132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BNSF 5 (543132) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. BNSF 5 (543132) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT704 | Single Phase Fault with Stuck Breaker on HICKMAN5 161.00 (542994) 161 kV Bus a. Apply Fault at the HICKMAN5 161.00 (542994) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HICKMAN5 (542994) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. HICKMAN5 (542994) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT705 | Single Phase Fault with Stuck Breaker on ANTIOCH5 161.00 (543050) 161 kV Bus a. Apply Fault at the ANTIOCH5 161.00 (543050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. ANTIOCH5 (543050) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT706 | Single Phase Fault with Stuck Breaker on REDEL 5 161.00 (543053) 161 kV Bus a. Apply Fault at the REDEL 5 161.00 (543053) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDEL 5 (543053) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. REDEL 5 (543053) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT707 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT708 | Single Phase Fault with Stuck Breaker on COLLEGE5 161.00 (543048) 161 kV Bus a. Apply Fault at the COLLEGE5 161.00 (543048) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLLEGE5 (543048) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. COLLEGE5 (543048) 161.0 kV to OLATHE 5 (543036) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT709 | Single Phase Fault with Stuck Breaker on OVERLPK5 161.00 (543047) 161 kV Bus a. Apply Fault at the OVERLPK5 161.00 (543047) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVERLPK5 (543047) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 b.2. OVERLPK5 (543047) 161.0 kV to BRKRIDG5 (543033) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT710 | Single Phase Fault with Stuck Breaker on FOREST 5 161.00 (543001) 161 kV Bus a. Apply Fault at the FOREST 5 161.00 (543001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOREST 5 (543001) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. FOREST 5 (543001) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT711 | Single Phase Fault with Stuck Breaker on BUNKRDG5 161.00 (543008) 161 kV Bus a. Apply Fault at the BUNKRDG5 161.00 (543008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUNKRDG5 (543008) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. BUNKRDG5 (543008) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT712 | Single Phase Fault with Stuck Breaker on WINJT S5 161.00 (543010) 161 kV Bus a. Apply Fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT S5 (543010) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT S5 (543010) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT713 | Single Phase Fault with Stuck Breaker on SHOLCRK5 161.00 (543029) 161 kV Bus a. Apply Fault at the SHOLCRK5 161.00 (543029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHOLCRK5 (543029) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. SHOLCRK5 (543029) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT714 | Single Phase Fault with Stuck Breaker on LINECRK5 161.00 (543025) 161 kV Bus a. Apply Fault at the LINECRK5 161.00 (543025) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINECRK5 (543025) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 b.2. LINECRK5 (543025) 161.0 kV to RIVRSID5 (543021) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT715 | Single Phase Fault with Stuck Breaker on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply Fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MERRIAM5 (543032) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. MERRIAM5 (543032) 161.0 kV to MERRIAM_CAP5 (542947) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT716 | Single Phase Fault with Stuck Breaker on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply Fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT717 | Single Phase Fault with Stuck Breaker on REEDER 5 161.00 (543052) 161 kV Bus a. Apply Fault at the REEDER 5 161.00 (543052) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REEDER 5 (543052) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 b.2. REEDER 5 (543052) 161.0 kV to KNLWRTH5 (543034) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT718 | Single Phase Fault with Stuck Breaker on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV to SEOTTWA5 (543055) 161.0 kV Transmission Circuit #1 b.2. S.OTTWA5 (543066) 161.0 kV to S.OTTWA21 (543121) 34.5 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT719 | Single Phase Fault with Stuck Breaker on WAGSTAF5 161.00 (543068) 161 kV Bus a. Apply Fault at the WAGSTAF5 161.00 (543068) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGSTAF5 (543068) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. WAGSTAF5 (543068) 161.0 kV to CENTENL5 (543067) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT720 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STL439 5 (547498) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. STL439 5 (547498) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT721 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT722 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT723 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to G14-001XFMR1 (583851) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT724 | Single Phase Fault with Stuck Breaker on G17-022-TAP 138.00 (588664) 138 kV Bus a. Apply Fault at the G17-022-TAP 138.00 (588664) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-022-TAP (588664) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. G17-022-TAP (588664) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT725 | Single Phase Fault with Stuck Breaker on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply Fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. WESTBORO 3 (635018) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT726 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER_ESST8 (640141) 69.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT727 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT728 | Single Phase Fault with Stuck Breaker on G17-120-TAP 115.00 (760007) 115 kV Bus a. Apply Fault at the G17-120-TAP 115.00 (760007) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-120-TAP (760007) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. G17-120-TAP (760007) 115.0 kV to AEC 3 (533361) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT729 | Single Phase Fault with Stuck Breaker on G17-202-TAP 161.00 (761422) 161 kV Bus a. Apply Fault at the G17-202-TAP 161.00 (761422) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-202-TAP (761422) 161.0 kV to N MADRD5 (505400) 161.0 kV Transmission Circuit #1 b.2. G17-202-TAP (761422) 161.0 kV to GEN-2017-202 (761418) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT730 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 2GIBSON (301291) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT731 | Single Phase Fault with Stuck Breaker on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply Fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASHRVL5 (505441) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.2. ASHRVL5 (505441) 161.0 kV to POP BLF5 (505438) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT732 | Single Phase Fault with Stuck Breaker on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply Fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7NEWMADXF12 (301530) 345.0 kV to 7NEWMAD (300046) 345.0 kV Transmission Circuit #z1 b.2. 7NEWMADXF12 (301530) 345.0 kV to 5NEWMADXF12 (301531) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT733 | Single Phase Fault with Stuck Breaker on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD5 (505412) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 b.2. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT734 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT735 | Single Phase Fault with Stuck Breaker on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply Fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLADN3 (533252) 115.0 kV to MIDLAND6 (532855) 230.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 b.2. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT736 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 b.2. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT737 | Single Phase Fault with Stuck Breaker on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply Fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT3 (533326) 115.0 kV to EMANHAT6 (532861) 230.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 b.2. EMANHAT3 (533326) 115.0 kV to LEVEE 3 (533327) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT738 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRINGH3 (533267) 115.0 kV to SPRGHL 5 (532914) 161.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.2. SPRINGH3 (533267) 115.0 kV to BONITA 3 (533262) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT739 | Single Phase Fault with Stuck Breaker on TECHILW3 115.00 (533181) 115 kV Bus a. Apply Fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT740 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to CRESWLS2 (533573) 69.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 b.2. CRESWLN4 (532981) 138.0 kV to CRESWLN2 (533543) 69.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT741 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT4 (532992) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT742 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT743 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT744 | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT745 | Single Phase Fault with Stuck Breaker on 5SEDALA (300117) 161 kV Bus a. Apply Fault at the 5SEDALA (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT746 | Single Phase Fault with Stuck Breaker on 2HOLDEN (300336) 69 kV Bus a. Apply Fault at the 2HOLDEN (300336) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HOLDEN (300336) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT747 | Single Phase Fault with Stuck Breaker on 2CENTRV (300323) 69 kV Bus a. Apply Fault at the 2CENTRV (300323) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CENTRV (300323) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT748 | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT749 | Single Phase Fault with Stuck Breaker on STHTOWN5 (542993) 161 kV Bus a. Apply Fault at the STHTOWN5 (542993) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHTOWN5 (542993) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT750 | Single Phase Fault with Stuck Breaker on S.HARP 5 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT751 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT752 | Single Phase Fault with Stuck Breaker on PECULR 7 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT753 | Single Phase Fault with Stuck Breaker on PECULR 5 (541342) 161 kV Bus a. Apply Fault at the PECULR 5 (541342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT754 | Single Phase Fault with Stuck Breaker on BELTONS5 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT755 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT756 | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT757 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT758 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT759 | Single Phase Fault with Stuck Breaker on NMANHT3 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHT3 (533347) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT760 | Single Phase Fault with Stuck Breaker on SUMMIT 7 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT761 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT762 | Single Phase Fault with Stuck Breaker on GEARY 3 (533336) 115 kV Bus a. Apply Fault at the GEARY 3 (533336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 3 (533336) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT763 | Single Phase Fault with Stuck Breaker on MCDOWEL3 (533335) 115 kV Bus a. Apply Fault at the MCDOWEL3 (533335) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL3 (533335) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT764 | Single Phase Fault with Stuck Breaker on GEARY 7 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 7 (532767) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT765 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT766 | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT767 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT768 | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT769 | Single Phase Fault with Stuck Breaker on SUMMIT 3 (533381) 115 kV Bus a. Apply Fault at the SUMMIT 3 (533381) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 3 (533381) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT770 | Single Phase Fault with Stuck Breaker on MENTOR 3 (533374) 115 kV Bus a. Apply Fault at the MENTOR 3 (533374) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT771 | Single Phase Fault with Stuck Breaker on NORTHVW3 (533371) 115 kV Bus a. Apply Fault at the NORTHVW3 (533371) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT772 | Single Phase Fault with Stuck Breaker on CRESWLN4 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT773 | Single Phase Fault with Stuck Breaker on TIMBJCT2 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT774 | Single Phase Fault with Stuck Breaker on CRESWLN2 (533543) 69 kV Bus a. Apply Fault at the CRESWLN2 (533543) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT775 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT776 | Single Phase Fault with Stuck Breaker on GILL 4 (533047) 138 kV Bus a. Apply Fault at the GILL 4 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT777 | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT778 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT779 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT780 | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 (533040) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT781 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT782 | Single Phase Fault with Stuck Breaker on RENFROW4 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT783 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT784 | Single Phase Fault with Stuck Breaker on CEDRCRK5 (543049) 161 kV Bus a. Apply Fault at the CEDRCRK5 (543049) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDRCRK5 (543049) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT785 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT786 | Single Phase Fault with Stuck Breaker on SWISVAL6 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT787 | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT788 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT789 | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT790 | Single Phase Fault with Stuck Breaker on TECHILW3 (533181) 115 kV Bus a. Apply Fault at the TECHILW3 (533181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT791 | Single Phase Fault with Stuck Breaker on LWRNCHL3 (533250) 115 kV Bus a. Apply Fault at the LWRNCHL3 (533250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LWRNCHL3 (533250) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT792 | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT793 | Single Phase Fault with Stuck Breaker on TIOGA 2 (533646) 69 kV Bus a. Apply Fault at the TIOGA 2 (533646) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 2 (533646) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT794 | Single Phase Fault with Stuck Breaker on ALTOO E2 (533673) 69 kV Bus a. Apply Fault at the ALTOO E2 (533673) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOO E2 (533673) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT795 | Single Phase Fault with Stuck Breaker on MONTGOM4 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM4 (533004) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT796 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT797 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT798 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT799 | Single Phase Fault with Stuck Breaker on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT800 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT801 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT802 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT803 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT804 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT805 | Single Phase Fault with Stuck Breaker on STRANGR3 (533268) 115 kV Bus a. Apply Fault at the STRANGR3 (533268) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT806 | Single Phase Fault with Stuck Breaker on SMTHVL 5 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT807 | Single Phase Fault with Stuck Breaker on NASHUA 5 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT808 | Single Phase Fault with Stuck Breaker on NASHUA-5 (543028) 161 kV Bus a. Apply Fault at the NASHUA-5 (543028) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT809 | Single Phase Fault with Stuck Breaker on RNRIDGE5 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT810 | Single Phase Fault with Stuck Breaker on HAWTHS5 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT811 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT812 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT813 | Single Phase Fault with Stuck Breaker on EASTOWN5 (541401) 161 kV Bus a. Apply Fault at the EASTOWN5 (541401) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT814 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT815 | Single Phase Fault with Stuck Breaker on ATCHSN 3 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT816 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT817 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT818 | Single Phase Fault with Stuck Breaker on ST JOE 5 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT819 | Single Phase Fault with Stuck Breaker on MIDWAY_5 (541369) 161 kV Bus a. Apply Fault at the MIDWAY_5 (541369) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDWAY_5 (541369) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT820 | Single Phase Fault with Stuck Breaker on LITCH 5 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT821 | Single Phase Fault with Stuck Breaker on ORO110 5 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT822 | Single Phase Fault with Stuck Breaker on ORO110 2 (547534) 69 kV Bus a. Apply Fault at the ORO110 2 (547534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 2 (547534) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT823 | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT824 | Single Phase Fault with Stuck Breaker on FRANKLIN2 (533876) 69 kV Bus a. Apply Fault at the FRANKLIN2 (533876) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN2 (533876) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT825 | Single Phase Fault with Stuck Breaker on AUBURN 6 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT826 | Single Phase Fault with Stuck Breaker on PLSTVAL5 (543077) 161 kV Bus a. Apply Fault at the PLSTVAL5 (543077) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSTVAL5 (543077) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT827 | Single Phase Fault with Stuck Breaker on MOONLT 5 (543044) 161 kV Bus a. Apply Fault at the MOONLT 5 (543044) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLT 5 (543044) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT828 | Single Phase Fault with Stuck Breaker on CRAIG 5 (542978) 161 kV Bus a. Apply Fault at the CRAIG 5 (542978) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT829 | Single Phase Fault with Stuck Breaker on 87TH 7 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT830 | Single Phase Fault with Stuck Breaker on 87TH 3 (533283) 115 kV Bus a. Apply Fault at the 87TH 3 (533283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 3 (533283) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT831 | Single Phase Fault with Stuck Breaker on SIKETAP5 (505427) 161 kV Bus a. Apply Fault at the SIKETAP5 (505427) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIKETAP5 (505427) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT832 | Single Phase Fault with Stuck Breaker on N MADRD2 (505402) 69 kV Bus a. Apply Fault at the N MADRD2 (505402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD2 (505402) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT833 | Single Phase Fault with Stuck Breaker on N MADRD5 (505400) 161 kV Bus a. Apply Fault at the N MADRD5 (505400) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD5 (505400) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT834 | Single Phase Fault with Stuck Breaker on KENNETT5 (505410) 161 kV Bus a. Apply Fault at the KENNETT5 (505410) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENNETT5 (505410) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT835 | Single Phase Fault with Stuck Breaker on PARAGLD5 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD5 (505412) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT836 | Single Phase Fault with Stuck Breaker on 2BAELLS (301286) 69 kV Bus a. Apply Fault at the 2BAELLS (301286) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BAELLS (301286) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT837 | Single Phase Fault with Stuck Breaker on 2ANNSTN (301236) 69 kV Bus a. Apply Fault at the 2ANNSTN (301236) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ANNSTN (301236) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT838 | Single Phase Fault with Stuck Breaker on RIV167 2 (547541) 69 kV Bus a. Apply Fault at the RIV167 2 (547541) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT839 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT840 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT841 | Single Phase Fault with Stuck Breaker on MARMATN2 (533639) 69 kV Bus a. Apply Fault at the MARMATN2 (533639) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT842 | Single Phase Fault with Stuck Breaker on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT843 | Single Phase Fault with Stuck Breaker on SOPITT 2 (533773) 69 kV Bus a. Apply Fault at the SOPITT 2 (533773) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOPITT 2 (533773) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT844 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT845 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT846 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT847 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT848 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT849 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT850 | Single Phase Fault with Stuck Breaker on EXPEDITION7 (532803) 345 kV Bus a. Apply Fault at the EXPEDITION7 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPEDITION7 (532803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT851 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT852 | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT853 | Single Phase Fault with Stuck Breaker on CIRCLE 3 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT854 | Single Phase Fault with Stuck Breaker on MOUNDRG3 (533429) 115 kV Bus a. Apply Fault at the MOUNDRG3 (533429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUNDRG3 (533429) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT855 | Single Phase Fault with Stuck Breaker on CHISHLM4 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_LOCAL_FAULT856 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT1 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT2 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT3 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT4 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT5 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT6 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT7 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT8 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT9 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT10 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT11 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT12 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT13 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT14 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT15 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT16 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT17 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT18 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT19 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT20 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT21 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT22 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT23 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT24 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT25 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT26 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT27 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT28 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT29 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT30 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT31 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT32 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT33 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT34 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT35 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT36 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT37 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT38 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT39 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT40 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT41 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT42 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT43 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT44 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT45 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT46 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT47 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT48 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT49 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT50 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT51 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT52 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT53 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT54 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT55 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT56 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT57 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT58 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT59 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 b.2. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT60 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT61 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT62 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT63 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT64 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT65 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT66 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT67 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT68 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT69 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 b.2. 5MORGANXF2 (301622) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT70 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT71 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT72 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT73 | Single Phase Fault with Stuck Breaker on G17-209-TAP 345.00 (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP 345.00 (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT74 | Single Phase Fault with Stuck Breaker on G15-052T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15-052T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15-052T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT75 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G17-086XFMR (589241) 34.5 kV Two Winding #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT76 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT77 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT78 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT79 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT80 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT81 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT82 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT83 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT84 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT85 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT86 | Single Phase Fault with Stuck Breaker on 7HUBEN (300042) 345 kV Bus a. Apply Fault at the 7HUBEN (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT87 | Single Phase Fault with Stuck Breaker on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT88 | Single Phase Fault with Stuck Breaker on BUFF_DUNES 7 (523118) 345 kV Bus a. Apply Fault at the BUFF_DUNES 7 (523118) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT89 | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT90 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT91 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT92 | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT93 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT94 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT95 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT96 | Single Phase Fault with Stuck Breaker on G16-050-TAP (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT97 | Single Phase Fault with Stuck Breaker on 5MORGANXF2 (301622) 161 kV Bus a. Apply Fault at the 5MORGANXF2 (301622) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT98 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT99 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT100 | Single Phase Fault with Stuck Breaker on GI-95_POI (709500) 345 kV Bus a. Apply Fault at the GI-95_POI (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT101 | Single Phase Fault with Stuck Breaker on LAMAR7 (599950) 345 kV Bus a. Apply Fault at the LAMAR7 (599950) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMAR7 (599950) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT102 | Single Phase Fault with Stuck Breaker on G17-209-TAP (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT103 | Single Phase Fault with Stuck Breaker on G15-052T (560053) 345 kV Bus a. Apply Fault at the G15-052T (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT104 | Single Phase Fault with Stuck Breaker on GEN-2016-153 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT105 | Single Phase Fault with Stuck Breaker on GEN-2017-018 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT106 | Single Phase Fault with Stuck Breaker on G17-183-TAP (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT107 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT108 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT109 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT110 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT111 | Single Phase Fault with Stuck Breaker on THISTLE4 (539804) 138 kV Bus a. Apply Fault at the THISTLE4 (539804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT112 | Single Phase Fault with Stuck Breaker on ST JOE 5 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT113 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P4_REGIONAL_FAULT114 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT2 | 3 Phase fault on CAR395 5 161.00 (547485) 161 kV Bus a. Apply fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.3. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT3 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT4 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT5 | 3 Phase fault on GLENELD3 115.00 (539663) 115 kV Bus a. Apply fault at the GLENELD3 115.00 (539663) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.2. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.3. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.4. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding #1 b.5. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT6 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT7 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT8 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT9 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT10 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT11 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT12 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT13 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT14 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT15 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT16 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT17 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT18 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT19 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT20 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT21 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT22 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT23 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT24 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT25 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT26 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT27 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT28 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT29 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT30 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT31 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT32 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT33 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT34 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT35 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT36 | 3 Phase fault on RICE 6 230.00 (530686) 230 kV Bus a. Apply fault at the RICE 6 230.00 (530686) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT37 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT38 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT39 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT40 | 3 Phase fault on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT41 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT42 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT43 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT44 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT45 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT46 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT47 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT48 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT49 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT50 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT51 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT52 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT53 | 3 Phase fault on BOEINGE4 138.00 (533030) 138 kV Bus a. Apply fault at the BOEINGE4 138.00 (533030) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOEINGE4 (533030) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT54 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT55 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT56 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT57 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT58 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT59 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT60 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT61 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT62 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT63 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT64 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT65 | 3 Phase fault on TCROCK 4 138.00 (532985) 138 kV Bus a. Apply fault at the TCROCK 4 138.00 (532985) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT66 | 3 Phase fault on QUINTON3 115.00 (533172) 115 kV Bus a. Apply fault at the QUINTON3 115.00 (533172) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT67 | 3 Phase fault on 6 GOLDN3 115.00 (533177) 115 kV Bus a. Apply fault at the 6 GOLDN3 115.00 (533177) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT68 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT69 | 3 Phase fault on INDIANH3 115.00 (533166) 115 kV Bus a. Apply fault at the INDIANH3 115.00 (533166) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT70 | 3 Phase fault on 17&FAIR3 115.00 (533175) 115 kV Bus a. Apply fault at the 17&FAIR3 115.00 (533175) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17&FAIR3 (533175) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT71 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT72 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT73 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT74 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT75 | 3 Phase fault on BONITA 3 115.00 (533262) 115 kV Bus a. Apply fault at the BONITA 3 115.00 (533262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONITA 3 (533262) 115.0 kV to SPRINGH3 (533267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT76 | 3 Phase fault on GEARY 3 115.00 (533336) 115 kV Bus a. Apply fault at the GEARY 3 115.00 (533336) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT77 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT78 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT79 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT80 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT81 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT82 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT83 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT84 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT85 | 3 Phase fault on EAST ST3 115.00 (533301) 115 kV Bus a. Apply fault at the EAST ST3 115.00 (533301) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT86 | 3 Phase fault on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT87 | 3 Phase fault on EMANHAT3 115.00 (533326) 115 kV Bus a. Apply fault at the EMANHAT3 115.00 (533326) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT3 (533326) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT88 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to MANVILE3 (533426) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT89 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT90 | 3 Phase fault on FAIRGDS3 115.00 (533236) 115 kV Bus a. Apply fault at the FAIRGDS3 115.00 (533236) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT91 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT92 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to MCDOWEL3 (533335) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT93 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT94 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to GEARY 3 (533336) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT95 | 3 Phase fault on WM BROS3 115.00 (533183) 115 kV Bus a. Apply fault at the WM BROS3 115.00 (533183) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WM BROS3 (533183) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT96 | 3 Phase fault on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT97 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT98 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT99 | 3 Phase fault on KERFORD3 115.00 (533216) 115 kV Bus a. Apply fault at the KERFORD3 115.00 (533216) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERFORD3 (533216) 115.0 kV to NW LEAV3 (533259) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT100 | 3 Phase fault on KSU W 3 115.00 (533333) 115 kV Bus a. Apply fault at the KSU W 3 115.00 (533333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT101 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT102 | 3 Phase fault on MANVILE3 115.00 (533426) 115 kV Bus a. Apply fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT103 | 3 Phase fault on REFINRY3 115.00 (533427) 115 kV Bus a. Apply fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT104 | 3 Phase fault on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT105 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT106 | 3 Phase fault on MORRIS 3 115.00 (533305) 115 kV Bus a. Apply fault at the MORRIS 3 115.00 (533305) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT107 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT108 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to STRANGR3 (533268) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT109 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT110 | 3 Phase fault on STRANGR3 115.00 (533268) 115 kV Bus a. Apply fault at the STRANGR3 115.00 (533268) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRANGR3 (533268) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT111 | 3 Phase fault on UNIONRG3 115.00 (533359) 115 kV Bus a. Apply fault at the UNIONRG3 115.00 (533359) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG3 (533359) 115.0 kV to TCHOPE 3 (533360) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT112 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT113 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT114 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to RA5HIPR2 (533706) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT115 | 3 Phase fault on FRNTR N2 69.000 (533593) 69 kV Bus a. Apply fault at the FRNTR N2 69.000 (533593) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNTR N2 (533593) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT116 | 3 Phase fault on BUTLERN2 69.000 (533583) 69 kV Bus a. Apply fault at the BUTLERN2 69.000 (533583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERN2 (533583) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT117 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT118 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC7CRES2 (533555) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT119 | 3 Phase fault on DAVIS 2 69.000 (533506) 69 kV Bus a. Apply fault at the DAVIS 2 69.000 (533506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 2 (533506) 69.0 kV to MWIRNJ22 (533529) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT120 | 3 Phase fault on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT121 | 3 Phase fault on INDEPEN2 69.000 (533694) 69 kV Bus a. Apply fault at the INDEPEN2 69.000 (533694) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT122 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to MACARTH2 (533813) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT123 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCAN 2 (533850) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT124 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT125 | 3 Phase fault on STROTHR2 69.000 (533556) 69 kV Bus a. Apply fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT126 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT127 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT128 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT129 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT130 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT131 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT132 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT133 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT134 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT135 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT136 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT137 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT138 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT139 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT140 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT141 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT142 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT143 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT144 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT145 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT146 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT147 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT148 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT149 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT150 | 3 Phase fault on 5WEDK 1 161.00 (345975) 161 kV Bus a. Apply fault at the 5WEDK 1 161.00 (345975) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAPE GIR1 (344280) 161.0 kV to 5CAPE GIR2 (344282) 161.0 kV Transmission Circuit #z b.2. 5CAPE GIR1 (344280) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #1 b.3. 5CAPE GIR1 (344280) 161.0 kV to 5WEDK 1 (345975) 161.0 kV Transmission Circuit #1 b.4. 5CHARMN 1 (344338) 161.0 kV to 5TRAIL_TR TP (345824) 161.0 kV Transmission Circuit #1 b.5. 5TRAIL TR (345823) 161.0 kV to 5TRAIL_TR TP (345824) 161.0 kV Transmission Circuit #z b.6. 5WEDK 1 (345975) 161.0 kV to 5WEDK 2 (345984) 161.0 kV Transmission Circuit #z b.7. 1CHARMIN (346035) 13.2 kV to 5CHARMN 1 (344338) 161.0 kV Two Winding #1 b.8. 1CHARMIN (346035) 13.2 kV to 5CHARMN 1 (344338) 161.0 kV Two Winding #2 b.9. 2TRAIL TR (346144) 69.0 kV to 5TRAIL TR (345823) 161.0 kV Two Winding #1 b.10. 1WEDEKIND (346157) 34.5 kV to 5WEDK 1 (345975) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT151 | 3 Phase fault on 5ORAN 161.00 (345375) 161 kV Bus a. Apply fault at the 5ORAN 161.00 (345375) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MORLEY (300121) 161.0 kV to 5ORAN (345375) 161.0 kV Transmission Circuit #1 b.2. 5KELSO 2 (344850) 161.0 kV to 5ORAN (345375) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT152 | 3 Phase fault on 7KELSO 2 345.00 (344849) 345 kV Bus a. Apply fault at the 7KELSO 2 345.00 (344849) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 2 (344849) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT153 | 3 Phase fault on 7LUTESVIL 345.00 (344974) 345 kV Bus a. Apply fault at the 7LUTESVIL 345.00 (344974) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7LUTESVIL (344974) 345.0 kV to 7ST FRANC (345773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT154 | 3 Phase fault on 7HERITAGE 345.00 (345434) 345 kV Bus a. Apply fault at the 7HERITAGE 345.00 (345434) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7LUTESVIL (344974) 345.0 kV to 7HERITAGE (345434) 345.0 kV Transmission Circuit #1 b.2. 7HERITAGE (345434) 345.0 kV to 5HERITAGE 1 (345976) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT155 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7ESSEX (300038) 345.0 kV to 7WNWMADRID1A (301407) 345.0 kV Transmission Circuit #1 b.2. 7ESSEX (300038) 345.0 kV to 7LUTESVIL (344974) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT156 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT157 | 3 Phase fault on 5BARNET 161.00 (300057) 161 kV Bus a. Apply fault at the 5BARNET 161.00 (300057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5BARNET (300057) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT158 | 3 Phase fault on 7KELSO 2 345.00 (344849) 345 kV Bus a. Apply fault at the 7KELSO 2 345.00 (344849) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 2 (344849) 345.0 kV to 5KELSO 2 (344850) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT159 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT160 | 3 Phase fault on 5CAPE GIR2 161.00 (344282) 161 kV Bus a. Apply fault at the 5CAPE GIR2 161.00 (344282) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAPE GIR1 (344280) 161.0 kV to 5CAPE GIR2 (344282) 161.0 kV Transmission Circuit #z b.2. 5CAPE GIR2 (344282) 161.0 kV to 5CAPE GIR3 (344286) 161.0 kV Transmission Circuit #z b.3. 5CAPE GIR2 (344282) 161.0 kV to 5VIADUCT 1 (345894) 161.0 kV Transmission Circuit #z b.4. 5CAPE GIR2 (344282) 161.0 kV to 5JOPPA SR (351006) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT161 | 3 Phase fault on 5CAPE GIR3 161.00 (344286) 161 kV Bus a. Apply fault at the 5CAPE GIR3 161.00 (344286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CAPE GIR2 (344282) 161.0 kV to 5CAPE GIR3 (344286) 161.0 kV Transmission Circuit #z b.2. 5CAPE GIR3 (344286) 161.0 kV to 5VIAD_TP (345891) 161.0 kV Transmission Circuit #2 b.3. 5CAPE GIR3 (344286) 161.0 kV to 5VIADUCT 2 (345893) 161.0 kV Transmission Circuit #z b.4. 5CAPE GIR3 (344286) 161.0 kV to 5HERITAGE 1 (345976) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT162 | 3 Phase fault on 8NEWMAD 500.00 (300035) 500 kV Bus a. Apply fault at the 8NEWMAD 500.00 (300035) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8NEWMAD (300035) 500.0 kV to 8WNEWMADRID (301406) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT163 | 3 Phase fault on 7STFRAN 345.00 (300048) 345 kV Bus a. Apply fault at the 7STFRAN 345.00 (300048) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7STFRAN (300048) 345.0 kV to 7GOBKNOB (300054) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT164 | 3 Phase fault on 5ESSEX 161.00 (300075) 161 kV Bus a. Apply fault at the 5ESSEX 161.00 (300075) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ESSEX (300075) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT165 | 3 Phase fault on 5GRNFRT 161.00 (300084) 161 kV Bus a. Apply fault at the 5GRNFRT 161.00 (300084) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRNFRT (300084) 161.0 kV to POP BLF5 (505438) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT166 | 3 Phase fault on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 b.3. 2GIBSON (301291) 69.0 kV to 5GIBSON (300083) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT167 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT168 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to N MADRD5 (505400) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT169 | 3 Phase fault on 2CAMBEL 69.000 (301196) 69 kV Bus a. Apply fault at the 2CAMBEL 69.000 (301196) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CAMBEL (301196) 69.0 kV to 2GIBSON (301291) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT170 | 3 Phase fault on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT171 | 3 Phase fault on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT172 | 3 Phase fault on 2GIBSON 69.000 (301291) 69 kV Bus a. Apply fault at the 2GIBSON 69.000 (301291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GIBSON (301291) 69.0 kV to 2KENNET (301294) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT173 | 3 Phase fault on 2GIBSON 69.000 (301291) 69 kV Bus a. Apply fault at the 2GIBSON 69.000 (301291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GIBSON (301291) 69.0 kV to 2CLARKTON (301432) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT174 | 3 Phase fault on 8POWERLN_RD%500.00 (338156) 500 kV Bus a. Apply fault at the 8POWERLN_RD%500.00 (338156) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8POWERLN_RD% (338156) 500.0 kV to 8DELL% (338187) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT175 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 5DELL# (338596) 161.0 kV to 1DELL T1 (338597) 13.8 kV Three Winding #1 b.2. 8DELL% (338187) 500.0 kV to 5DELL# (338596) 161.0 kV to 1DELL T2 (338598) 13.8 kV Three Winding #1 b.3. 8DELL% (338187) 500.0 kV to 5DELL# (338596) 161.0 kV to 1DELL T3 (338599) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT176 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 8SANS SOUCI% (338188) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT177 | 3 Phase fault on 5STEELE! 161.00 (338194) 161 kV Bus a. Apply fault at the 5STEELE! 161.00 (338194) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STEELE! (338194) 161.0 kV to 5HAYTI.S% (338200) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT178 | 3 Phase fault on 5HAYTI.S% 161.00 (338200) 161 kV Bus a. Apply fault at the 5HAYTI.S% 161.00 (338200) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HAYTI.S% (338200) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT179 | 3 Phase fault on 5JIM HILL% 161.00 (338202) 161 kV Bus a. Apply fault at the 5JIM HILL% 161.00 (338202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JIM HILL% (338202) 161.0 kV to 5RECTOR.N# (338689) 161.0 kV Transmission Circuit #1 b.2. 5PARAGOULD% (338204) 161.0 kV to 5HALLIDAY# (338709) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT180 | 3 Phase fault on N MADRD5 161.00 (505400) 161 kV Bus a. Apply fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X1 1 (505401) 13.8 kV Three Winding #1 b.2. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X2 1 (505403) 13.8 kV Three Winding #1 b.3. NMA X1 1 (505401) 13.8 kV to N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV Three Winding #1 b.6. NMA X2 1 (505403) 13.8 kV to N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT181 | 3 Phase fault on N MADRD5 161.00 (505400) 161 kV Bus a. Apply fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD5 (505400) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT182 | 3 Phase fault on KENNETT5 161.00 (505410) 161 kV Bus a. Apply fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEN X1 1 (505407) 13.8 kV to KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV Three Winding #1 b.3. KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV to KEN X2 1 (505409) 13.8 kV Three Winding #1 b.5. KENNETT5 (505410) 161.0 kV to KENNETT2 (505408) 69.0 kV to KEN X1 1 (505407) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT183 | 3 Phase fault on KENNETT5 161.00 (505410) 161 kV Bus a. Apply fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENNETT5 (505410) 161.0 kV to PARAGLD5 (505412) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT184 | 3 Phase fault on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRG X1 1 (505411) 13.8 kV to PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV Three Winding #1 b.2. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X1 1 (505411) 13.8 kV Three Winding #1 b.3. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X2 1 (505413) 13.8 kV Three Winding #1 b.4. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X3 1 (505415) 13.8 kV Three Winding #1 b.5. PRG X2 1 (505413) 13.8 kV to PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV Three Winding #1 b.9. PRG X3 1 (505415) 13.8 kV to PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT185 | 3 Phase fault on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT186 | 3 Phase fault on CENTR H5 161.00 (505416) 161 kV Bus a. Apply fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTR H5 (505416) 161.0 kV to JONESBO5 (505418) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT187 | 3 Phase fault on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKESTN5 (505428) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT188 | 3 Phase fault on POP BLF5 161.00 (505438) 161 kV Bus a. Apply fault at the POP BLF5 161.00 (505438) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PBL X1 1 (505435) 13.8 kV to POP BLF2 (505436) 69.0 kV to POP BLF5 (505438) 161.0 kV Three Winding #1 b.3. POP BLF2 (505436) 69.0 kV to POP BLF5 (505438) 161.0 kV to PBL X2 1 (505437) 13.8 kV Three Winding #1 b.4. POP BLF2 (505436) 69.0 kV to POP BLF5 (505438) 161.0 kV to PBL X3 1 (505439) 13.8 kV Three Winding #1 b.6. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X1 1 (505435) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT189 | 3 Phase fault on KENNETT5 161.00 (505410) 161 kV Bus a. Apply fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENNETT5 (505410) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT190 | 3 Phase fault on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGLD5 (505412) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT191 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT192 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT193 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT194 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT195 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT196 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT197 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT198 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT199 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT200 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT201 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT201 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT202 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT203 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT204 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT205 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT206 | 3 Phase fault on 5STFRANB2 161.00 (300115) 161 kV Bus a. Apply fault at the 5STFRANB2 161.00 (300115) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STFRANB2 (300115) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT207 | 3 Phase fault on 8WNEWMADRID 500.00 (301406) 500 kV Bus a. Apply fault at the 8WNEWMADRID 500.00 (301406) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8WNEWMADRID (301406) 500.0 kV to 8DELL% (338187) 500.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT208 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT209 | 3 Phase fault on 5PORTAGEVLE 161.00 (338201) 161 kV Bus a. Apply fault at the 5PORTAGEVLE 161.00 (338201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.3. 5PORTAGEVLE (338201) 161.0 kV to 1PORTGVIL (345534) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT210 | 3 Phase fault on 5PORTAGEVLE 161.00 (338201) 161 kV Bus a. Apply fault at the 5PORTAGEVLE 161.00 (338201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 8W.MEMPHIS% (338162) 500.0 kV to 8BHAM STEEL (360075) 500.0 kV Transmission Circuit #1 b.3. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT211 | 3 Phase fault on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT212 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT213 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT214 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT215 | 3 Phase fault on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT216 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT217 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT218 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT219 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT220 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT221 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT222 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT223 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT224 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT225 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT226 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT227 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT228 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT229 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT230 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT231 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT232 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to KERFORD3 (533216) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT233 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT234 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT235 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT236 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT237 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT238 | 3 Phase fault on 41CALIF3 115.00 (533160) 115 kV Bus a. Apply fault at the 41CALIF3 115.00 (533160) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT239 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to AMELIA 3 (533215) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT240 | 3 Phase fault on S GAGEE3 115.00 (533178) 115 kV Bus a. Apply fault at the S GAGEE3 115.00 (533178) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT241 | 3 Phase fault on CORONAD3 115.00 (533394) 115 kV Bus a. Apply fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT242 | 3 Phase fault on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT243 | 3 Phase fault on LEC U4 3 115.00 (533249) 115 kV Bus a. Apply fault at the LEC U4 3 115.00 (533249) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT244 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT245 | 3 Phase fault on MIDIANW2 69.000 (533597) 69 kV Bus a. Apply fault at the MIDIANW2 69.000 (533597) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIANW2 (533597) 69.0 kV to THUNBRD2 (533603) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT246 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT247 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT248 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT249 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT250 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT251 | 3 Phase fault on COMOTAR4 138.00 (533037) 138 kV Bus a. Apply fault at the COMOTAR4 138.00 (533037) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT252 | 3 Phase fault on INTERST4 138.00 (533051) 138 kV Bus a. Apply fault at the INTERST4 138.00 (533051) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT253 | 3 Phase fault on 43LORAN 115.00 (533440) 115 kV Bus a. Apply fault at the 43LORAN 115.00 (533440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.3. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT254 | 3 Phase fault on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWRNCHL3 (533250) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT255 | 3 Phase fault on PEIL 3 115.00 (533343) 115 kV Bus a. Apply fault at the PEIL 3 115.00 (533343) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PEIL 3 (533343) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.2. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT256 | 3 Phase fault on FRONTEN2 69.000 (533775) 69 kV Bus a. Apply fault at the FRONTEN2 69.000 (533775) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.2. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT257 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 b.5. DEARING1 (533089) 13.2 kV to DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT258 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 b.4. LIBERTY1 (533090) 13.2 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT259 | 3 Phase fault on NINMLTP4 138.00 (521128) 138 kV Bus a. Apply fault at the NINMLTP4 138.00 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT260 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT261 | 3 Phase fault on CDRDLTP4 138.00 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 138.00 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT262 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT263 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT264 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT265 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT266 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT267 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT268 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to CLINTON5 (541242) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT269 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT270 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT271 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT272 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT273 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT274 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT275 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT276 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT277 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT278 | 3 Phase fault on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. MIDLAND6 (532855) 230.0 kV to MIDLADN3 (533252) 115.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT279 | 3 Phase fault on TECHILL6 230.00 (532857) 230 kV Bus a. Apply fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT280 | 3 Phase fault on FOWLER 4 138.00 (533043) 138 kV Bus a. Apply fault at the FOWLER 4 138.00 (533043) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT281 | 3 Phase fault on 47TH ST4 138.00 (533058) 138 kV Bus a. Apply fault at the 47TH ST4 138.00 (533058) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. 47TH ST4 (533058) 138.0 kV to 64TH 4 (533066) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT282 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT283 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT284 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT285 | 3 Phase fault on TALLGRS4 138.00 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 138.00 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT286 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT287 | 3 Phase fault on CENTENN4 138.00 (533034) 138 kV Bus a. Apply fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT288 | 3 Phase fault on OXFORD 4 138.00 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 138.00 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT289 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT290 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT291 | 3 Phase fault on SC10BEL4 138.00 (533063) 138 kV Bus a. Apply fault at the SC10BEL4 138.00 (533063) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT292 | 3 Phase fault on BU11PON4 138.00 (533032) 138 kV Bus a. Apply fault at the BU11PON4 138.00 (533032) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT293 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT294 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT295 | 3 Phase fault on BEECHTP4 138.00 (533028) 138 kV Bus a. Apply fault at the BEECHTP4 138.00 (533028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.2. BEECH 4 (533027) 138.0 kV to BEECHTP4 (533028) 138.0 kV Transmission Circuit #1 b.3. BEECHTP4 (533028) 138.0 kV to HARRY 4 (533048) 138.0 kV Transmission Circuit #1 b.4. BEECHTP4 (533028) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT296 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT297 | 3 Phase fault on ANDOVER4 138.00 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 138.00 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT298 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT299 | 3 Phase fault on 29EVENG3 115.00 (533185) 115 kV Bus a. Apply fault at the 29EVENG3 115.00 (533185) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT300 | 3 Phase fault on SALTCRK3 115.00 (533434) 115 kV Bus a. Apply fault at the SALTCRK3 115.00 (533434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.2. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT301 | 3 Phase fault on 27CROCO3 115.00 (533187) 115 kV Bus a. Apply fault at the 27CROCO3 115.00 (533187) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT302 | 3 Phase fault on N TYLER3 115.00 (533168) 115 kV Bus a. Apply fault at the N TYLER3 115.00 (533168) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to N TYLER3 (533168) 115.0 kV Transmission Circuit #1 b.2. N TYLER3 (533168) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT303 | 3 Phase fault on FMC 3 115.00 (533241) 115 kV Bus a. Apply fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.2. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT304 | 3 Phase fault on EUDORA 3 115.00 (533240) 115 kV Bus a. Apply fault at the EUDORA 3 115.00 (533240) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.2. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT305 | 3 Phase fault on MNTCLLO3 115.00 (533281) 115 kV Bus a. Apply fault at the MNTCLLO3 115.00 (533281) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT306 | 3 Phase fault on EABILEN3 115.00 (533365) 115 kV Bus a. Apply fault at the EABILEN3 115.00 (533365) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT307 | 3 Phase fault on JCTCTY 3 115.00 (533330) 115 kV Bus a. Apply fault at the JCTCTY 3 115.00 (533330) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANZIO 3 (533321) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to JCTCTY 3 (533330) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT308 | 3 Phase fault on PARALEL3 115.00 (533218) 115 kV Bus a. Apply fault at the PARALEL3 115.00 (533218) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to PARALEL3 (533218) 115.0 kV Transmission Circuit #1 b.2. PARALEL3 (533218) 115.0 kV to WALNUT 3 (533220) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT309 | 3 Phase fault on SHERWOD3 115.00 (533194) 115 kV Bus a. Apply fault at the SHERWOD3 115.00 (533194) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT310 | 3 Phase fault on KEENE 3 115.00 (533167) 115 kV Bus a. Apply fault at the KEENE 3 115.00 (533167) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 b.2. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT311 | 3 Phase fault on SOUTHTN3 115.00 (533265) 115 kV Bus a. Apply fault at the SOUTHTN3 115.00 (533265) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.2. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT312 | 3 Phase fault on FORBES 3 115.00 (533157) 115 kV Bus a. Apply fault at the FORBES 3 115.00 (533157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FORBES 3 (533157) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.2. FORBES 3 (533157) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT313 | 3 Phase fault on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT314 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT315 | 3 Phase fault on 54&MERI3 115.00 (533156) 115 kV Bus a. Apply fault at the 54&MERI3 115.00 (533156) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT316 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT317 | 3 Phase fault on LEVEE 3 115.00 (533327) 115 kV Bus a. Apply fault at the LEVEE 3 115.00 (533327) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMANHAT3 (533326) 115.0 kV to LEVEE 3 (533327) 115.0 kV Transmission Circuit #1 b.2. LEVEE 3 (533327) 115.0 kV to MATTERS3 (533334) 115.0 kV Transmission Circuit #1 b.3. MATTERS3 (533334) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT318 | 3 Phase fault on BISMARK3 115.00 (533234) 115 kV Bus a. Apply fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT319 | 3 Phase fault on OSAGE J3 115.00 (533171) 115 kV Bus a. Apply fault at the OSAGE J3 115.00 (533171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.2. OSAGE 3 (533170) 115.0 kV to OSAGE J3 (533171) 115.0 kV Transmission Circuit #1 b.3. OSAGE J3 (533171) 115.0 kV to SCRANTN3 (533173) 115.0 kV Transmission Circuit #1 b.4. OSAGE J3 (533171) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.5. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT320 | 3 Phase fault on NTHLAND3 115.00 (533169) 115 kV Bus a. Apply fault at the NTHLAND3 115.00 (533169) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.2. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT321 | 3 Phase fault on TONGATP3 115.00 (533219) 115 kV Bus a. Apply fault at the TONGATP3 115.00 (533219) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONGATP3 (533219) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT322 | 3 Phase fault on 166TH 3 115.00 (533233) 115 kV Bus a. Apply fault at the 166TH 3 115.00 (533233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 166TH 3 (533233) 115.0 kV to JAGGARD3 (533243) 115.0 kV Transmission Circuit #1 b.2. 166TH 3 (533233) 115.0 kV to JARBALO3 (533244) 115.0 kV Transmission Circuit #1 b.3. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT323 | 3 Phase fault on HALLMRK3 115.00 (533242) 115 kV Bus a. Apply fault at the HALLMRK3 115.00 (533242) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALLMRK3 (533242) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 b.2. HALLMRK3 (533242) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. JARBALO3 (533244) 115.0 kV to EFAIRMNT3 (533246) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT324 | 3 Phase fault on PRAIRIE3 115.00 (533307) 115 kV Bus a. Apply fault at the PRAIRIE3 115.00 (533307) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.2. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT325 | 3 Phase fault on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT326 | 3 Phase fault on STULL T3 115.00 (533270) 115 kV Bus a. Apply fault at the STULL T3 115.00 (533270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.3. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.5. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT327 | 3 Phase fault on STAGGHL3 115.00 (533341) 115 kV Bus a. Apply fault at the STAGGHL3 115.00 (533341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.2. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT328 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT329 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT330 | 3 Phase fault on NORTHST3 115.00 (533370) 115 kV Bus a. Apply fault at the NORTHST3 115.00 (533370) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT331 | 3 Phase fault on FRTLEAV3 115.00 (533274) 115 kV Bus a. Apply fault at the FRTLEAV3 115.00 (533274) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 b.2. SPRUCE 3 (533266) 115.0 kV to THORNTN3 (533272) 115.0 kV Transmission Circuit #1 b.3. SPRUCE 3 (533266) 115.0 kV to FRTLEAV3 (533274) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT332 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT333 | 3 Phase fault on MAPLE J2 69.000 (533516) 69 kV Bus a. Apply fault at the MAPLE J2 69.000 (533516) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 2 (533506) 69.0 kV to MAPLE J2 (533516) 69.0 kV Transmission Circuit #1 b.2. E MADSN2 (533508) 69.0 kV to F MONRO2 (533510) 69.0 kV Transmission Circuit #1 b.3. E MADSN2 (533508) 69.0 kV to MAPLE J2 (533516) 69.0 kV Transmission Circuit #1 b.4. E MADSN2 (533508) 69.0 kV to 3 VANBU2 (533527) 69.0 kV Transmission Circuit #1 b.5. MAPLE J2 (533516) 69.0 kV to 2ND ELM2 (533520) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT334 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT335 | 3 Phase fault on ARCOTAP2 69.000 (533620) 69 kV Bus a. Apply fault at the ARCOTAP2 69.000 (533620) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCO 2 (533619) 69.0 kV to ARCOTAP2 (533620) 69.0 kV Transmission Circuit #1 b.2. ARCOTAP2 (533620) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.3. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.4. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.6. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT336 | 3 Phase fault on PARIS 2 69.000 (533548) 69 kV Bus a. Apply fault at the PARIS 2 69.000 (533548) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYW2 (533540) 69.0 kV to PARIS 2 (533548) 69.0 kV Transmission Circuit #1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT337 | 3 Phase fault on SC5SILV2 69.000 (533554) 69 kV Bus a. Apply fault at the SC5SILV2 69.000 (533554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKCTYE2 (533542) 69.0 kV to SC5SILV2 (533554) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.3. SC5SILV2 (533554) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT338 | 3 Phase fault on ROCKCRK2 69.000 (533458) 69 kV Bus a. Apply fault at the ROCKCRK2 69.000 (533458) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 2 (533456) 69.0 kV to ROCKCRK2 (533458) 69.0 kV Transmission Circuit #1 b.2. ROCKCRK2 (533458) 69.0 kV to VALLEY22 (533483) 69.0 kV Transmission Circuit #1 b.3. ARNOLD 2 (533471) 69.0 kV to NORTONV2 (533481) 69.0 kV Transmission Circuit #1 b.4. NORTONV2 (533481) 69.0 kV to VALLEY22 (533483) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT339 | 3 Phase fault on ORCHARD2 69.000 (533643) 69 kV Bus a. Apply fault at the ORCHARD2 69.000 (533643) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.3. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT340 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT341 | 3 Phase fault on SC4ROME2 69.000 (533553) 69 kV Bus a. Apply fault at the SC4ROME2 69.000 (533553) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to SC4ROME2 (533553) 69.0 kV Transmission Circuit #1 b.2. SC3MILL2 (533552) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 b.3. SC3MILL2 (533552) 69.0 kV to BELL 2 (533783) 69.0 kV Transmission Circuit #1 b.4. SC4ROME2 (533553) 69.0 kV to WELLING2 (533560) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT342 | 3 Phase fault on PECK 2 69.000 (533830) 69 kV Bus a. Apply fault at the PECK 2 69.000 (533830) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELL 2 (533783) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 b.2. GILL W 2 (533796) 69.0 kV to HAYSVJS2 (533802) 69.0 kV Transmission Circuit #1 b.3. HAYSVJS2 (533802) 69.0 kV to PECK 2 (533830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT343 | 3 Phase fault on MIDIANE2 69.000 (533610) 69 kV Bus a. Apply fault at the MIDIANE2 69.000 (533610) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERN2 (533583) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #1 b.2. MIDIANE2 (533610) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT344 | 3 Phase fault on BU5FURL2 69.000 (533861) 69 kV Bus a. Apply fault at the BU5FURL2 69.000 (533861) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. THUNBRD2 (533603) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 b.2. CHISHLM2 (533786) 69.0 kV to GRANT 2 (533799) 69.0 kV Transmission Circuit #1 b.3. GRANT 2 (533799) 69.0 kV to BU5FURL2 (533861) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT345 | 3 Phase fault on HYDROTP2 69.000 (533833) 69 kV Bus a. Apply fault at the HYDROTP2 69.000 (533833) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMAN2 (533787) 69.0 kV to HYDROTP2 (533833) 69.0 kV Transmission Circuit #1 b.2. RENEW 2 (533831) 69.0 kV to HYDROTP2 (533833) 69.0 kV Transmission Circuit #1 b.3. RENEW 2 (533831) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT346 | 3 Phase fault on COFFSUB2 69.000 (533683) 69 kV Bus a. Apply fault at the COFFSUB2 69.000 (533683) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFSUB2 (533683) 69.0 kV to CRA S 2 (533685) 69.0 kV Transmission Circuit #1 b.2. COFFSUB2 (533683) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT347 | 3 Phase fault on BEECRK2 69.000 (533677) 69 kV Bus a. Apply fault at the BEECRK2 69.000 (533677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEECRK2 (533677) 69.0 kV to CANEY 2 (533678) 69.0 kV Transmission Circuit #1 b.2. BEECRK2 (533677) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.3. BEECRK2 (533677) 69.0 kV to COBBTAP2 (533710) 69.0 kV Transmission Circuit #1 b.4. BEECRK2 (533677) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT348 | 3 Phase fault on ROUSE 2 69.000 (533771) 69 kV Bus a. Apply fault at the ROUSE 2 69.000 (533771) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.2. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT349 | 3 Phase fault on WILLJCT2 69.000 (533713) 69 kV Bus a. Apply fault at the WILLJCT2 69.000 (533713) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.2. WILLJCT2 (533713) 69.0 kV to ELKJSS 2 (533718) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT350 | 3 Phase fault on WARE 2 69.000 (533652) 69 kV Bus a. Apply fault at the WARE 2 69.000 (533652) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.2. WARE 2 (533652) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 b.3. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT351 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT352 | 3 Phase fault on PITNAC 2 69.000 (533769) 69 kV Bus a. Apply fault at the PITNAC 2 69.000 (533769) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.2. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.3. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT353 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT354 | 3 Phase fault on AQUARS 2 69.000 (533756) 69 kV Bus a. Apply fault at the AQUARS 2 69.000 (533756) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AQUARS 2 (533756) 69.0 kV to HUDSJCT2 (533764) 69.0 kV Transmission Circuit #1 b.2. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.3. HUDSJCT2 (533764) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT355 | 3 Phase fault on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT356 | 3 Phase fault on ADA 2 69.000 (533581) 69 kV Bus a. Apply fault at the ADA 2 69.000 (533581) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ADA 2 (533581) 69.0 kV to ELDORAD2 (533590) 69.0 kV Transmission Circuit #1 b.2. ADA 2 (533581) 69.0 kV to PESTER 2 (533600) 69.0 kV Transmission Circuit #1 b.3. CHESNEY2 (533589) 69.0 kV to MIDIANW2 (533597) 69.0 kV Transmission Circuit #1 b.4. CHESNEY2 (533589) 69.0 kV to PESTER 2 (533600) 69.0 kV Transmission Circuit #1 b.5. ELDORAD2 (533590) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT357 | 3 Phase fault on HAYSVJN2 69.000 (533804) 69 kV Bus a. Apply fault at the HAYSVJN2 69.000 (533804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to HAYSVJN2 (533804) 69.0 kV Transmission Circuit #1 b.2. HAYSVJN2 (533804) 69.0 kV to MIDLAND2 (533816) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT358 | 3 Phase fault on VULCTP 2 69.000 (533851) 69 kV Bus a. Apply fault at the VULCTP 2 69.000 (533851) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.2. LIN 2 (533812) 69.0 kV to VULCTP 2 (533851) 69.0 kV Transmission Circuit #1 b.3. LIN 2 (533812) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 b.4. SUNSET-2 (533844) 69.0 kV to SG1CHEN2 (533871) 69.0 kV Transmission Circuit #1 b.5. SG1CHEN2 (533871) 69.0 kV to SG8CRAG2 (533873) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT359 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT360 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT361 | 3 Phase fault on RAINBOW2 69.000 (533549) 69 kV Bus a. Apply fault at the RAINBOW2 69.000 (533549) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT362 | 3 Phase fault on RICHLAN2 69.000 (533550) 69 kV Bus a. Apply fault at the RICHLAN2 69.000 (533550) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.3. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.4. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT363 | 3 Phase fault on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.2. ASHGRV22 (533658) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.3. ASHGRJ12 (533659) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #z1 b.4. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT364 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT365 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT366 | 3 Phase fault on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT367 | 3 Phase fault on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT368 | 3 Phase fault on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.3. FREEMAN2 (541291) 69.0 kV to FREEMAN_SP2 (541540) 69.0 kV Transmission Circuit #1 b.4. ANCONDA2 (541292) 69.0 kV to HSNVLW 2 (541293) 69.0 kV Transmission Circuit #1 b.5. HSNVLW 2 (541293) 69.0 kV to HSNVLS 2 (541294) 69.0 kV Transmission Circuit #1 b.6. HSNVLS 2 (541294) 69.0 kV to HSNVL 2 (541295) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT369 | 3 Phase fault on STALEY 2 69.000 (541261) 69 kV Bus a. Apply fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT370 | 3 Phase fault on RAYMORE 69.000 (541347) 69 kV Bus a. Apply fault at the RAYMORE 69.000 (541347) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to RAYMORE (541347) 69.0 kV Transmission Circuit #1 b.2. BELTONS2 (541290) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 b.3. RAYMORE (541347) 69.0 kV to RAYTAP (541348) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT371 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT372 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT373 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT374 | 3 Phase fault on STERLNG7 115.00 (640362) 115 kV Bus a. Apply fault at the STERLNG7 115.00 (640362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV to STERLNG7 (640362) 115.0 kV Transmission Circuit #1 b.2. FIRTH 7 (640171) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 b.3. FIRTH 7 (640171) 115.0 kV to FIRTH 9 (640172) 34.5 kV to FIRTH T1 9 (643057) 13.8 kV Three Winding #1 b.5. STERLNG7 (640362) 115.0 kV to S974 8 (647974) 69.0 kV to STERLING T19 (643144) 13.8 kV Three Winding #1 b.6. FIRTH T1 9 (643057) 13.8 kV to FIRTH 9 (640172) 34.5 kV to FIRTH 7 (640171) 115.0 kV Three Winding #1 b.7. STERLING T19 (643144) 13.8 kV to S974 8 (647974) 69.0 kV to STERLNG7 (640362) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT375 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT376 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT377 | 3 Phase fault on KAW W 5 161.00 (546655) 161 kV Bus a. Apply fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT378 | 3 Phase fault on MAYSOTH5 161.00 (546722) 161 kV Bus a. Apply fault at the MAYSOTH5 161.00 (546722) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT379 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT380 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT381 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT382 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT383 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT384 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT385 | 3 Phase fault on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.3. EMANHAT6 (532861) 230.0 kV to EMANHAT3 (533326) 115.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT386 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT387 | 3 Phase fault on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT388 | 3 Phase fault on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT389 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT390 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 b.4. MONTGOM1 (533091) 13.2 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT391 | 3 Phase fault on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.3. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT392 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT393 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT394 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT395 | 3 Phase fault on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 3 (533151) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT396 | 3 Phase fault on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPMAN3 (533362) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT397 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT398 | 3 Phase fault on FT JCT 3 115.00 (533328) 115 kV Bus a. Apply fault at the FT JCT 3 115.00 (533328) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FT JCT 3 (533328) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT399 | 3 Phase fault on HARTLND3 115.00 (533197) 115 kV Bus a. Apply fault at the HARTLND3 115.00 (533197) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTLND3 (533197) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT400 | 3 Phase fault on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INDNOLA3 (533162) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT401 | 3 Phase fault on JARBALO3 115.00 (533244) 115 kV Bus a. Apply fault at the JARBALO3 115.00 (533244) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JARBALO3 (533244) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT402 | 3 Phase fault on KSU E 3 115.00 (533346) 115 kV Bus a. Apply fault at the KSU E 3 115.00 (533346) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSU E 3 (533346) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT403 | 3 Phase fault on NMANHT3 115.00 (533347) 115 kV Bus a. Apply fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT3 (533347) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT404 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT405 | 3 Phase fault on NW LEAV3 115.00 (533259) 115 kV Bus a. Apply fault at the NW LEAV3 115.00 (533259) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NW LEAV3 (533259) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT406 | 3 Phase fault on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBRLN3 (533273) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT407 | 3 Phase fault on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAUGHN 3 (533308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT408 | 3 Phase fault on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT409 | 3 Phase fault on WILDCAT3 115.00 (533345) 115 kV Bus a. Apply fault at the WILDCAT3 115.00 (533345) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILDCAT3 (533345) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT410 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT411 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT412 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT413 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN4 (532981) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT414 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT415 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT416 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT417 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT4 (532992) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT418 | 3 Phase fault on ALTOO E2 69.000 (533673) 69 kV Bus a. Apply fault at the ALTOO E2 69.000 (533673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT419 | 3 Phase fault on ALTOO W2 69.000 (533674) 69 kV Bus a. Apply fault at the ALTOO W2 69.000 (533674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT420 | 3 Phase fault on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM2 (533786) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT421 | 3 Phase fault on COALCRK2 69.000 (533633) 69 kV Bus a. Apply fault at the COALCRK2 69.000 (533633) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALCRK2 (533633) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT422 | 3 Phase fault on DAVIS 2 69.000 (533506) 69 kV Bus a. Apply fault at the DAVIS 2 69.000 (533506) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 2 (533506) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT423 | 3 Phase fault on DEARING2 69.000 (533688) 69 kV Bus a. Apply fault at the DEARING2 69.000 (533688) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT424 | 3 Phase fault on MONTGOM2 69.000 (533698) 69 kV Bus a. Apply fault at the MONTGOM2 69.000 (533698) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT425 | 3 Phase fault on MULBERY2 69.000 (533767) 69 kV Bus a. Apply fault at the MULBERY2 69.000 (533767) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MULBERY2 (533767) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT426 | 3 Phase fault on GILL W 2 69.000 (533796) 69 kV Bus a. Apply fault at the GILL W 2 69.000 (533796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 2 (533796) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT427 | 3 Phase fault on OAK 2 69.000 (533547) 69 kV Bus a. Apply fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK 2 (533547) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT428 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT429 | 3 Phase fault on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT430 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT431 | 3 Phase fault on UDALL 2 69.000 (533559) 69 kV Bus a. Apply fault at the UDALL 2 69.000 (533559) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UDALL 2 (533559) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT432 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT433 | 3 Phase fault on WAVERLY3 115.00 (533278) 115 kV Bus a. Apply fault at the WAVERLY3 115.00 (533278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.2. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT434 | 3 Phase fault on 19THST 3 115.00 (533256) 115 kV Bus a. Apply fault at the 19THST 3 115.00 (533256) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRGDS3 (533236) 115.0 kV to 19THST 3 (533256) 115.0 kV Transmission Circuit #1 b.2. 19THST 3 (533256) 115.0 kV to FREESTATE3 (533257) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT435 | 3 Phase fault on CARB-KW 3 115.00 (533195) 115 kV Bus a. Apply fault at the CARB-KW 3 115.00 (533195) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.2. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT436 | 3 Phase fault on FREESTATE3 115.00 (533257) 115 kV Bus a. Apply fault at the FREESTATE3 115.00 (533257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT437 | 3 Phase fault on SHAWNEE3 115.00 (533176) 115 kV Bus a. Apply fault at the SHAWNEE3 115.00 (533176) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT438 | 3 Phase fault on CRAWFRD3 115.00 (533364) 115 kV Bus a. Apply fault at the CRAWFRD3 115.00 (533364) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. CRAWFRD3 (533364) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 b.3. MENTOR 3 (533374) 115.0 kV to SCHILNG3 (533377) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT439 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT440 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT441 | 3 Phase fault on MOONLIT3 115.00 (533254) 115 kV Bus a. Apply fault at the MOONLIT3 115.00 (533254) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT442 | 3 Phase fault on SO GATE3 115.00 (533379) 115 kV Bus a. Apply fault at the SO GATE3 115.00 (533379) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.2. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT443 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT444 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT445 | 3 Phase fault on DEERCRK2 69.000 (533457) 69 kV Bus a. Apply fault at the DEERCRK2 69.000 (533457) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 2 (533456) 69.0 kV to DEERCRK2 (533457) 69.0 kV Transmission Circuit #1 b.2. DEERCRK2 (533457) 69.0 kV to SANTAFJ2 (533460) 69.0 kV Transmission Circuit #1 b.3. SANTAFJ2 (533460) 69.0 kV to 2MADISN2 (533461) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT446 | 3 Phase fault on LITCH S2 69.000 (533766) 69 kV Bus a. Apply fault at the LITCH S2 69.000 (533766) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT447 | 3 Phase fault on HUDSON-2 69.000 (533763) 69 kV Bus a. Apply fault at the HUDSON-2 69.000 (533763) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUDSON-2 (533763) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT448 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT449 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT450 | 3 Phase fault on SPRINGH3 115.00 (533267) 115 kV Bus a. Apply fault at the SPRINGH3 115.00 (533267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRINGH3 (533267) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT451 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT452 | 3 Phase fault on CLATONA7 115.00 (640111) 115 kV Bus a. Apply fault at the CLATONA7 115.00 (640111) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to CLATONA7 (640111) 115.0 kV Transmission Circuit #1 b.2. CLATONA7 (640111) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT453 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT454 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT455 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT7 (640235) 115.0 kV to HUMBOLT5 (640234) 161.0 kV to HUMBOLDT T29 (643087) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT456 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT457 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT458 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT459 | 3 Phase fault on COOPER 869.000 (640446) 69 kV Bus a. Apply fault at the COOPER 869.000 (640446) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT460 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT461 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT462 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT463 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT464 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT465 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT466 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT467 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT468 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT469 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT470 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT471 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT472 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT473 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT474 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT475 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT476 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT477 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT478 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT479 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT480 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT481 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT482 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT483 | 3 Phase fault on S1250 5 161 (646250) 161 kV Bus a. Apply fault at the S1250 5 161 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT484 | 3 Phase fault on S1211 5 161 (646211) 161 kV Bus a. Apply fault at the S1211 5 161 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load #O0 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT485 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT486 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT487 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT488 | 3 Phase fault on S1258 5 161.00 (646258) 161 kV Bus a. Apply fault at the S1258 5 161.00 (646258) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT489 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT490 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT491 | 3 Phase fault on S1398 5 161.00 (646398) 161 kV Bus a. Apply fault at the S1398 5 161.00 (646398) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.2. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT492 | 3 Phase fault on KELLY 5 161.00 (532913) 161 kV Bus a. Apply fault at the KELLY 5 161.00 (532913) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 5 (532913) 161.0 kV to TECHILL5 (532920) 161.0 kV Transmission Circuit #1 b.2. KELLY 5 (532913) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 b.3. KELLY 5 (532913) 161.0 kV to KELLY 3 (533217) 115.0 kV to KELLY 1 (532942) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT493 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT494 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT495 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT496 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT497 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT498 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT499 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT500 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT501 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT502 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT503 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT504 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT505 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT506 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT507 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT508 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT509 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT510 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT511 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT512 | 3 Phase fault on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT513 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT514 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT515 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT516 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT517 | 3 Phase fault on S1263 5 161.00 (646263) 161 kV Bus a. Apply fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.2. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT518 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT519 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT520 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT521 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT522 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT523 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT524 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT525 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT526 | 3 Phase fault on SIKETAP5 161.00 (505427) 161 kV Bus a. Apply fault at the SIKETAP5 161.00 (505427) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to SIKETAP5 (505427) 161.0 kV Transmission Circuit #1 b.2. SIKETAP5 (505427) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT527 | 3 Phase fault on IODINE 4 138.00 (520957) 138 kV Bus a. Apply fault at the IODINE 4 138.00 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT528 | 3 Phase fault on GLASMTN4 138.00 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 138.00 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT529 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT530 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT531 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT532 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT533 | 3 Phase fault on SEILING4 138.00 (520553) 138 kV Bus a. Apply fault at the SEILING4 138.00 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT534 | 3 Phase fault on WHEAGLE4 138.00 (514761) 138 kV Bus a. Apply fault at the WHEAGLE4 138.00 (514761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. NEWKIRK4 (514759) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.3. NEWKIRK4 (514759) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.4. NEWKIRK4 (514759) 138.0 kV to OMNUKRK4 (529290) 138.0 kV Transmission Circuit #1 b.5. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.6. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.7. NWKRKAT4 (514764) 138.0 kV to NEWKIR-WFEC4 (521012) 138.0 kV Transmission Circuit #1 b.8. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.9. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.10. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.11. PECKHMT4 (515381) 138.0 kV to NWBRAMN4 (520450) 138.0 kV Transmission Circuit #1 b.12. WHEAGLE4 (514761) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT535 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT536 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT537 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT538 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT539 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT540 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT541 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT542 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT543 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT544 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT545 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT546 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT547 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT548 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT549 | 3 Phase fault on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT550 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT551 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT552 | 3 Phase fault on ELMCREK6 230.00 (539639) 230 kV Bus a. Apply fault at the ELMCREK6 230.00 (539639) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT553 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT554 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT555 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT556 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT557 | 3 Phase fault on JEWELL 3 115.00 (539669) 115 kV Bus a. Apply fault at the JEWELL 3 115.00 (539669) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.2. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.4. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT558 | 3 Phase fault on CLIFTON3 115.00 (539656) 115 kV Bus a. Apply fault at the CLIFTON3 115.00 (539656) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLIFTON3 (539656) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT559 | 3 Phase fault on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT560 | 3 Phase fault on CONCRD6 230.00 (539658) 230 kV Bus a. Apply fault at the CONCRD6 230.00 (539658) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT561 | 3 Phase fault on BARBER 4 138.00 (539674) 138 kV Bus a. Apply fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT562 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT563 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. Present in the base case as well. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT563 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25S | Transfer | GROUP3_P1_LOCAL_FAULT989 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Oscillatory response due to non-convergence following the event. Present in the base case also. No CQ units meet the PTDF criteria. | Contingent on the queued Multi - Sheldon - Monolith 115 kV upgrade. Stable response observed after the upgrade is in-service.
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT564 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT565 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT566 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT567 | 3 Phase fault on 5EDMONS 161.00 (300034) 161 kV Bus a. Apply fault at the 5EDMONS 161.00 (300034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT568 | 3 Phase fault on 8NEWMAD 500.00 (300035) 500 kV Bus a. Apply fault at the 8NEWMAD 500.00 (300035) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8NEWMAD (300035) 500.0 kV to 8NEWMADXF34 (301528) 500.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT569 | 3 Phase fault on 7MCCRED 345.00 (300044) 345 kV Bus a. Apply fault at the 7MCCRED 345.00 (300044) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT570 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT571 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT572 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7NEWMADXF34 (301529) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT573 | 3 Phase fault on 7NEWMAD 345.00 (300046) 345 kV Bus a. Apply fault at the 7NEWMAD 345.00 (300046) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMAD (300046) 345.0 kV to 7NEWMADXF12 (301530) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT574 | 3 Phase fault on 7STFRAN 345.00 (300048) 345 kV Bus a. Apply fault at the 7STFRAN 345.00 (300048) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7STFRAN (300048) 345.0 kV to 7WNWMADRID2 (301418) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT575 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT576 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT577 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT578 | 3 Phase fault on 5GENTRY 161.00 (300073) 161 kV Bus a. Apply fault at the 5GENTRY 161.00 (300073) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GENTRY (300073) 161.0 kV to 5FAIRPTB2 (300076) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT579 | 3 Phase fault on 5ESSEX 161.00 (300075) 161 kV Bus a. Apply fault at the 5ESSEX 161.00 (300075) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5ESSEX (300075) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT580 | 3 Phase fault on 5FAIRPTB2 161.00 (300076) 161 kV Bus a. Apply fault at the 5FAIRPTB2 161.00 (300076) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT581 | 3 Phase fault on 5GEORGE 161.00 (300082) 161 kV Bus a. Apply fault at the 5GEORGE 161.00 (300082) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GEORGE (300082) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT582 | 3 Phase fault on 5MARYVB2 161.00 (300097) 161 kV Bus a. Apply fault at the 5MARYVB2 161.00 (300097) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARYVB2 (300097) 161.0 kV to MARYVLE5 (541251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT583 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M0 (301396) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT584 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M1 (301397) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT585 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M2 (301398) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT586 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5M7M3 (301399) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT587 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NEWMADCP (301405) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT588 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NEWMADXF12 (301531) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT589 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NMDSU100HS (301538) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT590 | 3 Phase fault on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMAD (300103) 161.0 kV to 5NMDSU200HS (301539) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT591 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT592 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOL (301040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT593 | 3 Phase fault on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT594 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT595 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT596 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT597 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT598 | 3 Phase fault on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STJUDEW (300170) 69.0 kV to 2NMCOAL (300171) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT599 | 3 Phase fault on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STJUDEW (300170) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT600 | 3 Phase fault on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2STJUDEW (300170) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT601 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2MAGNOL (300328) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT602 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2ROSEHL (300334) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT603 | 3 Phase fault on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT604 | 3 Phase fault on 2CHAPHL 69.000 (300324) 69 kV Bus a. Apply fault at the 2CHAPHL 69.000 (300324) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CHAPHL (300324) 69.0 kV to 2RT Z (300325) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT605 | 3 Phase fault on 2RT Z 69.000 (300325) 69 kV Bus a. Apply fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RT Z (300325) 69.0 kV to 2COLMBUS (300326) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT606 | 3 Phase fault on 2RT Z 69.000 (300325) 69 kV Bus a. Apply fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2RT Z (300325) 69.0 kV to 2ELM (300327) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT607 | 3 Phase fault on 2ELM 69.000 (300327) 69 kV Bus a. Apply fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT608 | 3 Phase fault on 2ROSEHL 69.000 (300334) 69 kV Bus a. Apply fault at the 2ROSEHL 69.000 (300334) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROSEHL (300334) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT609 | 3 Phase fault on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT610 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT611 | 3 Phase fault on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT612 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT613 | 3 Phase fault on 5GRAVOIB1 161.00 (300555) 161 kV Bus a. Apply fault at the 5GRAVOIB1 161.00 (300555) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5GRAVOIB1 (300555) 161.0 kV to 5GRAVOIB2 (300574) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT614 | 3 Phase fault on 2JASPER 69.000 (300649) 69 kV Bus a. Apply fault at the 2JASPER 69.000 (300649) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2JASPER (300649) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT615 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT616 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT617 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT618 | 3 Phase fault on 2CLINTN 69.000 (300692) 69 kV Bus a. Apply fault at the 2CLINTN 69.000 (300692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT619 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT620 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT621 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT622 | 3 Phase fault on 2DMNDTP 69.000 (300745) 69 kV Bus a. Apply fault at the 2DMNDTP 69.000 (300745) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DMNDTP (300745) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT623 | 3 Phase fault on 2REEDS 69.000 (300751) 69 kV Bus a. Apply fault at the 2REEDS 69.000 (300751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2REEDS (300751) 69.0 kV to CARTHG 2 (505490) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT624 | 3 Phase fault on 2ELKTON 69.000 (300773) 69 kV Bus a. Apply fault at the 2ELKTON 69.000 (300773) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ELKTON (300773) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT625 | 3 Phase fault on 2KNOBBY 69.000 (300780) 69 kV Bus a. Apply fault at the 2KNOBBY 69.000 (300780) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KNOBBY (300780) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT626 | 3 Phase fault on 2WARSAW 69.000 (300790) 69 kV Bus a. Apply fault at the 2WARSAW 69.000 (300790) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2WARSAW (300790) 69.0 kV to 2TURKEYCRK (301401) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT627 | 3 Phase fault on 5LAMAR 161.00 (300794) 161 kV Bus a. Apply fault at the 5LAMAR 161.00 (300794) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LAMAR (300794) 161.0 kV to 5JASPER (300950) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT628 | 3 Phase fault on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT629 | 3 Phase fault on 2ICONTP 69.000 (300809) 69 kV Bus a. Apply fault at the 2ICONTP 69.000 (300809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ICONTP (300809) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT630 | 3 Phase fault on 2OSCEOL 69.000 (300811) 69 kV Bus a. Apply fault at the 2OSCEOL 69.000 (300811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT631 | 3 Phase fault on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT632 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT633 | 3 Phase fault on 2AID 69.000 (301190) 69 kV Bus a. Apply fault at the 2AID 69.000 (301190) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AID (301190) 69.0 kV to 2AIDJCT (301191) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT634 | 3 Phase fault on 2AIDJCT 69.000 (301191) 69 kV Bus a. Apply fault at the 2AIDJCT 69.000 (301191) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AIDJCT (301191) 69.0 kV to 2PUXICO (301221) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT635 | 3 Phase fault on 2AIDJCT 69.000 (301191) 69 kV Bus a. Apply fault at the 2AIDJCT 69.000 (301191) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AIDJCT (301191) 69.0 kV to 2BLOOMF (301237) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT636 | 3 Phase fault on 2ARAB 69.000 (301192) 69 kV Bus a. Apply fault at the 2ARAB 69.000 (301192) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ARAB (301192) 69.0 kV to 2ADVANC (301235) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT637 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2FISK (301205) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT638 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2PUXICO (301221) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT639 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2ROMBAR (301223) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT640 | 3 Phase fault on 2ASHRVL 69.000 (301194) 69 kV Bus a. Apply fault at the 2ASHRVL 69.000 (301194) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to 2WAPELO (301226) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT641 | 3 Phase fault on 2FISK 69.000 (301205) 69 kV Bus a. Apply fault at the 2FISK 69.000 (301205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FISK (301205) 69.0 kV to 2DUDLEY (301228) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT642 | 3 Phase fault on 2MALDEN 69.000 (301214) 69 kV Bus a. Apply fault at the 2MALDEN 69.000 (301214) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MALDEN (301214) 69.0 kV to 2PARMA (301250) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT643 | 3 Phase fault on 2ROMBAR 69.000 (301223) 69 kV Bus a. Apply fault at the 2ROMBAR 69.000 (301223) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ROMBAR (301223) 69.0 kV to 2PBNORTH (301412) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT644 | 3 Phase fault on 2ADVANC 69.000 (301235) 69 kV Bus a. Apply fault at the 2ADVANC 69.000 (301235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ADVANC (301235) 69.0 kV to 2ARDEOLA (301257) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT645 | 3 Phase fault on 2ADVANC 69.000 (301235) 69 kV Bus a. Apply fault at the 2ADVANC 69.000 (301235) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ADVANC (301235) 69.0 kV to 2WHTWTR (301279) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT646 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2DOGWOD (301239) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT647 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2LILBRN (301246) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT648 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2WOLFIS (301252) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT649 | 3 Phase fault on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ANNSTN (301236) 69.0 kV to 2WYATT (301253) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT650 | 3 Phase fault on 2BLOOMF 69.000 (301237) 69 kV Bus a. Apply fault at the 2BLOOMF 69.000 (301237) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2BLOOMF (301237) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT651 | 3 Phase fault on 2DOGWOD 69.000 (301239) 69 kV Bus a. Apply fault at the 2DOGWOD 69.000 (301239) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DOGWOD (301239) 69.0 kV to 2MATHWS (301247) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT652 | 3 Phase fault on 2DOGWOD 69.000 (301239) 69 kV Bus a. Apply fault at the 2DOGWOD 69.000 (301239) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2DOGWOD (301239) 69.0 kV to 2MINER (301254) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT653 | 3 Phase fault on 2FRISCO 69.000 (301240) 69 kV Bus a. Apply fault at the 2FRISCO 69.000 (301240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRISCO (301240) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT654 | 3 Phase fault on 2FRISCO 69.000 (301240) 69 kV Bus a. Apply fault at the 2FRISCO 69.000 (301240) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FRISCO (301240) 69.0 kV to 2PARMA (301250) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT655 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to 2IDALMA (301244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT656 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT657 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV to 2ARDEOLA (301257) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT658 | 3 Phase fault on 2IDALMA 69.000 (301244) 69 kV Bus a. Apply fault at the 2IDALMA 69.000 (301244) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALMA (301244) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT659 | 3 Phase fault on 2KELLY 69.000 (301245) 69 kV Bus a. Apply fault at the 2KELLY 69.000 (301245) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2KELLY (301245) 69.0 kV to 2VANDSR (301251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT660 | 3 Phase fault on 2LILBRN 69.000 (301246) 69 kV Bus a. Apply fault at the 2LILBRN 69.000 (301246) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2LILBRN (301246) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT661 | 3 Phase fault on 2MATHWS 69.000 (301247) 69 kV Bus a. Apply fault at the 2MATHWS 69.000 (301247) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MATHWS (301247) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT662 | 3 Phase fault on 2MOREHS 69.000 (301248) 69 kV Bus a. Apply fault at the 2MOREHS 69.000 (301248) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOREHS (301248) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT663 | 3 Phase fault on 2MOREJT 69.000 (301249) 69 kV Bus a. Apply fault at the 2MOREJT 69.000 (301249) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MOREJT (301249) 69.0 kV to 2VANDSR (301251) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT664 | 3 Phase fault on 2PARMA 69.000 (301250) 69 kV Bus a. Apply fault at the 2PARMA 69.000 (301250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PARMA (301250) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT665 | 3 Phase fault on 2VANDSR 69.000 (301251) 69 kV Bus a. Apply fault at the 2VANDSR 69.000 (301251) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2VANDSR (301251) 69.0 kV to 2MORLEY (301255) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT666 | 3 Phase fault on 2AVONKN 69.000 (301285) 69 kV Bus a. Apply fault at the 2AVONKN 69.000 (301285) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AVONKN (301285) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT667 | 3 Phase fault on 2AVONKN 69.000 (301285) 69 kV Bus a. Apply fault at the 2AVONKN 69.000 (301285) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2AVONKN (301285) 69.0 kV to 2GIDJCT (301293) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT668 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT669 | 3 Phase fault on 5LOSTVALY 161.00 (301402) 161 kV Bus a. Apply fault at the 5LOSTVALY 161.00 (301402) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT670 | 3 Phase fault on 7WNWMADRID1A345.00 (301407) 345 kV Bus a. Apply fault at the 7WNWMADRID1A345.00 (301407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1A (301407) 345.0 kV to 7WNWMADRID1B (301416) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT671 | 3 Phase fault on 7WNWMADRID1B345.00 (301416) 345 kV Bus a. Apply fault at the 7WNWMADRID1B345.00 (301416) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 7WNWMADRID1C (301417) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT672 | 3 Phase fault on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOKC (301522) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT673 | 3 Phase fault on 5SHARSNV 161.00 (301515) 161 kV Bus a. Apply fault at the 5SHARSNV 161.00 (301515) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SHARSNV (301515) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT674 | 3 Phase fault on 5PLATCTY 161.00 (301552) 161 kV Bus a. Apply fault at the 5PLATCTY 161.00 (301552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PLATCTY (301552) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT675 | 3 Phase fault on 5CHARLSTN 161.00 (344333) 161 kV Bus a. Apply fault at the 5CHARLSTN 161.00 (344333) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHARLSTN (344333) 161.0 kV to 5MINER 1 (345203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT676 | 3 Phase fault on 5KELSO 1 161.00 (344847) 161 kV Bus a. Apply fault at the 5KELSO 1 161.00 (344847) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KELSO 1 (344847) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT677 | 3 Phase fault on 5KELSO 1 161.00 (344847) 161 kV Bus a. Apply fault at the 5KELSO 1 161.00 (344847) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KELSO 1 (344847) 161.0 kV to 5MINER 1 (345203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT678 | 3 Phase fault on 5KELSO 1 161.00 (344847) 161 kV Bus a. Apply fault at the 5KELSO 1 161.00 (344847) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5KELSO 1 (344847) 161.0 kV to 5VIAD_TP (345891) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT679 | 3 Phase fault on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 1 (344848) 345.0 kV to 7KELSO 2 (344849) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT680 | 3 Phase fault on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 1 (344848) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT681 | 3 Phase fault on 7MCCREDIE 345.00 (345088) 345 kV Bus a. Apply fault at the 7MCCREDIE 345.00 (345088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT682 | 3 Phase fault on 5MINER 1 161.00 (345203) 161 kV Bus a. Apply fault at the 5MINER 1 161.00 (345203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MINER 1 (345203) 161.0 kV to 5MINER 2 (345204) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT683 | 3 Phase fault on 5MINER 1 161.00 (345203) 161 kV Bus a. Apply fault at the 5MINER 1 161.00 (345203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MINER 1 (345203) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT684 | 3 Phase fault on 5RCHLND 1 161.00 (345588) 161 kV Bus a. Apply fault at the 5RCHLND 1 161.00 (345588) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RCHLND 1 (345588) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT685 | 3 Phase fault on 5STODDARD 1 161.00 (345790) 161 kV Bus a. Apply fault at the 5STODDARD 1 161.00 (345790) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STODDARD 1 (345790) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT686 | 3 Phase fault on 5VIAD_TP 161.00 (345891) 161 kV Bus a. Apply fault at the 5VIAD_TP 161.00 (345891) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5VIAD_TP (345891) 161.0 kV to 5VIADUCT 3 (345892) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT687 | 3 Phase fault on 7W_FRFT_E 345.00 (346992) 345 kV Bus a. Apply fault at the 7W_FRFT_E 345.00 (346992) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7W_FRFT_E (346992) 345.0 kV to 7SHAWNEE FP (360002) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT688 | 3 Phase fault on 7JOPPA TS 345.00 (347325) 345 kV Bus a. Apply fault at the 7JOPPA TS 345.00 (347325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JOPPA TS (347325) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT689 | 3 Phase fault on 5JOPPA S TP1161.00 (347334) 161 kV Bus a. Apply fault at the 5JOPPA S TP1161.00 (347334) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA S TP1 (347334) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at Silk (505432) and New Madrid (300006, 300007) generating sites following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT690 | 3 Phase fault on 5JOPPA T3 161.00 (347335) 161 kV Bus a. Apply fault at the 5JOPPA T3 161.00 (347335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA T3 (347335) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at Silk (505432) and New Madrid (300006, 300007) generating sites following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT691 | 3 Phase fault on 5MARION S 161.00 (347523) 161 kV Bus a. Apply fault at the 5MARION S 161.00 (347523) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MARION S (347523) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT692 | 3 Phase fault on 7COMM 345.00 (348287) 345 kV Bus a. Apply fault at the 7COMM 345.00 (348287) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7COMM (348287) 345.0 kV to 7JORD (348289) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT693 | 3 Phase fault on 7JORD 345.00 (348289) 345 kV Bus a. Apply fault at the 7JORD 345.00 (348289) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JORD (348289) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT694 | 3 Phase fault on 7MASS 345.00 (348294) 345 kV Bus a. Apply fault at the 7MASS 345.00 (348294) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MASS (348294) 345.0 kV to 7SHAWNEE FP (360002) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT695 | 3 Phase fault on 5NAUVOO TN 161.00 (360479) 161 kV Bus a. Apply fault at the 5NAUVOO TN 161.00 (360479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NAUVOO TN (360479) 161.0 kV to 5RIDGELY TN (360521) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT696 | 3 Phase fault on 5RIDGELY TN 161.00 (360521) 161 kV Bus a. Apply fault at the 5RIDGELY TN 161.00 (360521) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RIDGELY TN (360521) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT697 | 3 Phase fault on 5TIPTONVL TN161.00 (361261) 161 kV Bus a. Apply fault at the 5TIPTONVL TN161.00 (361261) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TIPTONVL TN (361261) 161.0 kV to 5POLK TP (361596) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT698 | 3 Phase fault on 5TROY TN 161.00 (361422) 161 kV Bus a. Apply fault at the 5TROY TN 161.00 (361422) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TROY TN (361422) 161.0 kV to 5POLK TP (361596) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT699 | 3 Phase fault on 5POLK TP 161.00 (361596) 161 kV Bus a. Apply fault at the 5POLK TP 161.00 (361596) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5POLK TP (361596) 161.0 kV to 5POLK (361597) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT700 | 3 Phase fault on N MADRD5 161.00 (505400) 161 kV Bus a. Apply fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD5 (505400) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT701 | 3 Phase fault on N MADRD2 69.000 (505402) 69 kV Bus a. Apply fault at the N MADRD2 69.000 (505402) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT702 | 3 Phase fault on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT703 | 3 Phase fault on PIGGOTT2 69.000 (505406) 69 kV Bus a. Apply fault at the PIGGOTT2 69.000 (505406) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIGGOTT2 (505406) 69.0 kV to KENNETT2 (505408) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT704 | 3 Phase fault on SIKETAP5 161.00 (505427) 161 kV Bus a. Apply fault at the SIKETAP5 161.00 (505427) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKETAP5 (505427) 161.0 kV to SIKE SW5 (505433) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT705 | 3 Phase fault on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKESTN5 (505428) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT706 | 3 Phase fault on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDALIA 5 (505434) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT707 | 3 Phase fault on POP BLF5 161.00 (505438) 161 kV Bus a. Apply fault at the POP BLF5 161.00 (505438) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POP BLF5 (505438) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT708 | 3 Phase fault on WASHBURN5 161.00 (505485) 161 kV Bus a. Apply fault at the WASHBURN5 161.00 (505485) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBURN5 (505485) 161.0 kV to NEO SPA5 (505486) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT709 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT710 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to NEO184 5 (547471) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT711 | 3 Phase fault on NEO SPA5 161.00 (505486) 161 kV Bus a. Apply fault at the NEO SPA5 161.00 (505486) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEO SPA5 (505486) 161.0 kV to TIP292 5 (547472) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT712 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT713 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT714 | 3 Phase fault on SPRGFLD5 161.00 (505492) 161 kV Bus a. Apply fault at the SPRGFLD5 161.00 (505492) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGFLD5 (505492) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT715 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT716 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to BOBCAT 7 (516106) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT717 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT719 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT720 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT721 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT722 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulations crashes due to non-convergence. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT723 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT724 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT725 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT726 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT727 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT728 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT729 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT730 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT731 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT732 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT733 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT734 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT735 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT736 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT737 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT738 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT739 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT740 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT741 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT742 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT743 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT744 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT745 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT746 | 3 Phase fault on WACO S 4 138.00 (533071) 138 kV Bus a. Apply fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT747 | 3 Phase fault on TECHILW3 115.00 (533181) 115 kV Bus a. Apply fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT748 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to MW SOLV2 (533477) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT749 | 3 Phase fault on MIDLADN3 115.00 (533252) 115 kV Bus a. Apply fault at the MIDLADN3 115.00 (533252) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT750 | 3 Phase fault on FREESTATE3 115.00 (533257) 115 kV Bus a. Apply fault at the FREESTATE3 115.00 (533257) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FREESTATE3 (533257) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT751 | 3 Phase fault on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT752 | 3 Phase fault on KSU W 3 115.00 (533333) 115 kV Bus a. Apply fault at the KSU W 3 115.00 (533333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KSU W 3 (533333) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT753 | 3 Phase fault on MCDOWEL3 115.00 (533335) 115 kV Bus a. Apply fault at the MCDOWEL3 115.00 (533335) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT754 | 3 Phase fault on AEC 3 115.00 (533361) 115 kV Bus a. Apply fault at the AEC 3 115.00 (533361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT755 | 3 Phase fault on BERG 3 115.00 (533367) 115 kV Bus a. Apply fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT756 | 3 Phase fault on BERG 3 115.00 (533367) 115 kV Bus a. Apply fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT757 | 3 Phase fault on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT758 | 3 Phase fault on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT759 | 3 Phase fault on ARKVAL 3 115.00 (533411) 115 kV Bus a. Apply fault at the ARKVAL 3 115.00 (533411) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT760 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT761 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT762 | 3 Phase fault on AKRON 2 69.000 (533541) 69 kV Bus a. Apply fault at the AKRON 2 69.000 (533541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AKRON 2 (533541) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT763 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT764 | 3 Phase fault on CRESWLN2 69.000 (533543) 69 kV Bus a. Apply fault at the CRESWLN2 69.000 (533543) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT765 | 3 Phase fault on FLORAL 2 69.000 (533545) 69 kV Bus a. Apply fault at the FLORAL 2 69.000 (533545) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORAL 2 (533545) 69.0 kV to FLORALJ2 (533546) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT766 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to SC1KING2 (533551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT767 | 3 Phase fault on FLORALJ2 69.000 (533546) 69 kV Bus a. Apply fault at the FLORALJ2 69.000 (533546) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLORALJ2 (533546) 69.0 kV to TIMBER 2 (533557) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT768 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT769 | 3 Phase fault on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT770 | 3 Phase fault on BUTLERN2 69.000 (533583) 69 kV Bus a. Apply fault at the BUTLERN2 69.000 (533583) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERN2 (533583) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT771 | 3 Phase fault on MIDIANW2 69.000 (533597) 69 kV Bus a. Apply fault at the MIDIANW2 69.000 (533597) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIANW2 (533597) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT772 | 3 Phase fault on TIOGA 2 69.000 (533646) 69 kV Bus a. Apply fault at the TIOGA 2 69.000 (533646) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT773 | 3 Phase fault on CGENSUB2 69.000 (533662) 69 kV Bus a. Apply fault at the CGENSUB2 69.000 (533662) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CGENSUB2 (533662) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT774 | 3 Phase fault on ALTAMNT2 69.000 (533671) 69 kV Bus a. Apply fault at the ALTAMNT2 69.000 (533671) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT775 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODESH2 (533699) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT776 | 3 Phase fault on ARGO 2 69.000 (533675) 69 kV Bus a. Apply fault at the ARGO 2 69.000 (533675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARGO 2 (533675) 69.0 kV to NEODJCT2 (533700) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT777 | 3 Phase fault on CHERRYV2 69.000 (533679) 69 kV Bus a. Apply fault at the CHERRYV2 69.000 (533679) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHERRYV2 (533679) 69.0 kV to CHRYJCT2 (533680) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT778 | 3 Phase fault on YELLOWJ2 69.000 (533692) 69 kV Bus a. Apply fault at the YELLOWJ2 69.000 (533692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YELLOWJ2 (533692) 69.0 kV to NEW ALB2 (533701) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT779 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT780 | 3 Phase fault on NEODJCT2 69.000 (533700) 69 kV Bus a. Apply fault at the NEODJCT2 69.000 (533700) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEODJCT2 (533700) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT781 | 3 Phase fault on NEW ALB2 69.000 (533701) 69 kV Bus a. Apply fault at the NEW ALB2 69.000 (533701) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEW ALB2 (533701) 69.0 kV to STUDBKR2 (533705) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT782 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT783 | 3 Phase fault on LITCH N2 69.000 (533765) 69 kV Bus a. Apply fault at the LITCH N2 69.000 (533765) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT784 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT785 | 3 Phase fault on GILL E 2 69.000 (533795) 69 kV Bus a. Apply fault at the GILL E 2 69.000 (533795) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILL W 2 (533796) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT786 | 3 Phase fault on RIPLEYE2 69.000 (533859) 69 kV Bus a. Apply fault at the RIPLEYE2 69.000 (533859) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIPLEYE2 (533859) 69.0 kV to RIPLEYM2 (533860) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT787 | 3 Phase fault on EAST SUB 2 69.000 (533990) 69 kV Bus a. Apply fault at the EAST SUB 2 69.000 (533990) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT788 | 3 Phase fault on WEST SUB 2 69.000 (533991) 69 kV Bus a. Apply fault at the WEST SUB 2 69.000 (533991) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT789 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT790 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT791 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT792 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT793 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT794 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT795 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT796 | 3 Phase fault on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDLIAW_CAP5 (541146) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT797 | 3 Phase fault on ST JOE_CAP5 161.00 (541147) 161 kV Bus a. Apply fault at the ST JOE_CAP5 161.00 (541147) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE_CAP5 (541147) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT798 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT799 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT800 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT801 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT802 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT803 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT804 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT805 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT806 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT807 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT808 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT809 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT810 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT811 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT812 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT813 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT814 | 3 Phase fault on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMTHVL 5 (541204) 161.0 kV to POPE (541349) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT815 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT816 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT817 | 3 Phase fault on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT818 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT819 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDALIA5 (541209) 161.0 kV to WAFBE_SW5 (541337) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT820 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT821 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT822 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT823 | 3 Phase fault on KCI 5 161.00 (541212) 161 kV Bus a. Apply fault at the KCI 5 161.00 (541212) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCI 5 (541212) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT824 | 3 Phase fault on FRLVW 5 161.00 (541213) 161 kV Bus a. Apply fault at the FRLVW 5 161.00 (541213) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRLVW 5 (541213) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT825 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT826 | 3 Phase fault on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT827 | 3 Phase fault on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT828 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT829 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT830 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT831 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT832 | 3 Phase fault on DUNCAN 5 161.00 (541235) 161 kV Bus a. Apply fault at the DUNCAN 5 161.00 (541235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNCAN 5 (541235) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT833 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT834 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT835 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to BRADDYVILLE5 (635038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT836 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT837 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT838 | 3 Phase fault on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ST JOE 5 (541253) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT839 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT840 | 3 Phase fault on EAST 5 161.00 (541254) 161 kV Bus a. Apply fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT841 | 3 Phase fault on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT842 | 3 Phase fault on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to ALABAMA5 (541354) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT843 | 3 Phase fault on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKE RD5 (541255) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT844 | 3 Phase fault on IND PRK5 161.00 (541256) 161 kV Bus a. Apply fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT845 | 3 Phase fault on COOK 5 161.00 (541257) 161 kV Bus a. Apply fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT846 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT847 | 3 Phase fault on TURNER_RD5 161.00 (541259) 161 kV Bus a. Apply fault at the TURNER_RD5 161.00 (541259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURNER_RD5 (541259) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT848 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to WARSAWTP (541281) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT849 | 3 Phase fault on WARSAW 2 69.000 (541277) 69 kV Bus a. Apply fault at the WARSAW 2 69.000 (541277) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARSAW 2 (541277) 69.0 kV to NWARSAW2 (541315) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT850 | 3 Phase fault on RGREEN 2 69.000 (541279) 69 kV Bus a. Apply fault at the RGREEN 2 69.000 (541279) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RGREEN 2 (541279) 69.0 kV to PHILL 2 (541280) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT851 | 3 Phase fault on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT852 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT853 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT854 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 5 (541341) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT855 | 3 Phase fault on PECULR 5 161.00 (541342) 161 kV Bus a. Apply fault at the PECULR 5 161.00 (541342) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECULR 5 (541342) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT856 | 3 Phase fault on IATAN5 161.00 (541350) 161 kV Bus a. Apply fault at the IATAN5 161.00 (541350) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT857 | 3 Phase fault on AMOIL 2 69.000 (541358) 69 kV Bus a. Apply fault at the AMOIL 2 69.000 (541358) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOIL 2 (541358) 69.0 kV to MIDWY1 2 (541368) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT858 | 3 Phase fault on MIDWY1 2 69.000 (541368) 69 kV Bus a. Apply fault at the MIDWY1 2 69.000 (541368) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWY1 2 (541368) 69.0 kV to MDWYTP 2 (541389) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT859 | 3 Phase fault on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAY_5 (541369) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT860 | 3 Phase fault on SAVANAH2 69.000 (541391) 69 kV Bus a. Apply fault at the SAVANAH2 69.000 (541391) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAVANAH2 (541391) 69.0 kV to EDMOND2 (541392) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT861 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT862 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT863 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT864 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT865 | 3 Phase fault on CRAIG_CAP 5 161.00 (542945) 161 kV Bus a. Apply fault at the CRAIG_CAP 5 161.00 (542945) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG_CAP 5 (542945) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT866 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT867 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM_CAP5 (542947) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT868 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT869 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN_CAP5 (542950) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT870 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT871 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT872 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT873 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT874 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to CEDARNL5 (543054) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT875 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT876 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT877 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT878 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT879 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT880 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT881 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT882 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT883 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT884 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT885 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT886 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT887 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT888 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #@2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT889 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT890 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT891 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT892 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT893 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT894 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT895 | 3 Phase fault on CRAIG 5 161.00 (542978) 161 kV Bus a. Apply fault at the CRAIG 5 161.00 (542978) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIG 5 (542978) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT896 | 3 Phase fault on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT897 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT898 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT899 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT900 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT901 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT902 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT903 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #@1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT904 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT905 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT906 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT907 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT908 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT909 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT910 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT911 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT912 | 3 Phase fault on LVISTA 5 161.00 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 161.00 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT913 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT914 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT915 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT916 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT917 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT918 | 3 Phase fault on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT919 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT920 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT921 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT922 | 3 Phase fault on CLAYCM15 161.00 (543022) 161 kV Bus a. Apply fault at the CLAYCM15 161.00 (543022) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLAYCM15 (543022) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT923 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT924 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT925 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to CEDRCRK5 (543049) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT926 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT927 | 3 Phase fault on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM5 (543032) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT928 | 3 Phase fault on BRKRIDG5 161.00 (543033) 161 kV Bus a. Apply fault at the BRKRIDG5 161.00 (543033) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKRIDG5 (543033) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT929 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT930 | 3 Phase fault on KNLWRTH5 161.00 (543034) 161 kV Bus a. Apply fault at the KNLWRTH5 161.00 (543034) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNLWRTH5 (543034) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT931 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT932 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT933 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT934 | 3 Phase fault on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT935 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT936 | 3 Phase fault on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT937 | 3 Phase fault on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LENEXA 5 (543038) 161.0 kV to REEDER 5 (543052) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT938 | 3 Phase fault on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT939 | 3 Phase fault on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT940 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT941 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT942 | 3 Phase fault on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEOTTWA5 (543055) 161.0 kV to NEASTOTTW5 (543166) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT943 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT944 | 3 Phase fault on CNTRVIL5 161.00 (543065) 161 kV Bus a. Apply fault at the CNTRVIL5 161.00 (543065) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CNTRVIL5 (543065) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT945 | 3 Phase fault on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.OTTWA5 (543066) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT946 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT947 | 3 Phase fault on CENTENL5 161.00 (543067) 161 kV Bus a. Apply fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT948 | 3 Phase fault on COL282 2 69.000 (547411) 69 kV Bus a. Apply fault at the COL282 2 69.000 (547411) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL282 2 (547411) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT949 | 3 Phase fault on SEK225T2 69.000 (547412) 69 kV Bus a. Apply fault at the SEK225T2 69.000 (547412) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEK225T2 (547412) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT950 | 3 Phase fault on WEB105 2 69.000 (547431) 69 kV Bus a. Apply fault at the WEB105 2 69.000 (547431) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB105 2 (547431) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT951 | 3 Phase fault on SCM66T 2 69.000 (547455) 69 kV Bus a. Apply fault at the SCM66T 2 69.000 (547455) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCM66T 2 (547455) 69.0 kV to COL 94 2 (547530) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT952 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT953 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT954 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT955 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT956 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT957 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT958 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT959 | 3 Phase fault on LAR382 5 161.00 (547479) 161 kV Bus a. Apply fault at the LAR382 5 161.00 (547479) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAR382 5 (547479) 161.0 kV to MON383 5 (547480) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT960 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT961 | 3 Phase fault on JOP389 5 161.00 (547483) 161 kV Bus a. Apply fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT962 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT963 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP 64 2 (547526) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT964 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT965 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT966 | 3 Phase fault on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP 59 2 (547525) 69.0 kV to JOP430 2 (547608) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT967 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to CAR108 2 (547532) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT968 | 3 Phase fault on WEB436 2 69.000 (547527) 69 kV Bus a. Apply fault at the WEB436 2 69.000 (547527) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEB436 2 (547527) 69.0 kV to ORO110 2 (547534) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT969 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT970 | 3 Phase fault on COL 94 2 69.000 (547530) 69 kV Bus a. Apply fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT971 | 3 Phase fault on ATL109 2 69.000 (547533) 69 kV Bus a. Apply fault at the ATL109 2 69.000 (547533) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 2 (547533) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT972 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to OAK280 2 (547556) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT973 | 3 Phase fault on ORO110 2 69.000 (547534) 69 kV Bus a. Apply fault at the ORO110 2 69.000 (547534) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 2 (547534) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT974 | 3 Phase fault on JOP145 2 69.000 (547539) 69 kV Bus a. Apply fault at the JOP145 2 69.000 (547539) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 2 (547539) 69.0 kV to JOP341 2 (547574) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT975 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT976 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT977 | 3 Phase fault on BAX271 2 69.000 (547554) 69 kV Bus a. Apply fault at the BAX271 2 69.000 (547554) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAX271 2 (547554) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT978 | 3 Phase fault on GLF339 2 69.000 (547690) 69 kV Bus a. Apply fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT979 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT980 | 3 Phase fault on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT981 | 3 Phase fault on BPS SUB7 115.00 (640088) 115 kV Bus a. Apply fault at the BPS SUB7 115.00 (640088) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BPS SUB7 (640088) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT982 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT983 | 3 Phase fault on COOPER_ESST869.000 (640141) 69 kV Bus a. Apply fault at the COOPER_ESST869.000 (640141) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_ESST8 (640141) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT984 | 3 Phase fault on COOPER_602 869.000 (640143) 69 kV Bus a. Apply fault at the COOPER_602 869.000 (640143) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT985 | 3 Phase fault on CRETE__7 115.00 (640153) 115 kV Bus a. Apply fault at the CRETE__7 115.00 (640153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRETE__7 (640153) 115.0 kV to SHELDON7 (640278) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT986 | 3 Phase fault on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT987 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT988 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT989 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Oscillatory response due to non-convergence following the event. Present in the base case also. No CQ units meet the PTDF criteria. | Contingent on the queued Multi - Sheldon - Monolith 115 kV upgrade. Stable response observed after the upgrade is in-service.
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT990 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT991 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT992 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT993 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT994 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT995 | 3 Phase fault on GI94_POI 345.00 (709400) 345 kV Bus a. Apply fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT996 | 3 Phase fault on 7ESSEX 345.00 (300038) 345 kV Bus a. Apply fault at the 7ESSEX 345.00 (300038) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5ESSEX (300075) 161.0 kV to 7ESSEX (300038) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT997 | 3 Phase fault on 7STFRAN 345.00 (300048) 345 kV Bus a. Apply fault at the 7STFRAN 345.00 (300048) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5STFRNB3 (300116) 161.0 kV to 7STFRAN (300048) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT998 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT999 | 3 Phase fault on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1000 | 3 Phase fault on 5FAIRPTB2 161.00 (300076) 161 kV Bus a. Apply fault at the 5FAIRPTB2 161.00 (300076) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2FAIRPT (300249) 69.0 kV to 5FAIRPTB2 (300076) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1001 | 3 Phase fault on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2PITTSV (300331) 69.0 kV to 5PITTSV (300110) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1002 | 3 Phase fault on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1003 | 3 Phase fault on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1004 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1005 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1006 | 3 Phase fault on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2OSCEOL (300811) 69.0 kV to 5OSCEOL (301040) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1007 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1008 | 3 Phase fault on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1009 | 3 Phase fault on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1010 | 3 Phase fault on 5TURKEYCRK 161.00 (301370) 161 kV Bus a. Apply fault at the 5TURKEYCRK 161.00 (301370) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2TURKEYCRK (301401) 69.0 kV to 5TURKEYCRK (301370) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1011 | 3 Phase fault on 8WNEWMADRID 500.00 (301406) 500 kV Bus a. Apply fault at the 8WNEWMADRID 500.00 (301406) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7WNWMADRID1B (301416) 345.0 kV to 8WNEWMADRID (301406) 500.0 kV Two Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1012 | 3 Phase fault on 8NEWMADXF34 500.00 (301528) 500 kV Bus a. Apply fault at the 8NEWMADXF34 500.00 (301528) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMADXF34 (301529) 345.0 kV to 8NEWMADXF34 (301528) 500.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1013 | 3 Phase fault on 8NEWMADXF34 500.00 (301528) 500 kV Bus a. Apply fault at the 8NEWMADXF34 500.00 (301528) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7NEWMADXF34 (301529) 345.0 kV to 8NEWMADXF34 (301528) 500.0 kV Two Winding #4 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1014 | 3 Phase fault on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5NEWMADXF12 (301531) 161.0 kV to 7NEWMADXF12 (301530) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1015 | 3 Phase fault on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5NEWMADXF12 (301531) 161.0 kV to 7NEWMADXF12 (301530) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1016 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 5DELL% (338185) 161.0 kV to 1DELL1 (338183) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1017 | 3 Phase fault on 8DELL% 500.00 (338187) 500 kV Bus a. Apply fault at the 8DELL% 500.00 (338187) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8DELL% (338187) 500.0 kV to 5DELL% (338185) 161.0 kV to 1DELL2 (338184) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1018 | 3 Phase fault on 5JIM HILL% 161.00 (338202) 161 kV Bus a. Apply fault at the 5JIM HILL% 161.00 (338202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JIM HILL% (338202) 161.0 kV to 3JIM HILL! (338230) 115.0 kV to 1JIM HILL (338209) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1019 | 3 Phase fault on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7KELSO 1 (344848) 345.0 kV to 5KELSO 1 (344847) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1020 | 3 Phase fault on 7JOPPA TS 345.00 (347325) 345 kV Bus a. Apply fault at the 7JOPPA TS 345.00 (347325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JOPPA TS (351003) 161.0 kV to 7JOPPA TS (347325) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1021 | 3 Phase fault on 7JORD 345.00 (348289) 345 kV Bus a. Apply fault at the 7JORD 345.00 (348289) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JORD (348289) 345.0 kV to 4JORD (348292) 138.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1022 | 3 Phase fault on 7MASS 345.00 (348294) 345 kV Bus a. Apply fault at the 7MASS 345.00 (348294) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MASS (348294) 345.0 kV to 5MASS (348295) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1023 | 3 Phase fault on 8SHAWNEE FP 500.00 (360001) 500 kV Bus a. Apply fault at the 8SHAWNEE FP 500.00 (360001) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHAWNEE FP (360001) 500.0 kV to 7SHAWNEE FP (360002) 345.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1024 | 3 Phase fault on CENTR H5 161.00 (505416) 161 kV Bus a. Apply fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X1 1 (505417) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1025 | 3 Phase fault on CENTR H5 161.00 (505416) 161 kV Bus a. Apply fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X2 1 (505419) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1026 | 3 Phase fault on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKESTN5 (505428) 161.0 kV to SIKESTN2 (505430) 69.0 kV to SIK X1 1 (505429) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1027 | 3 Phase fault on SIKE SW5 161.00 (505433) 161 kV Bus a. Apply fault at the SIKE SW5 161.00 (505433) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIKE SW5 (505433) 161.0 kV to SIKE SW2 (505423) 69.0 kV to SIK X2 1 (505431) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1028 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1029 | 3 Phase fault on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTHG 2 (505490) 69.0 kV to CARTHAG5 (505488) 161.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1030 | 3 Phase fault on MOORLND4 138.00 (520999) 138 kV Bus a. Apply fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 (520999) 138.0 kV to MOORLND2 (520995) 69.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1031 | 3 Phase fault on HOYT 7 345.00 (532765) 345 kV Bus a. Apply fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1032 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1033 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1034 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1035 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1036 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1037 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1038 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1039 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1040 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1041 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1042 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1043 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1044 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1045 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1046 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1047 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1048 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1049 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1050 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1051 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1052 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1053 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1054 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1055 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1056 | 3 Phase fault on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1057 | 3 Phase fault on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1058 | 3 Phase fault on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1059 | 3 Phase fault on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1060 | 3 Phase fault on NMANHT6 230.00 (532865) 230 kV Bus a. Apply fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMANHT6 (532865) 230.0 kV to NMANHT3 (533347) 115.0 kV to NMANHX1 (532901) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1061 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1062 | 3 Phase fault on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1063 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1064 | 3 Phase fault on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1065 | 3 Phase fault on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1066 | 3 Phase fault on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to SPRINGH3 (533267) 115.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1067 | 3 Phase fault on TECHILL5 161.00 (532920) 161 kV Bus a. Apply fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1068 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1069 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1070 | 3 Phase fault on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1071 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1072 | 3 Phase fault on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1073 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1074 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1075 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1076 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1077 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1078 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1079 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1080 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1081 | 3 Phase fault on 17TH 4 138.00 (533064) 138 kV Bus a. Apply fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1082 | 3 Phase fault on COLINE 3 115.00 (533153) 115 kV Bus a. Apply fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1083 | 3 Phase fault on ARNOLD 3 115.00 (533211) 115 kV Bus a. Apply fault at the ARNOLD 3 115.00 (533211) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARNOLD 3 (533211) 115.0 kV to ARNOLD 2 (533471) 69.0 kV to ARNOLD 1 (533449) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1084 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to NCTYSVC2 (533505) 69.0 kV to CITIES 1 (533453) 3.9 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1085 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1086 | 3 Phase fault on HEC 3 115.00 (533419) 115 kV Bus a. Apply fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1087 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1088 | 3 Phase fault on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1089 | 3 Phase fault on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1090 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1091 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1092 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1093 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1094 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1095 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1096 | 3 Phase fault on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONTGOM2 (533698) 69.0 kV to MONTGOM4 (533004) 138.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1097 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 2 (533742) 69.0 kV to MOUND 4 (533013) 138.0 kV to MOUND1X1 (533095) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1098 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1099 | 3 Phase fault on LITCH 5 161.00 (532932) 161 kV Bus a. Apply fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1100 | 3 Phase fault on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1101 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1102 | 3 Phase fault on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1103 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1104 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1105 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1106 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1107 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1108 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDN 2 (541271) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1109 | 3 Phase fault on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1110 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY2 (541287) 69.0 kV to MARTCTY5 (541210) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1111 | 3 Phase fault on PHILL 5 161.00 (541225) 161 kV Bus a. Apply fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 2 (541280) 69.0 kV to PHILL 5 (541225) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1112 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1113 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1114 | 3 Phase fault on HSNVL 5 161.00 (541239) 161 kV Bus a. Apply fault at the HSNVL 5 161.00 (541239) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSNVL 2 (541295) 69.0 kV to HSNVL 5 (541239) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1115 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1116 | 3 Phase fault on CLINTON5 161.00 (541242) 161 kV Bus a. Apply fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1117 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1118 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 2 (541263) 69.0 kV to SIBLEYPL (541250) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1119 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to MRVL#1 (541378) 69.0 kV to MARYVIL11 (541519) 13.2 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1120 | 3 Phase fault on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARYVLE5 (541251) 161.0 kV to MRVL#2 (541359) 69.0 kV to MARYVIL21 (541520) 13.2 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1121 | 3 Phase fault on BELTONS5 161.00 (541340) 161 kV Bus a. Apply fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELTONS2 (541290) 69.0 kV to BELTONS5 (541340) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1122 | 3 Phase fault on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1123 | 3 Phase fault on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1124 | 3 Phase fault on EDMOND5 161.00 (541355) 161 kV Bus a. Apply fault at the EDMOND5 161.00 (541355) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDMOND5 (541355) 161.0 kV to EDMOND2 (541392) 69.0 kV to EDMOND-T (541522) 13.1 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1125 | 3 Phase fault on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAY_5 (541369) 161.0 kV to MIDWY1 2 (541368) 69.0 kV to MIDWY-T1 (541521) 13.2 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1126 | 3 Phase fault on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWAY_5 (541369) 161.0 kV to MIDWY2 2 (541390) 69.0 kV to MIDWY-T2 (541393) 13.2 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1127 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1128 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1129 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1130 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1131 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1132 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1133 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1134 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1135 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1136 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1137 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1138 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1139 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1140 | 3 Phase fault on IATAN 7 345.00 (542982) 345 kV Bus a. Apply fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1141 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1142 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1143 | 3 Phase fault on ATL109 5 161.00 (547466) 161 kV Bus a. Apply fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1144 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1145 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1146 | 3 Phase fault on JOP145 5 161.00 (547470) 161 kV Bus a. Apply fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1147 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1148 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1149 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1150 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1151 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1152 | 3 Phase fault on 2SEDALI 69.000 (300541) 69 kV Bus a. Apply fault at the 2SEDALI 69.000 (300541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2SEDALI (300541) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1153 | 3 Phase fault on 2IDALIA 69.000 (301243) 69 kV Bus a. Apply fault at the 2IDALIA 69.000 (301243) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2IDALIA (301243) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1154 | 3 Phase fault on 5NEWMADCP 161.00 (301405) 161 kV Bus a. Apply fault at the 5NEWMADCP 161.00 (301405) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5NEWMADCP (301405) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1155 | 3 Phase fault on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALDEN 2 (505404) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1156 | 3 Phase fault on PIGGOTT2 69.000 (505406) 69 kV Bus a. Apply fault at the PIGGOTT2 69.000 (505406) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIGGOTT2 (505406) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1157 | 3 Phase fault on KENNETT2 69.000 (505408) 69 kV Bus a. Apply fault at the KENNETT2 69.000 (505408) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENNETT2 (505408) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1158 | 3 Phase fault on PARAGLD2 69.000 (505414) 69 kV Bus a. Apply fault at the PARAGLD2 69.000 (505414) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARAGLD2 (505414) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_LOCAL_FAULT1159 | 3 Phase fault on FIRTH 7 115.00 (640171) 115 kV Bus a. Apply fault at the FIRTH 7 115.00 (640171) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FIRTH 7 (640171) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT1 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT2 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT3 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT4 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT5 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT6 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT7 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT8 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT9 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT10 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT11 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT12 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT13 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT14 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT15 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT16 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT17 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT18 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT19 | 3 Phase fault on REDWILO3 345.00 (640325) 345 kV Bus a. Apply fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT20 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT21 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT22 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT23 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT24 | 3 Phase fault on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7HUBEN (300042) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT25 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT26 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT27 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT28 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to LAMAR7 (599950) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT29 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT30 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT31 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT32 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT33 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT34 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT35 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT36 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT37 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT38 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT39 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT40 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT41 | 3 Phase fault on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT42 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT43 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT44 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT45 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT46 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT47 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT48 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT49 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT50 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P1_REGIONAL_FAULT51 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT1 | Single Phase Fault with Stuck Breaker on RUSSELL3 115.00 (539701) 115 kV Bus a. Apply Fault at the RUSSELL3 115.00 (539701) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLSWTP3 (539642) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.2. COVERT 3 (539644) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.3. COVERT 3 (539644) 115.0 kV to WALDO 3 (539698) 115.0 kV Transmission Circuit #1 b.4. IONIA 3 (539647) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.5. IONIA 3 (539647) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.6. BELOIT 3 (539650) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.7. BELOIT 3 (539650) 115.0 kV to GLENELD3 (539663) 115.0 kV Transmission Circuit #1 b.8. CONCORD3 (539657) 115.0 kV to JEWELL 3 (539669) 115.0 kV Transmission Circuit #1 b.9. GLENELD3 (539663) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.10. PHLBURG3 (539685) 115.0 kV to SMITH-C3 (539693) 115.0 kV Transmission Circuit #1 b.11. WALDO 3 (539698) 115.0 kV to RUSSELL3 (539701) 115.0 kV Transmission Circuit #1 b.12. BELOIT 3 (539650) 115.0 kV to BELOIT 1 (539750) 34.5 kV to BELOIT-T (539901) 7.2 kV Three Winding #1 b.13. GLENELD3 (539663) 115.0 kV to GLENELD1 (539709) 34.5 kV to GLNELD-T (539909) 13.8 kV Three Winding #1 b.14. JEWELL 3 (539669) 115.0 kV to JEWELL 1 (539714) 34.5 kV to JEWEEL-T (539914) 2.4 kV Three Winding #1 b.15. SMITH-C3 (539693) 115.0 kV to SMITH-C1 (539731) 34.5 kV to SMITHC-T (539934) 7.2 kV Three Winding #1 b.16. WALDO 3 (539698) 115.0 kV to WALDO 1 (539734) 34.5 kV to WALDO-T (539938) 7.2 kV Three Winding #1 b.17. RUSSELL3 (539701) 115.0 kV to RUSSELL1 (539703) 34.5 kV to RUSSEL-T (539943) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT2 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 b.3. LITCH 5 (532932) 161.0 kV to LITCH N2 (533765) 69.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 b.4. LITCH 5 (532932) 161.0 kV to LITCH S2 (533766) 69.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT3 | Single Phase Fault with Stuck Breaker on 29TH 4 138.00 (533024) 138 kV Bus a. Apply Fault at the 29TH 4 138.00 (533024) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT4 | Single Phase Fault with Stuck Breaker on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT5 | Single Phase Fault with Stuck Breaker on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply Fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT6 | Single Phase Fault with Stuck Breaker on MAIZE 4 138.00 (533054) 138 kV Bus a. Apply Fault at the MAIZE 4 138.00 (533054) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT7 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.2. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. TIOGA 4 (532996) 138.0 kV to TIOGA 2 (533646) 69.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT8 | Single Phase Fault with Stuck Breaker on 6 GOLDN3 115.00 (533177) 115 kV Bus a. Apply Fault at the 6 GOLDN3 115.00 (533177) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT9 | Single Phase Fault with Stuck Breaker on AEC 3 115.00 (533361) 115 kV Bus a. Apply Fault at the AEC 3 115.00 (533361) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AEC 3 (533361) 115.0 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.2. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.4. AEC 3 (533361) 115.0 kV to AEC W1 (533887) 34.5 kV Two Winding #1 b.5. AEC 3 (533361) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT10 | Single Phase Fault with Stuck Breaker on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply Fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.3. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT11 | Single Phase Fault with Stuck Breaker on INDIANH3 115.00 (533166) 115 kV Bus a. Apply Fault at the INDIANH3 115.00 (533166) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.3. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT12 | Single Phase Fault with Stuck Breaker on LEC U4 3 115.00 (533249) 115 kV Bus a. Apply Fault at the LEC U4 3 115.00 (533249) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 (532662) 14.4 kV to LEC U4 3 (533249) 115.0 kV Two Winding #1 b.2. JARBALO3 (533244) 115.0 kV to LEC U4 3 (533249) 115.0 kV Transmission Circuit #1 b.3. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT13 | Single Phase Fault with Stuck Breaker on LEC U3 3 115.00 (533248) 115 kV Bus a. Apply Fault at the LEC U3 3 115.00 (533248) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT14 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. MORRIS 3 (533305) 115.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT15 | Single Phase Fault with Stuck Breaker on SMOKYHLLS3 115.00 (533378) 115 kV Bus a. Apply Fault at the SMOKYHLLS3 115.00 (533378) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 b.2. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT16 | Single Phase Fault with Stuck Breaker on S ALMA 3 115.00 (533339) 115 kV Bus a. Apply Fault at the S ALMA 3 115.00 (533339) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 b.2. MCDOWEL3 (533335) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT17 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT18 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT19 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT20 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC121 (532740) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT21 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC341 (532741) 13.8 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.3. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT22 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC7 1 (532744) 18.0 kV to EMPEC 7 (532768) 345.0 kV Two Winding #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT23 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT24 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U2 (532652) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT25 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT26 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT27 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U3 (532653) 26.0 kV to JEC N 7 (532766) 345.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT28 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT29 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT30 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT31 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT32 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT33 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT34 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT35 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT36 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT37 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT38 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT39 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT40 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT41 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT42 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT43 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT44 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT45 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT46 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT47 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT48 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT49 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT50 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT51 | Single Phase Fault with Stuck Breaker on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.3. AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV to AUBURN 1 (532880) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT52 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT53 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT54 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICE 6 (530686) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT55 | Single Phase Fault with Stuck Breaker on EMCPHER6 230.00 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 230.00 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to EMCPHER6 (532872) 230.0 kV Transmission Circuit #1 b.2. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.3. EMCPHER6 (532872) 230.0 kV to EMCPHER3 (533417) 115.0 kV to EMCPHER1 (532894) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT56 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U1 (532651) 26.0 kV to JEC 6 (532852) 230.0 kV Two Winding #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT57 | Single Phase Fault with Stuck Breaker on JEC 6 230.00 (532852) 230 kV Bus a. Apply Fault at the JEC 6 230.00 (532852) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC U1 (532651) 26.0 kV to JEC 6 (532852) 230.0 kV Two Winding #1 b.2. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT58 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT59 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC 6 (532852) 230.0 kV to EMANHAT6 (532861) 230.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT60 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT61 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to MIDLAND6 (532855) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT62 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV to LAWHILL1 (532882) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT63 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to LEC U5 6 (532854) 230.0 kV Transmission Circuit #1 b.2. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT64 | Single Phase Fault with Stuck Breaker on MCDOWEL6 230.00 (532862) 230 kV Bus a. Apply Fault at the MCDOWEL6 230.00 (532862) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MCDOWEL6 (532862) 230.0 kV to MCDOWEL3 (533335) 115.0 kV to MCDOWL 1 (532898) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT65 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT66 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT67 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT68 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT69 | Single Phase Fault with Stuck Breaker on MORRIS 6 230.00 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 230.00 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL6 (532862) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 3 (533305) 115.0 kV to MORRIS2X1 (532890) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT70 | Single Phase Fault with Stuck Breaker on NMANHT6 230.00 (532865) 230 kV Bus a. Apply Fault at the NMANHT6 230.00 (532865) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 b.2. NMANHT6 (532865) 230.0 kV to ELMCREK6 (539639) 230.0 kV Transmission Circuit #1 b.3. NMANHT6 (532865) 230.0 kV to NMANHT3 (533347) 115.0 kV to NMANHX1 (532901) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT71 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT72 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT73 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT74 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT75 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT76 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 b.4. SUMMIT 6 (532873) 230.0 kV to SUMMIT 3 (533381) 115.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT77 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT78 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT79 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to MORRIS 6 (532863) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT80 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT81 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT82 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAWHILL6 (532853) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT83 | Single Phase Fault with Stuck Breaker on UNIONRG6 230.00 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 230.00 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.2. SUMMIT 6 (532873) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 b.3. UNIONRG6 (532874) 230.0 kV to DVISTA 6 (532875) 230.0 kV Transmission Circuit #1 b.4. UNIONRG6 (532874) 230.0 kV to UNIONRG3 (533359) 115.0 kV to UNIONRG1 (532817) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT84 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to FRANKLIN5 (532938) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.3. FRANKLIN5 (532938) 161.0 kV to FRANKLIN2 (533876) 69.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT85 | Single Phase Fault with Stuck Breaker on 17TH 4 138.00 (533064) 138 kV Bus a. Apply Fault at the 17TH 4 138.00 (533064) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANAL 4 (533033) 138.0 kV to FOWLER 4 (533043) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.3. FOWLER 4 (533043) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.4. 17TH 4 (533064) 138.0 kV to 17TH 2 (533840) 69.0 kV to 17TH 4 1 (533112) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT86 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.6. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.8. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT87 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. OTTRCRK4 (532997) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.3. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.5. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.6. ALTOONA4 (533001) 138.0 kV to ALTOO E2 (533673) 69.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 b.7. ALTOONA4 (533001) 138.0 kV to ALTOO W2 (533674) 69.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT88 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT89 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT90 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN1 1 (532821) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT91 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT92 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT93 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTN2 1 (532822) 13.8 kV to BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT94 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT95 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.4. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT96 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT97 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.4. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT98 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESW1 1 (533080) 13.2 kV to CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.2. CRESW2 1 (533081) 13.2 kV to CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.3. CRESWLN4 (532981) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT99 | Single Phase Fault with Stuck Breaker on SLATECRK4 138.00 (533070) 138 kV Bus a. Apply Fault at the SLATECRK4 138.00 (533070) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.2. CRESWLN4 (532981) 138.0 kV to SLATECRK4 (533070) 138.0 kV Transmission Circuit #1 b.3. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.4. SLATEXFMR1 (533139) 34.5 kV to SLATEGSU1 (533140) 34.5 kV Transmission Circuit #1 b.5. SLATEGEN1 (533141) 0.7 kV to SLATEGSU1 (533140) 34.5 kV Two Winding #1 b.6. SLATECRK4 (533070) 138.0 kV to SLATEXFMR1 (533139) 34.5 kV to SLATETV1 (533142) 13.2 kV Three Winding #1 b.7. CRESW1 1 (533080) 13.2 kV to CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT100 | Single Phase Fault with Stuck Breaker on MIDLTNT4 138.00 (514804) 138 kV Bus a. Apply Fault at the MIDLTNT4 138.00 (514804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.4. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.7. MIDLTNT4 (514804) 138.0 kV to GEN-2016-071 (587480) 138.0 kV Transmission Circuit #1 b.8. CRESWLN4 (532981) 138.0 kV to OXFORD 4 (532982) 138.0 kV Transmission Circuit #1 b.9. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT101 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHIKASI4 (514757) 138.0 kV to KILDARE4 (514760) 138.0 kV Transmission Circuit #1 b.2. KILDARE4 (514760) 138.0 kV to WHEAGLE4 (514761) 138.0 kV Transmission Circuit #1 b.3. KILDARE4 (514760) 138.0 kV to NWKRKAT4 (514764) 138.0 kV Transmission Circuit #1 b.4. MIDLTNT4 (514804) 138.0 kV to PECKHMT4 (515381) 138.0 kV Transmission Circuit #1 b.5. MIDLTNT4 (514804) 138.0 kV to CHILOCCO4 (521198) 138.0 kV Transmission Circuit #1 b.6. MIDLTNT4 (514804) 138.0 kV to CRESWLN4 (532981) 138.0 kV Transmission Circuit #1 b.7. MIDLTNT4 (514804) 138.0 kV to GEN-2016-071 (587480) 138.0 kV Transmission Circuit #1 b.8. CRESW2 1 (533081) 13.2 kV to CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.9. CRESWLN4 (532981) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT102 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.2. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.5. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT103 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. FARBER 4 (533042) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.6. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT104 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.6. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT105 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT106 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH11 1 (532829) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT107 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.5. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.6. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT108 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.3. WICH12 1 (532830) 13.8 kV to WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT109 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT1 (532723) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT110 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.2. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT111 | Single Phase Fault with Stuck Breaker on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply Fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEC DG 1 (532730) 4.2 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT112 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT2 (532724) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT113 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT114 | Single Phase Fault with Stuck Breaker on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply Fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 b.3. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT115 | Single Phase Fault with Stuck Breaker on EVANS S4 138.00 (533041) 138 kV Bus a. Apply Fault at the EVANS S4 138.00 (533041) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 b.2. EVANS S4 (533041) 138.0 kV to EEC GT3 (532725) 18.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT116 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.5. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 b.6. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT117 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.3. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT118 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT119 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.3. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.4. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT120 | Single Phase Fault with Stuck Breaker on GILL W 4 138.00 (533045) 138 kV Bus a. Apply Fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT121 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.6. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT122 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.3. NEAST3X1 (533110) 11.3 kV to NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT123 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.4. NEAST5X1 (533111) 13.2 kV to NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT124 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.8. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.10. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT125 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.5. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.6. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.7. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT126 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT127 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.3. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT128 | Single Phase Fault with Stuck Breaker on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply Fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 4 (532982) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.3. SUMNER 4 (532984) 138.0 kV to SC10BEL4 (533063) 138.0 kV Transmission Circuit #1 b.4. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.5. SUMNER 4 (532984) 138.0 kV to GEN-2017-121 (761838) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT129 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT130 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT131 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMNER 4 (532984) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT132 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TCROCK 4 (532985) 138.0 kV to TIMBJCT4 (532992) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT133 | Single Phase Fault with Stuck Breaker on VIOLA 4 138.00 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 138.00 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT134 | Single Phase Fault with Stuck Breaker on 17&FAIR3 115.00 (533175) 115 kV Bus a. Apply Fault at the 17&FAIR3 115.00 (533175) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDIANH3 (533166) 115.0 kV to 17&FAIR3 (533175) 115.0 kV Transmission Circuit #1 b.2. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.3. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. 17&FAIR3 (533175) 115.0 kV to EDUCATE3 (533196) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT135 | Single Phase Fault with Stuck Breaker on FORBES 3 115.00 (533157) 115 kV Bus a. Apply Fault at the FORBES 3 115.00 (533157) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORBES 3 (533157) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.2. FORBES 3 (533157) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.3. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.4. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT136 | Single Phase Fault with Stuck Breaker on 41CALIF3 115.00 (533160) 115 kV Bus a. Apply Fault at the 41CALIF3 115.00 (533160) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.3. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT137 | Single Phase Fault with Stuck Breaker on FMC 3 115.00 (533241) 115 kV Bus a. Apply Fault at the FMC 3 115.00 (533241) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.2. FMC 3 (533241) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 b.3. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT138 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.2. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.3. 87TH 1X1 (532818) 13.8 kV to 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT139 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT140 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 b.2. AUBURN 3 (533151) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT141 | Single Phase Fault with Stuck Breaker on AUBURN 6 230.00 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 230.00 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. AUBURN 1 (532880) 14.4 kV to AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT142 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 1 (532880) 14.4 kV to AUBURN 6 (532851) 230.0 kV to AUBURN 3 (533151) 115.0 kV Three Winding #1 b.2. AUBURN 3 (533151) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT143 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.3. AUBURN 3 (533151) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT144 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.2. CHAPMAN3 (533362) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT145 | Single Phase Fault with Stuck Breaker on CHAPMAN3 115.00 (533362) 115 kV Bus a. Apply Fault at the CHAPMAN3 115.00 (533362) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT146 | Single Phase Fault with Stuck Breaker on CLAYCTR3 115.00 (533323) 115 kV Bus a. Apply Fault at the CLAYCTR3 115.00 (533323) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLAYCSS3 (533320) 115.0 kV to CLAYCTR3 (533323) 115.0 kV Transmission Circuit #1 b.2. CLAYCTR3 (533323) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.4. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT147 | Single Phase Fault with Stuck Breaker on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.3. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.4. AEC 3 (533361) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 b.5. CHAPMAN3 (533362) 115.0 kV to EABILEN3 (533365) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT148 | Single Phase Fault with Stuck Breaker on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.4. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.5. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.6. CIRCLE 3 (533413) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT149 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT150 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.2. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 b.5. CIRCLE 1 (532892) 13.8 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT151 | Single Phase Fault with Stuck Breaker on HEC GT 3 115.00 (533421) 115 kV Bus a. Apply Fault at the HEC GT 3 115.00 (533421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to HEC GT 3 (533421) 115.0 kV Transmission Circuit #1 b.3. HEC GT 3 (533421) 115.0 kV to HEC GT2 (532696) 13.8 kV Two Winding #1 b.4. HEC GT 3 (533421) 115.0 kV to HEC GT3 (532697) 13.8 kV Two Winding #1 b.5. HEC GT 3 (533421) 115.0 kV to HEC GT4 (532698) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT152 | Single Phase Fault with Stuck Breaker on CITIES 3 115.00 (533414) 115 kV Bus a. Apply Fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 b.2. CITIES 3 (533414) 115.0 kV to SALTCRK3 (533434) 115.0 kV Transmission Circuit #1 b.3. SALTCRK3 (533434) 115.0 kV to 3 VANBU3 (533435) 115.0 kV Transmission Circuit #1 b.4. CITIES 3 (533414) 115.0 kV to NCTYSVC2 (533505) 69.0 kV to CITIES 1 (533453) 3.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT153 | Single Phase Fault with Stuck Breaker on MANVILE3 115.00 (533426) 115 kV Bus a. Apply Fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to MCPHGT4 (532705) 13.8 kV Two Winding #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT154 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to MCPHGT3 (532704) 13.8 kV Two Winding #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT155 | Single Phase Fault with Stuck Breaker on COLINE 3 115.00 (533153) 115 kV Bus a. Apply Fault at the COLINE 3 115.00 (533153) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.3. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.5. COLINE 3 (533153) 115.0 kV to COLINE 2 (533456) 69.0 kV to COLINE 1 (533443) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT156 | Single Phase Fault with Stuck Breaker on BISMARK3 115.00 (533234) 115 kV Bus a. Apply Fault at the BISMARK3 115.00 (533234) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK3 (533234) 115.0 kV to FAIRGDS3 (533236) 115.0 kV Transmission Circuit #1 b.2. BISMARK3 (533234) 115.0 kV to FMC 3 (533241) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. FAIRGDS3 (533236) 115.0 kV to EUDORA 3 (533240) 115.0 kV Transmission Circuit #1 b.5. EUDORA 3 (533240) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT157 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.4. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT158 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.3. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.5. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT159 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to 54&MERI3 (533156) 115.0 kV Transmission Circuit #1 b.2. 54&MERI3 (533156) 115.0 kV to HOYT 3 (533163) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to HTI JCT3 (533165) 115.0 kV Transmission Circuit #1 b.4. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.5. HOYT 3 (533163) 115.0 kV to HOYT 7 (532765) 345.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT160 | Single Phase Fault with Stuck Breaker on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. INDNOLA3 (533162) 115.0 kV to INDIANH3 (533166) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT161 | Single Phase Fault with Stuck Breaker on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 b.3. HOYT 3 (533163) 115.0 kV to NTHLAND3 (533169) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT162 | Single Phase Fault with Stuck Breaker on INDNOLA3 115.00 (533162) 115 kV Bus a. Apply Fault at the INDNOLA3 115.00 (533162) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to INDNOLA3 (533162) 115.0 kV Transmission Circuit #1 b.2. INDNOLA3 (533162) 115.0 kV to N TYLER3 (533168) 115.0 kV Transmission Circuit #1 b.3. N TYLER3 (533168) 115.0 kV to 4VAN N 3 (533201) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT163 | Single Phase Fault with Stuck Breaker on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply Fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARSHAL3 (533303) 115.0 kV to KNOB HL3 (533332) 115.0 kV Transmission Circuit #1 b.2. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. KNOB HL3 (533332) 115.0 kV to STEELEC7 (640426) 115.0 kV Transmission Circuit #1 b.4. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.5. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT164 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. EAST ST3 (533301) 115.0 kV to LANG 3 (533304) 115.0 kV Transmission Circuit #1 b.3. LANG 3 (533304) 115.0 kV to READING3 (533306) 115.0 kV Transmission Circuit #1 b.4. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.5. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT165 | Single Phase Fault with Stuck Breaker on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply Fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT166 | Single Phase Fault with Stuck Breaker on LWRNCHL3 115.00 (533250) 115 kV Bus a. Apply Fault at the LWRNCHL3 115.00 (533250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U4 3 (533249) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LWRNCHL3 (533250) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 b.3. FREESTATE3 (533257) 115.0 kV to WREN 3 (533280) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT167 | Single Phase Fault with Stuck Breaker on STULL T3 115.00 (533270) 115 kV Bus a. Apply Fault at the STULL T3 115.00 (533270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.3. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT168 | Single Phase Fault with Stuck Breaker on BALDCRK3 115.00 (533232) 115 kV Bus a. Apply Fault at the BALDCRK3 115.00 (533232) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT169 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEC U3 3 (533248) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. LAWHILL1 (532882) 14.4 kV to LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT170 | Single Phase Fault with Stuck Breaker on LAWHILL6 230.00 (532853) 230 kV Bus a. Apply Fault at the LAWHILL6 230.00 (532853) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LWRNCHL3 (533250) 115.0 kV to 6TH ST 3 (533264) 115.0 kV Transmission Circuit #1 b.2. LAWHILL1 (532882) 14.4 kV to LAWHILL6 (532853) 230.0 kV to LWRNCHL3 (533250) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT171 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.7. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT172 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 b.2. MOUN 2X1 (533097) 7.2 kV to MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT173 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.2. NMANHT3 (533347) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT174 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.2. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT175 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.2. NMANHT3 (533347) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT176 | Single Phase Fault with Stuck Breaker on NMANHT3 115.00 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 115.00 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHX1 (532901) 14.4 kV to NMANHT6 (532865) 230.0 kV to NMANHT3 (533347) 115.0 kV Three Winding #1 b.2. NMANHT3 (533347) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT177 | Single Phase Fault with Stuck Breaker on NORTHVW3 115.00 (533371) 115 kV Bus a. Apply Fault at the NORTHVW3 115.00 (533371) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.3. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.4. NORTHVW3 (533371) 115.0 kV to G17-120-TAP (760007) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT178 | Single Phase Fault with Stuck Breaker on PENTAGN3 115.00 (533261) 115 kV Bus a. Apply Fault at the PENTAGN3 115.00 (533261) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAGGARD3 (533243) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.2. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.3. PENTAGN3 (533261) 115.0 kV to MNTCLLO3 (533281) 115.0 kV Transmission Circuit #1 b.4. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.5. MNTCLLO3 (533281) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT179 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 b.2. RENO 1X1 (532807) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT180 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. RENO 2X1 (532810) 14.4 kV to RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT181 | Single Phase Fault with Stuck Breaker on RENO 3 115.00 (533416) 115 kV Bus a. Apply Fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT182 | Single Phase Fault with Stuck Breaker on SALINA 3 115.00 (533376) 115 kV Bus a. Apply Fault at the SALINA 3 115.00 (533376) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFRD3 (533364) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 b.2. NORTHST3 (533370) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.3. NORTHST3 (533370) 115.0 kV to SALINA 3 (533376) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT183 | Single Phase Fault with Stuck Breaker on 29EVENG3 115.00 (533185) 115 kV Bus a. Apply Fault at the 29EVENG3 115.00 (533185) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUINTON3 (533172) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 b.2. 17&FAIR3 (533175) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.4. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.5. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.6. 29EVENG3 (533185) 115.0 kV to 29 GAGE3 (533186) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT184 | Single Phase Fault with Stuck Breaker on S GAGEE3 115.00 (533178) 115 kV Bus a. Apply Fault at the S GAGEE3 115.00 (533178) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 b.2. S GAGEE3 (533178) 115.0 kV to 29EVENG3 (533185) 115.0 kV Transmission Circuit #1 b.3. S GAGEE3 (533178) 115.0 kV to CNTRLXN3 (533188) 115.0 kV Transmission Circuit #1 b.4. S GAGEE3 (533178) 115.0 kV to SHERWOD3 (533194) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT185 | Single Phase Fault with Stuck Breaker on SUMMIT 6 230.00 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 230.00 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.3. SMOKYHLLS3 (533378) 115.0 kV to SO GATE3 (533379) 115.0 kV Transmission Circuit #1 b.4. SO GATE3 (533379) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.5. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT2 1 (532896) 13.8 kV Three Winding #1 b.6. SUMMIT 3 (533381) 115.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMIT3 1 (532897) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT186 | Single Phase Fault with Stuck Breaker on SWLWRNC3 115.00 (533271) 115 kV Bus a. Apply Fault at the SWLWRNC3 115.00 (533271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.5. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.7. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.8. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT187 | Single Phase Fault with Stuck Breaker on SWLWRNC3 115.00 (533271) 115 kV Bus a. Apply Fault at the SWLWRNC3 115.00 (533271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BALDCRK3 (533232) 115.0 kV to LWRNCHL3 (533250) 115.0 kV Transmission Circuit #1 b.2. BALDCRK3 (533232) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.3. FAIRGDS3 (533236) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.4. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.5. FREESTATE3 (533257) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT188 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 41CALIF3 (533160) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.8. AEC 3 (533361) 115.0 kV to AEC E1 (533886) 34.5 kV Two Winding #2 b.9. AEC E1 (533886) 34.5 kV to AEC GT1 (532681) 13.8 kV Two Winding #1 b.10. AEC E1 (533886) 34.5 kV to AEC W1 (533887) 34.5 kV Transmission Circuit #z1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT189 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.4. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.5. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.6. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.7. LWRNCHL3 (533250) 115.0 kV to MOCKBRD3 (533253) 115.0 kV Transmission Circuit #1 b.8. MOCKBRD3 (533253) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. MOCKBRD3 (533253) 115.0 kV to SWLWRNC3 (533271) 115.0 kV Transmission Circuit #1 b.10. STULL 3 (533269) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.11. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT190 | Single Phase Fault with Stuck Breaker on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. MOONLIT3 (533254) 115.0 kV to WAVERLY3 (533278) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 b.5. WAVERLY3 (533278) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT191 | Single Phase Fault with Stuck Breaker on TIMBRLN3 115.00 (533273) 115 kV Bus a. Apply Fault at the TIMBRLN3 115.00 (533273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLIT3 (533254) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.2. BONITA 3 (533262) 115.0 kV to SOUTHTN3 (533265) 115.0 kV Transmission Circuit #1 b.3. SOUTHTN3 (533265) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 b.4. TIMBRLN3 (533273) 115.0 kV to 87TH 3 (533283) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT192 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.3. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.4. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.5. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.6. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.7. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.8. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT193 | Single Phase Fault with Stuck Breaker on WEMPORI3 115.00 (533309) 115 kV Bus a. Apply Fault at the WEMPORI3 115.00 (533309) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST ST3 (533301) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. LANG 3 (533304) 115.0 kV to PRAIRIE3 (533307) 115.0 kV Transmission Circuit #1 b.3. MORRIS 3 (533305) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.4. PRAIRIE3 (533307) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.5. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.6. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT194 | Single Phase Fault with Stuck Breaker on WJCCTY 3 115.00 (533342) 115 kV Bus a. Apply Fault at the WJCCTY 3 115.00 (533342) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANZIO 3 (533321) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.2. FT JCT 3 (533328) 115.0 kV to WJCCTY 3 (533342) 115.0 kV Transmission Circuit #1 b.3. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.5. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT195 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT196 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT197 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.4. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.5. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT198 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT199 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.6. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.7. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT200 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.3. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.4. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. ELPASO 4 (533039) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 b.6. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.7. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.8. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT201 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.4. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 b.5. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT202 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT203 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.3. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 b.4. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.5. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 b.6. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.7. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.8. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT204 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.5. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 b.6. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT205 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.7. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT206 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.3. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 b.4. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 b.5. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.6. NEOSHO 4 (533021) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 b.7. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT207 | Single Phase Fault with Stuck Breaker on KSU W 3 115.00 (533333) 115 kV Bus a. Apply Fault at the KSU W 3 115.00 (533333) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KSU W 3 (533333) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #z1 b.2. KSU W 3 (533333) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 b.3. MATTERS3 (533334) 115.0 kV to KSU E 3 (533346) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT208 | Single Phase Fault with Stuck Breaker on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply Fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.2. TONGATP3 (533219) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.3. BISMARK3 (533234) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.4. LEC U3 3 (533248) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #1 b.5. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 b.6. MIDLADN3 (533252) 115.0 kV to PENTAGN3 (533261) 115.0 kV Transmission Circuit #1 b.7. MIDLADN3 (533252) 115.0 kV to MIDLAND6 (532855) 230.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT209 | Single Phase Fault with Stuck Breaker on TECHILL5 161.00 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.3. 6 GOLDN3 (533177) 115.0 kV to TECHILW3 (533181) 115.0 kV Transmission Circuit #1 b.4. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.5. TECHILW3 (533181) 115.0 kV to TEC E 3 (533203) 115.0 kV Transmission Circuit #1 b.6. TECHILW3 (533181) 115.0 kV to MIDLADN3 (533252) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.9. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILW3 (533181) 115.0 kV to TECHILL5 (532920) 161.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 b.12. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 b.13. TECHIL4X (533885) 12.5 kV to TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT210 | Single Phase Fault with Stuck Breaker on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply Fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MCCRED (300044) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.2. 7MCCREDIE (345088) 345.0 kV to 7OVERTON (345408) 345.0 kV Transmission Circuit #1 b.3. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 b.4. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT211 | Single Phase Fault with Stuck Breaker on 5KELSO 2 161.00 (344850) 161 kV Bus a. Apply Fault at the 5KELSO 2 161.00 (344850) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CAPE GIR1 (344280) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #1 b.2. 5KELSO 1 (344847) 161.0 kV to 5KELSO 2 (344850) 161.0 kV Transmission Circuit #z b.3. 7KELSO 2 (344849) 345.0 kV to 5KELSO 2 (344850) 161.0 kV Two Winding #2 b.4. 5KELSO 2 (344850) 161.0 kV to 5ORAN (345375) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT212 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 b.3. 5HAYTI.S% (338200) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT213 | Single Phase Fault with Stuck Breaker on 5PORTAGEVLE 161.00 (338201) 161 kV Bus a. Apply Fault at the 5PORTAGEVLE 161.00 (338201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 5STEELE! (338194) 161.0 kV to 5HAYTI.S% (338200) 161.0 kV Transmission Circuit #1 b.3. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.4. 5PORTAGEVLE (338201) 161.0 kV to 1PORTGVIL (345534) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT214 | Single Phase Fault with Stuck Breaker on 5HAYTI.S% 161.00 (338200) 161 kV Bus a. Apply Fault at the 5HAYTI.S% 161.00 (338200) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.2. 5HAYTI.S% (338200) 161.0 kV to 5PORTAGEVLE (338201) 161.0 kV Transmission Circuit #1 b.3. 5PORTAGEVLE (338201) 161.0 kV to 1PORTGVIL (345534) 34.5 kV Two Winding #1 b.4. 1HAYTI N (344720) 34.5 kV to 5HAYTI.S% (338200) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT215 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 5JIM HILL% (338202) 161.0 kV Transmission Circuit #1 b.3. 5JIM HILL% (338202) 161.0 kV to 5RECTOR.N# (338689) 161.0 kV Transmission Circuit #1 b.4. 5PARAGOULD% (338204) 161.0 kV to 5HALLIDAY# (338709) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT216 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT217 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT218 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT219 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT220 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT221 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT222 | Single Phase Fault with Stuck Breaker on SEDALIA5 161.00 (541209) 161 kV Bus a. Apply Fault at the SEDALIA5 161.00 (541209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDALIA5 (541209) 161.0 kV to SEDEAST5 (541241) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT223 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT224 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT225 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT226 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT227 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT228 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT229 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT230 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT231 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT232 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT233 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC G2 1 (542956) 24.0 kV to LACYGNE7 (542981) 345.0 kV Two Winding #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT234 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT235 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT236 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT237 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT238 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT239 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT240 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT241 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT242 | Single Phase Fault with Stuck Breaker on JOP145 5 161.00 (547470) 161 kV Bus a. Apply Fault at the JOP145 5 161.00 (547470) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.2. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.3. JOP145 5 (547470) 161.0 kV to JOP145 2 (547539) 69.0 kV to JOP145 1 (547707) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT243 | Single Phase Fault with Stuck Breaker on JOP389 5 161.00 (547483) 161 kV Bus a. Apply Fault at the JOP389 5 161.00 (547483) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SVRCK469 5 (547462) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. TIP292 5 (547472) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.3. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.4. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #2 b.5. JOP389 5 (547483) 161.0 kV to JOP389 2 (547592) 69.0 kV to JOP389 1 (547713) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT244 | Single Phase Fault with Stuck Breaker on RIV167 5 161.00 (547502) 161 kV Bus a. Apply Fault at the RIV167 5 161.00 (547502) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.2. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to R12G4531 (547642) 13.8 kV Two Winding #1 b.4. RIV453 5 (547501) 161.0 kV to R13G167 (547643) 13.8 kV Two Winding #1 b.5. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.6. RIV167 5 (547502) 161.0 kV to R10G1671 (547647) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT245 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT246 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT247 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT248 | Single Phase Fault with Stuck Breaker on RIV452T 5 161.00 (547503) 161 kV Bus a. Apply Fault at the RIV452T 5 161.00 (547503) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.3. RIV453 5 (547501) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 b.4. RIV167 5 (547502) 161.0 kV to RIV452T 5 (547503) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT249 | Single Phase Fault with Stuck Breaker on CAR395 5 161.00 (547485) 161 kV Bus a. Apply Fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.4. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.5. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT250 | Single Phase Fault with Stuck Breaker on FIR417 5 161.00 (547490) 161 kV Bus a. Apply Fault at the FIR417 5 161.00 (547490) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT251 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP145 5 (547470) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 b.2. JOP389 5 (547483) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT252 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 b.3. TNO2-1 (509894) 34.5 kV to T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT253 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT254 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT255 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT256 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT257 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT258 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.3. BAX271 2 (547554) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.4. QUA377 2 (547590) 69.0 kV to HOC404 2 (547601) 69.0 kV Transmission Circuit #1 b.5. HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT259 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.3. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.4. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.6. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT260 | Single Phase Fault with Stuck Breaker on CAR395 5 161.00 (547485) 161 kV Bus a. Apply Fault at the CAR395 5 161.00 (547485) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.3. ASB349 5 (547476) 161.0 kV to A1G349 1 (547649) 13.8 kV Two Winding #1 b.4. ASB349 5 (547476) 161.0 kV to A2G349 1 (547650) 13.8 kV Two Winding #1 b.5. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT261 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT262 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT263 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 b.2. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT264 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT265 | Single Phase Fault with Stuck Breaker on HAWTHN5 161.00 (543665) 161 kV Bus a. Apply Fault at the HAWTHN5 161.00 (543665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAW G5 1 (542951) 22.0 kV to HAWTHN5 (543665) 161.0 kV Two Winding #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT266 | Single Phase Fault with Stuck Breaker on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply Fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT7 1 (542963) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.2. HAWCT8 1 (542964) 13.8 kV to LEVEE 5 (542976) 161.0 kV Two Winding #1 b.3. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT267 | Single Phase Fault with Stuck Breaker on NEASTN5 161.0 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.0 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.5. NEASTN5 (543666) 161.0 kV to Load #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT268 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 b.3. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT269 | Single Phase Fault with Stuck Breaker on HAWTHS_G65 161.00 (543129) 161 kV Bus a. Apply Fault at the HAWTHS_G65 161.00 (543129) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWCT6 1 (542961) 16.8 kV to HAWTHS_G65 (543129) 161.0 kV Two Winding #1 b.2. HAW G9 1 (542967) 13.8 kV to HAWTHS5 (542973) 161.0 kV Two Winding #1 b.3. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT270 | Single Phase Fault with Stuck Breaker on ARCHIE 5 161.00 (541207) 161 kV Bus a. Apply Fault at the ARCHIE 5 161.00 (541207) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCHIE 5 (541207) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 b.2. ARCHIE 5 (541207) 161.0 kV to ADRIAN 5 (541240) 161.0 kV Transmission Circuit #1 b.3. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT271 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT272 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT273 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT274 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT275 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT276 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT277 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT278 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT279 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 b.2. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 b.3. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.4. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.5. MARMTNW5 (532935) 161.0 kV to MARMATN2 (533639) 69.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT280 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLINE 3 (533153) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.2. 4CORNER3 (533158) 115.0 kV to CARB-KW 3 (533195) 115.0 kV Transmission Circuit #1 b.3. SHAWNEE3 (533176) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #1 b.4. SHAWNEE3 (533176) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.5. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 b.6. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 b.7. TECHILE3 (533182) 115.0 kV to STULL T3 (533270) 115.0 kV Transmission Circuit #1 b.8. TECHILE3 (533182) 115.0 kV to INNOVIA1 (533884) 13.8 kV Two Winding #1 b.9. CARB-KW 3 (533195) 115.0 kV to HARTLND3 (533197) 115.0 kV Transmission Circuit #1 b.10. TECHILL1 (532886) 13.8 kV to TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV Three Winding #1 b.11. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT281 | Single Phase Fault with Stuck Breaker on CORONAD3 115.00 (533394) 115 kV Bus a. Apply Fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 b.2. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT282 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT283 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT284 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN3 1 (532816) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT285 | Single Phase Fault with Stuck Breaker on BELAIRE4 138.00 (532988) 138 kV Bus a. Apply Fault at the BELAIRE4 138.00 (532988) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 b.2. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.3. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT286 | Single Phase Fault with Stuck Breaker on AUBURN 3 115.00 (533151) 115 kV Bus a. Apply Fault at the AUBURN 3 115.00 (533151) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 3 (533151) 115.0 kV to CROOKED3 (533155) 115.0 kV Transmission Circuit #1 b.2. AUBURN 3 (533151) 115.0 kV to KEENE 3 (533167) 115.0 kV Transmission Circuit #1 b.3. KEENE 3 (533167) 115.0 kV to S ALMA 3 (533339) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT287 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.4. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT288 | Single Phase Fault with Stuck Breaker on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply Fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT289 | Single Phase Fault with Stuck Breaker on CGENSUB2 69.000 (533662) 69 kV Bus a. Apply Fault at the CGENSUB2 69.000 (533662) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 b.2. CGENTAP2 (533661) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 b.3. CGENSUB2 (533662) 69.0 kV to CHANP2 2 (533664) 69.0 kV Transmission Circuit #1 b.4. CGENSUB2 (533662) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT290 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. BENTON 4 (532986) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT291 | Single Phase Fault with Stuck Breaker on BENTON 4 138.00 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.2. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.3. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT292 | Single Phase Fault with Stuck Breaker on WJCCTYW3 115.00 (533344) 115 kV Bus a. Apply Fault at the WJCCTYW3 115.00 (533344) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCFOUND3 (533329) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.2. GEARY 3 (533336) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 b.3. WJCCTY 3 (533342) 115.0 kV to WJCCTYW3 (533344) 115.0 kV Transmission Circuit #1 b.4. WJCCTYW3 (533344) 115.0 kV to CHAPMAN3 (533362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT293 | Single Phase Fault with Stuck Breaker on STAGGHL3 115.00 (533341) 115 kV Bus a. Apply Fault at the STAGGHL3 115.00 (533341) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL3 (533335) 115.0 kV to STAGGHL3 (533341) 115.0 kV Transmission Circuit #1 b.2. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.3. PEIL 3 (533343) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT294 | Single Phase Fault with Stuck Breaker on WILDCAT3 115.00 (533345) 115 kV Bus a. Apply Fault at the WILDCAT3 115.00 (533345) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STAGGHL3 (533341) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.2. PEIL 3 (533343) 115.0 kV to WILDCAT3 (533345) 115.0 kV Transmission Circuit #1 b.3. PEIL 3 (533343) 115.0 kV to NMANHT3 (533347) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT295 | Single Phase Fault with Stuck Breaker on ALLEN 2 69.000 (533621) 69 kV Bus a. Apply Fault at the ALLEN 2 69.000 (533621) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.5. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT296 | Single Phase Fault with Stuck Breaker on ALLEN 2 69.000 (533621) 69 kV Bus a. Apply Fault at the ALLEN 2 69.000 (533621) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. COALCRK2 (533633) 69.0 kV to ENA 2 (533634) 69.0 kV Transmission Circuit #1 b.5. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT297 | Single Phase Fault with Stuck Breaker on ATHENS 2 69.000 (533623) 69 kV Bus a. Apply Fault at the ATHENS 2 69.000 (533623) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. ATHENS 2 (533623) 69.0 kV to LEHIGTP2 (533638) 69.0 kV Transmission Circuit #1 b.3. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.4. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.5. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT298 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 b.2. BUTLERN2 (533583) 69.0 kV to SKELLY 2 (533602) 69.0 kV Transmission Circuit #1 b.3. BUTLERN2 (533583) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #z1 b.4. BUTLERN2 (533583) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #1 b.5. FRNTR N2 (533593) 69.0 kV to BUTLERS2 (533609) 69.0 kV Transmission Circuit #1 b.6. BUTLERS2 (533609) 69.0 kV to BUTLERS4 (532989) 138.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT299 | Single Phase Fault with Stuck Breaker on CHRYJCT2 69.000 (533680) 69 kV Bus a. Apply Fault at the CHRYJCT2 69.000 (533680) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHERRYV2 (533679) 69.0 kV to CHRYJCT2 (533680) 69.0 kV Transmission Circuit #1 b.2. CHERRYV2 (533679) 69.0 kV to RA6BROO2 (533707) 69.0 kV Transmission Circuit #1 b.3. CHRYJCT2 (533680) 69.0 kV to INDEPEN2 (533694) 69.0 kV Transmission Circuit #1 b.4. CHRYJCT2 (533680) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT300 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.4. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 b.5. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.6. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT301 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #z1 b.2. PARIS 2 (533548) 69.0 kV to CRESWLS2 (533573) 69.0 kV Transmission Circuit #1 b.3. CRESW2 1 (533081) 13.2 kV to CRESWLS2 (533573) 69.0 kV to CRESWLN4 (532981) 138.0 kV Three Winding #1 b.5. CRESWLN4 (532981) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT302 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.2. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT303 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT304 | Single Phase Fault with Stuck Breaker on DEPAUL 2 69.000 (533759) 69 kV Bus a. Apply Fault at the DEPAUL 2 69.000 (533759) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.2. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT305 | Single Phase Fault with Stuck Breaker on DEARING4 138.00 (533002) 138 kV Bus a. Apply Fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. BEECRK2 (533677) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.5. COFFSUB2 (533683) 69.0 kV to DEARING2 (533688) 69.0 kV Transmission Circuit #1 b.6. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT306 | Single Phase Fault with Stuck Breaker on ELPASOE4 138.00 (533059) 138 kV Bus a. Apply Fault at the ELPASOE4 138.00 (533059) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BU11PON4 (533032) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.2. ELPASO 4 (533039) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #z1 b.3. FARBER 4 (533042) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.4. 47TH ST4 (533058) 138.0 kV to ELPASOE4 (533059) 138.0 kV Transmission Circuit #1 b.5. ELPASO 2 (533793) 69.0 kV to MULVANE2 (533821) 69.0 kV Transmission Circuit #1 b.6. ELPASO 2 (533793) 69.0 kV to OAKLAWN2 (533824) 69.0 kV Transmission Circuit #1 b.7. ELPASOE4 (533059) 138.0 kV to ELPASO 2 (533793) 69.0 kV to ELPASO 1 (533105) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT307 | Single Phase Fault with Stuck Breaker on FTSCOTT2 69.000 (533635) 69 kV Bus a. Apply Fault at the FTSCOTT2 69.000 (533635) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.4. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.5. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT308 | Single Phase Fault with Stuck Breaker on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply Fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to FRONTEN2 (533775) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. FRONTEN2 (533775) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT309 | Single Phase Fault with Stuck Breaker on WARE 2 69.000 (533652) 69 kV Bus a. Apply Fault at the WARE 2 69.000 (533652) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTSCOTT2 (533635) 69.0 kV to WARE 2 (533652) 69.0 kV Transmission Circuit #1 b.2. WARE 2 (533652) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.4. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.5. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. SHEFFLD2 (533774) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT310 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 b.4. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.5. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.6. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT311 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. SUNFLRS2 (533670) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.4. CHRYJCT2 (533680) 69.0 kV to LIBERT-2 (533697) 69.0 kV Transmission Circuit #1 b.5. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT312 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to HUDSJCT2 (533764) 69.0 kV Transmission Circuit #1 b.2. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.3. HUDSJCT2 (533764) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.5. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.6. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT313 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.2. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.4. MULBERY2 (533767) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.5. MULBERY2 (533767) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.6. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT314 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEPAUL 2 (533759) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.2. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.3. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.4. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT315 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.6. LITCH1 1 (532952) 13.2 kV to LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT316 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT317 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.4. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.5. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.6. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT318 | Single Phase Fault with Stuck Breaker on MONTGOM4 138.00 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 138.00 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.3. INDEPEN2 (533694) 69.0 kV to MONTGOM2 (533698) 69.0 kV Transmission Circuit #1 b.4. MONTGOM2 (533698) 69.0 kV to WILLJCT2 (533713) 69.0 kV Transmission Circuit #1 b.5. MONTGOM4 (533004) 138.0 kV to MONTGOM2 (533698) 69.0 kV to MONTGOM1 (533091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT319 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT320 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT321 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.3. NEC U3 (532711) 12.0 kV to NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV Three Winding #1 b.4. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT322 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNT2 (533671) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.3. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.4. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT323 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. GIRARD 2 (533761) 69.0 kV to GIR JCT2 (533762) 69.0 kV Transmission Circuit #1 b.5. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.6. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 b.7. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.8. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT324 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. MINNEHA2 (533817) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #1 b.5. NOEASTW2 (533822) 69.0 kV to NOEASTE2 (533823) 69.0 kV Transmission Circuit #z1 b.6. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT325 | Single Phase Fault with Stuck Breaker on OAK 2 69.000 (533547) 69 kV Bus a. Apply Fault at the OAK 2 69.000 (533547) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 b.2. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.3. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.4. OAK 2 (533547) 69.0 kV to PRAIRIJ2 (533563) 69.0 kV Transmission Circuit #1 b.5. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT326 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT327 | Single Phase Fault with Stuck Breaker on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply Fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.4. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT328 | Single Phase Fault with Stuck Breaker on PITTSBG2 69.000 (533770) 69 kV Bus a. Apply Fault at the PITTSBG2 69.000 (533770) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to HUDSJCT2 (533764) 69.0 kV Transmission Circuit #1 b.2. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.3. DEPAUL 2 (533759) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.4. HUDSON-2 (533763) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 b.5. HUDSJCT2 (533764) 69.0 kV to PITTSBG2 (533770) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT329 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.3. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.4. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.5. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT330 | Single Phase Fault with Stuck Breaker on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 b.2. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.3. RICHLAN2 (533550) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.5. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT331 | Single Phase Fault with Stuck Breaker on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AKRON 2 (533541) 69.0 kV to TIMBJCT2 (533558) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT2 (533558) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT332 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT1 (533120) 13.2 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT333 | Single Phase Fault with Stuck Breaker on TIMBJCT2 69.000 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 69.000 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT2 (533558) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT334 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATHENS 2 (533623) 69.0 kV to ORCHARD2 (533643) 69.0 kV Transmission Circuit #1 b.2. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 b.3. ORCHARD2 (533643) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.4. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.5. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.6. TIOGA 2 (533646) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 b.7. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT335 | Single Phase Fault with Stuck Breaker on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply Fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ARCOTAP2 (533620) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.2. ALLEN 2 (533621) 69.0 kV to MONARCH2 (533641) 69.0 kV Transmission Circuit #1 b.3. COALCRK2 (533633) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 b.4. TIOGA 2 (533646) 69.0 kV to UN7ROSE2 (533649) 69.0 kV Transmission Circuit #1 b.5. TIOGA 2 (533646) 69.0 kV to ASHGRJ22 (533660) 69.0 kV Transmission Circuit #1 b.6. TIOGA 2 (533646) 69.0 kV to CHANTAP2 (533666) 69.0 kV Transmission Circuit #1 b.7. TIOGA 2 (533646) 69.0 kV to TIOGA 4 (532996) 138.0 kV to TIOGA 1 (533084) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT336 | Single Phase Fault with Stuck Breaker on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply Fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAN2 (533550) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.2. TIMBJCT2 (533558) 69.0 kV to UDALL 2 (533559) 69.0 kV Transmission Circuit #1 b.3. BU10BEN2 (533585) 69.0 kV to WEAVER 2 (533604) 69.0 kV Transmission Circuit #1 b.4. WEAVER 2 (533604) 69.0 kV to RH JCT 2 (533837) 69.0 kV Transmission Circuit #1 b.5. WEAVER 2 (533604) 69.0 kV to WEAVER 4 (532991) 138.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT337 | Single Phase Fault with Stuck Breaker on LITCH 5 161.00 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 161.00 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AQUARS 2 (533756) 69.0 kV to LITCH N2 (533765) 69.0 kV Transmission Circuit #1 b.2. LITCH N2 (533765) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #z1 b.3. LITCH N2 (533765) 69.0 kV to PITNAC 2 (533769) 69.0 kV Transmission Circuit #1 b.4. LITCH S2 (533766) 69.0 kV to ROUSE 2 (533771) 69.0 kV Transmission Circuit #1 b.5. LITCH S2 (533766) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.6. LITCH N2 (533765) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH2 1 (532953) 13.2 kV Three Winding #1 b.7. LITCH S2 (533766) 69.0 kV to LITCH 5 (532932) 161.0 kV to LITCH1 1 (532952) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT338 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.3. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.4. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.5. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 b.6. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.7. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT339 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to ASB349 5 (547476) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.3. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT340 | Single Phase Fault with Stuck Breaker on BAX488 5 161.00 (547729) 161 kV Bus a. Apply Fault at the BAX488 5 161.00 (547729) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT341 | Single Phase Fault with Stuck Breaker on ATL109 5 161.00 (547466) 161 kV Bus a. Apply Fault at the ATL109 5 161.00 (547466) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.2. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.4. ATL109 5 (547466) 161.0 kV to ATL109 2 (547533) 69.0 kV to ATL109 1 (547702) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT342 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.3. ORO110 5 (547467) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 b.4. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 b.5. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.6. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT343 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT344 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT345 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT346 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT347 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT348 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT349 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT350 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-121 : PTDF of 0.09072 - GEN-2017-131 : PTDF of 0.05985 - GEN-2017-188 : PTDF of 0.03266 - GEN-2017-220 : PTDF of 0.06960 - GEN-2017-221 : PTDF of 0.06960 - GEN-2017-226 : PTDF of 0.08239 - GEN-2017-227 : PTDF of 0.08239 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT351 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT352 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT353 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT354 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT355 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT356 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT357 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT358 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. NEAST_DG1 (543160) 4.2 kV to NE CT11 (542958) 13.8 kV Two Winding #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT359 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTH_B2_1 (543003) 13.2 kV Two Winding #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT360 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 b.3. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT361 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT362 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 13 1 (532805) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT363 | Single Phase Fault with Stuck Breaker on JEC N 7 345.00 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. JEC N 7 (532766) 345.0 kV to JEC 6 (532852) 230.0 kV to JEC 26 1 (532806) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT364 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT365 | Single Phase Fault with Stuck Breaker on SEDLIAW_CAP5161.00 (541146) 161 kV Bus a. Apply Fault at the SEDLIAW_CAP5161.00 (541146) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 b.2. SEDS 2 (541272) 69.0 kV to SEDALIA5 (541209) 161.0 kV Two Winding #2 b.3. SEDLIAW_CAP5 (541146) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT366 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT367 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.2. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 b.3. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT368 | Single Phase Fault with Stuck Breaker on SUB N-161 161.00 (548820) 161 kV Bus a. Apply Fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT369 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT370 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT371 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 b.2. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT372 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT373 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT374 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT375 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT376 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT377 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT378 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-121 : PTDF of 0.09072 - GEN-2017-131 : PTDF of 0.05985 - GEN-2017-188 : PTDF of 0.03266 - GEN-2017-220 : PTDF of 0.06960 - GEN-2017-221 : PTDF of 0.06960 - GEN-2017-226 : PTDF of 0.08239 - GEN-2017-227 : PTDF of 0.08239 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT379 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT380 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT381 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 b.3. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT382 | Single Phase Fault with Stuck Breaker on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply Fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 b.2. CANEYRV7 (532780) 345.0 kV to CANEYWF7 (532781) 345.0 kV Transmission Circuit #1 b.3. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT383 | Single Phase Fault with Stuck Breaker on GEARY 7 345.00 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.3. GEARY 7 (532767) 345.0 kV to GEARY 3 (533336) 115.0 kV to GEARY1X1 (532834) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT384 | Single Phase Fault with Stuck Breaker on HOYT 7 345.00 (532765) 345 kV Bus a. Apply Fault at the HOYT 7 345.00 (532765) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOYT 7 (532765) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. HOYT 7 (532765) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.3. HOYT 7 (532765) 345.0 kV to HOYT 3 (533163) 115.0 kV to HOYT 1 (532804) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT385 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT386 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 b.3. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT387 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT388 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT389 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT390 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT391 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to STRANGR3 (533268) 115.0 kV to STRAN1 1 (532811) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT392 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT393 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT394 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT395 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT396 | Single Phase Fault with Stuck Breaker on S3458 3 345.00 (645458) 345 kV Bus a. Apply Fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT397 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT398 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT399 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT400 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT401 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT402 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT403 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1216 5 (646216) 161.0 kV to Load #O0 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.3. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT404 | Single Phase Fault with Stuck Breaker on S1263 5 161.00 (646263) 161 kV Bus a. Apply Fault at the S1263 5 161.00 (646263) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1263 5 (646263) 161.0 kV Transmission Circuit #1 b.2. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S967 8 (647967) 69.0 kV Transmission Circuit #1 b.5. S1263 5 (646263) 161.0 kV to W BROCK8 (647111) 69.0 kV to S1263T19 (648263) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT405 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT406 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1398 5 (646398) 161.0 kV Transmission Circuit #1 b.3. S1398 5 (646398) 161.0 kV to S1399 5 (646399) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT407 | Single Phase Fault with Stuck Breaker on HUMBOLT5 161.00 (640234) 161 kV Bus a. Apply Fault at the HUMBOLT5 161.00 (640234) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S975 8 (647975) 69.0 kV to S975T4 9 (648275) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT408 | Single Phase Fault with Stuck Breaker on N MADRD5 161.00 (505400) 161 kV Bus a. Apply Fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to N MADRD5 (505400) 161.0 kV Transmission Circuit #1 b.2. N MADRD5 (505400) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 b.3. N MADRD5 (505400) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 b.4. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X1 1 (505401) 13.8 kV Three Winding #1 b.5. N MADRD5 (505400) 161.0 kV to N MADRD2 (505402) 69.0 kV to NMA X2 1 (505403) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT409 | Single Phase Fault with Stuck Breaker on N MADRD5 161.00 (505400) 161 kV Bus a. Apply Fault at the N MADRD5 161.00 (505400) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STJUDEW (300170) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.2. 2LILBRN (301246) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.3. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 b.4. N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV to NMA X1 1 (505401) 13.8 kV Three Winding #1 b.5. N MADRD2 (505402) 69.0 kV to N MADRD5 (505400) 161.0 kV to NMA X2 1 (505403) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT410 | Single Phase Fault with Stuck Breaker on KENNETT5 161.00 (505410) 161 kV Bus a. Apply Fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIGGOTT2 (505406) 69.0 kV to KENNETT2 (505408) 69.0 kV Transmission Circuit #1 b.2. KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV to KEN X1 1 (505407) 13.8 kV Three Winding #1 b.3. KENNETT2 (505408) 69.0 kV to KENNETT5 (505410) 161.0 kV to KEN X2 1 (505409) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT411 | Single Phase Fault with Stuck Breaker on KENNETT5 161.00 (505410) 161 kV Bus a. Apply Fault at the KENNETT5 161.00 (505410) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD5 (505400) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 b.2. KENNETT5 (505410) 161.0 kV to PARAGLD5 (505412) 161.0 kV Transmission Circuit #1 b.3. KENNETT5 (505410) 161.0 kV to KENNETT2 (505408) 69.0 kV to KEN X1 1 (505407) 13.8 kV Three Winding #1 b.4. KENNETT5 (505410) 161.0 kV to KENNETT2 (505408) 69.0 kV to KEN X2 1 (505409) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT412 | Single Phase Fault with Stuck Breaker on PIGGOTT2 69.000 (505406) 69 kV Bus a. Apply Fault at the PIGGOTT2 69.000 (505406) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 b.2. PIGGOTT2 (505406) 69.0 kV to KENNETT2 (505408) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT413 | Single Phase Fault with Stuck Breaker on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENNETT5 (505410) 161.0 kV to PARAGLD5 (505412) 161.0 kV Transmission Circuit #1 b.2. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 b.3. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X1 1 (505411) 13.8 kV Three Winding #1 b.4. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X2 1 (505413) 13.8 kV Three Winding #1 b.5. PARAGLD5 (505412) 161.0 kV to PARAGLD2 (505414) 69.0 kV to PRG X3 1 (505415) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT414 | Single Phase Fault with Stuck Breaker on SIKESTN5 161.00 (505428) 161 kV Bus a. Apply Fault at the SIKESTN5 161.00 (505428) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MINER 1 (345203) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 b.2. SIKETAP5 (505427) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 b.3. SIKESTN5 (505428) 161.0 kV to SIKGEN 1 (505432) 13.8 kV Two Winding #1 b.4. SIKESTN5 (505428) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.5. SIKESTN5 (505428) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 b.6. SIKESTN5 (505428) 161.0 kV to SIKESTN2 (505430) 69.0 kV to SIK X1 1 (505429) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT415 | Single Phase Fault with Stuck Breaker on POP BLF5 161.00 (505438) 161 kV Bus a. Apply Fault at the POP BLF5 161.00 (505438) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GRNFRT (300084) 161.0 kV to POP BLF5 (505438) 161.0 kV Transmission Circuit #1 b.2. POP BLF5 (505438) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 b.3. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X1 1 (505435) 13.8 kV Three Winding #1 b.4. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X2 1 (505437) 13.8 kV Three Winding #1 b.5. POP BLF5 (505438) 161.0 kV to POP BLF2 (505436) 69.0 kV to PBL X3 1 (505439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT416 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Load #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT417 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD2 (505402) 69.0 kV to MALDEN 2 (505404) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT418 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT419 | Single Phase Fault with Stuck Breaker on MALDEN 2 69.000 (505404) 69 kV Bus a. Apply Fault at the MALDEN 2 69.000 (505404) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MALDEN 2 (505404) 69.0 kV to PIGGOTT2 (505406) 69.0 kV Transmission Circuit #1 b.2. MALDEN 2 (505404) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT420 | Single Phase Fault with Stuck Breaker on CENTR H5 161.00 (505416) 161 kV Bus a. Apply Fault at the CENTR H5 161.00 (505416) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 b.2. CENTR H5 (505416) 161.0 kV to JONESBO5 (505418) 161.0 kV Transmission Circuit #1 b.3. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X1 1 (505417) 13.8 kV Three Winding #1 b.4. CENTR H5 (505416) 161.0 kV to CENTR H2 (505420) 69.0 kV to CEH X2 1 (505419) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT421 | Single Phase Fault with Stuck Breaker on 5ESSEX 161.00 (300075) 161 kV Bus a. Apply Fault at the 5ESSEX 161.00 (300075) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5ESSEX (300075) 161.0 kV to 7ESSEX (300038) 345.0 kV Two Winding #1 b.2. 5ESSEX (300075) 161.0 kV to 5ESSEXGSU1 (301533) 161.0 kV Transmission Circuit #1 b.3. 5ESSEX (300075) 161.0 kV to 5STODDARD 2 (345791) 161.0 kV Transmission Circuit #1 b.4. 5ESSEX (300075) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.5. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #1 b.6. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #2 b.7. SIKESTN5 (505428) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.8. IDALIA 5 (505434) 161.0 kV to ASHRVL5 (505441) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT422 | Single Phase Fault with Stuck Breaker on CARTHAG5 161.00 (505488) 161 kV Bus a. Apply Fault at the CARTHAG5 161.00 (505488) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEO SPA5 (505486) 161.0 kV to CARTHAG5 (505488) 161.0 kV Transmission Circuit #1 b.2. CARTHAG5 (505488) 161.0 kV to ATL109 5 (547466) 161.0 kV Transmission Circuit #1 b.3. CARTHAG5 (505488) 161.0 kV to LAR382 5 (547479) 161.0 kV Transmission Circuit #1 b.4. CARTHAG5 (505488) 161.0 kV to CAR395 5 (547485) 161.0 kV Transmission Circuit #1 b.5. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.6. CAR395 5 (547485) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.7. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X1 1 (505487) 13.8 kV Three Winding #1 b.8. CARTHAG5 (505488) 161.0 kV to CARTHG 2 (505490) 69.0 kV to CRG X2 1 (505489) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT423 | Single Phase Fault with Stuck Breaker on NWARSAW5 161.00 (541314) 161 kV Bus a. Apply Fault at the NWARSAW5 161.00 (541314) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5EDMONS (300034) 161.0 kV to 5GRAVOIB1 (300555) 161.0 kV Transmission Circuit #1 b.2. 5EDMONS (300034) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.3. 5CLINTN (300071) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.4. 5TURKEYCRK (301370) 161.0 kV to 5LOSTVALY (301402) 161.0 kV Transmission Circuit #1 b.5. 5LOSTVALY (301402) 161.0 kV to TRUMAN 5 (505502) 161.0 kV Transmission Circuit #1 b.6. 5LOSTVALY (301402) 161.0 kV to NWARSAW5 (541314) 161.0 kV Transmission Circuit #1 b.7. TRUMAN 5 (505502) 161.0 kV to TRU123 1 (505504) 13.8 kV Two Winding #1 b.8. TRUMAN 5 (505502) 161.0 kV to TRU456 1 (505506) 13.8 kV Two Winding #1 b.9. NWARSAW2 (541315) 69.0 kV to NWARSAW5 (541314) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT424 | Single Phase Fault with Stuck Breaker on STROTHR2 69.000 (533556) 69 kV Bus a. Apply Fault at the STROTHR2 69.000 (533556) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to STROTHR2 (533556) 69.0 kV Transmission Circuit #1 b.2. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT425 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.0 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.0 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.3. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.4. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.5. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT426 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.4. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.5. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.6. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.7. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.8. HARPER 4 (539668) 138.0 kV to HARPER 1 (539713) 34.5 kV to HARPER-T (539913) 8.7 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT427 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT428 | Single Phase Fault with Stuck Breaker on CONCRD6 230.00 (539658) 230 kV Bus a. Apply Fault at the CONCRD6 230.00 (539658) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. CONCORD3 (539657) 115.0 kV to CONCRD6 (539658) 230.0 kV to CONCOD-T (539904) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT429 | Single Phase Fault with Stuck Breaker on GRNLEAF3 115.00 (539665) 115 kV Bus a. Apply Fault at the GRNLEAF3 115.00 (539665) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON1 (539655) 13.8 kV to CLIFTON3 (539656) 115.0 kV Two Winding #1 b.3. CLIFTON3 (539656) 115.0 kV to CONCORD3 (539657) 115.0 kV Transmission Circuit #1 b.4. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.5. CLIFTON3 (539656) 115.0 kV to CLIFSUB1 (539704) 34.5 kV to CLIFTN-T (539903) 13.8 kV Three Winding #1 b.6. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT430 | Single Phase Fault with Stuck Breaker on CLIFTON3 115.00 (539656) 115 kV Bus a. Apply Fault at the CLIFTON3 115.00 (539656) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOB HL3 (533332) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.2. CLIFTON3 (539656) 115.0 kV to GRNLEAF3 (539665) 115.0 kV Transmission Circuit #1 b.3. GRNLEAF3 (539665) 115.0 kV to GRNLEAF1 (539711) 34.5 kV to GRNLEF-T (539911) 12.8 kV Three Winding #1 b.4. CLIFTN-T (539903) 13.8 kV to CLIFSUB1 (539704) 34.5 kV to CLIFTON3 (539656) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT431 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT432 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT433 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT434 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT435 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT436 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP#1 (541165) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.2. S.HARP#2 (541166) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.3. S.HARP#3 (541167) 13.8 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.4. ARCHIE 5 (541207) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT437 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.4. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT438 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT439 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT440 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT441 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT442 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT443 | Single Phase Fault with Stuck Breaker on METRO 5 161.00 (546742) 161 kV Bus a. Apply Fault at the METRO 5 161.00 (546742) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.4. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT444 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 b.4. FARML 4 (512734) 138.0 kV to Fixed Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT445 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT446 | Single Phase Fault with Stuck Breaker on PAWN-ED3 115.00 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 115.00 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.4. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.6. KINSLEY3 (530619) 115.0 kV to GEN-2016-016 (587120) 115.0 kV Transmission Circuit #1 b.7. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.8. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.9. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.10. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.11. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT447 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT448 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT449 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to SHELDON7 (640278) 115.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT450 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT451 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT452 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT453 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT454 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT455 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT456 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT457 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT458 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 8 (640446) 69.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT459 | Single Phase Fault with Stuck Breaker on S963 8 69.000 (647963) 69 kV Bus a. Apply Fault at the S963 8 69.000 (647963) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER_602 8 (640143) 69.0 kV to COOPER 8 (640446) 69.0 kV Transmission Circuit #z1 b.2. COOPER_602 8 (640143) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.3. AUBRNT 8 (647101) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.4. W BROCK8 (647111) 69.0 kV to S963 8 (647963) 69.0 kV Transmission Circuit #1 b.5. S963 8 (647963) 69.0 kV to S973 8 (647973) 69.0 kV Transmission Circuit #1 b.6. S963 8 (647963) 69.0 kV to S977 8 (647977) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT460 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK 2 (533547) 69.0 kV to RAINBOW2 (533549) 69.0 kV Transmission Circuit #1 b.2. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.3. STROTHR2 (533556) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.4. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.5. WINFLD 2 (533561) 69.0 kV to EAST SUB 2 (533990) 69.0 kV Transmission Circuit #1 b.6. WINFLD 2 (533561) 69.0 kV to WEST SUB 2 (533991) 69.0 kV Transmission Circuit #1 b.7. EAST SUB 2 (533990) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 b.8. WEST SUB 2 (533991) 69.0 kV to VIKING SUB 2 (533992) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT461 | Single Phase Fault with Stuck Breaker on WINFLD 2 69.000 (533561) 69 kV Bus a. Apply Fault at the WINFLD 2 69.000 (533561) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAINBOW2 (533549) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 b.2. WINFLD 2 (533561) 69.0 kV to Load #P1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT462 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT463 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT464 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT465 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT466 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT467 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT468 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT469 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT470 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT471 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT472 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT473 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT474 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT475 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT476 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT477 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to G17-108-TAP (761278) 161.0 kV Transmission Circuit #1 b.2. 5CLINTN (300071) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT478 | Single Phase Fault with Stuck Breaker on 5GENTRY 161.00 (300073) 161 kV Bus a. Apply Fault at the 5GENTRY 161.00 (300073) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GENTRY (300073) 161.0 kV to 5NODWAY (300104) 161.0 kV Transmission Circuit #1 b.2. 5GENTRY (300073) 161.0 kV to 5FAIRPTB2 (300076) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT479 | Single Phase Fault with Stuck Breaker on 5FAIRPTB2 161.00 (300076) 161 kV Bus a. Apply Fault at the 5FAIRPTB2 161.00 (300076) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.2. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT480 | Single Phase Fault with Stuck Breaker on 5HICKCK 161.00 (300087) 161 kV Bus a. Apply Fault at the 5HICKCK 161.00 (300087) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HICKCK (300087) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #1 b.2. 5HICKCK (300087) 161.0 kV to 5LOCUST (300094) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT481 | Single Phase Fault with Stuck Breaker on 5NEWMAD 161.00 (300103) 161 kV Bus a. Apply Fault at the 5NEWMAD 161.00 (300103) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMAD (300103) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 b.2. 5NEWMAD (300103) 161.0 kV to 5NEWMADCP (301405) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT482 | Single Phase Fault with Stuck Breaker on 5OSBORN 161.00 (300107) 161 kV Bus a. Apply Fault at the 5OSBORN 161.00 (300107) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSBORN (300107) 161.0 kV to 5FAIRPTB1 (301564) 161.0 kV Transmission Circuit #1 b.2. 5OSBORN (300107) 161.0 kV to 5REX (301310) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT483 | Single Phase Fault with Stuck Breaker on 5OSCEOLTP 161.00 (300108) 161 kV Bus a. Apply Fault at the 5OSCEOLTP 161.00 (300108) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOLTP (300108) 161.0 kV to 5OSCEOKCTP (301477) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOLTP (300108) 161.0 kV to 5COLLINS (300816) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT484 | Single Phase Fault with Stuck Breaker on 5PITTSV 161.00 (300110) 161 kV Bus a. Apply Fault at the 5PITTSV 161.00 (300110) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5PITTSV (300110) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #1 b.2. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT485 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to WINDSR 5 (541217) 161.0 kV Transmission Circuit #1 b.2. 5SEDALA (300117) 161.0 kV to SEDALIA5 (541209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT486 | Single Phase Fault with Stuck Breaker on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply Fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HOLDENB2 (300124) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5HOLDENB2 (300124) 161.0 kV to 5HOLDENB1 (301561) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT487 | Single Phase Fault with Stuck Breaker on 2STJUDEW 69.000 (300170) 69 kV Bus a. Apply Fault at the 2STJUDEW 69.000 (300170) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2STJUDEW (300170) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.2. 2STJUDEW (300170) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT488 | Single Phase Fault with Stuck Breaker on 2JAMESN 69.000 (300202) 69 kV Bus a. Apply Fault at the 2JAMESN 69.000 (300202) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2JAMESN (300202) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2JAMESN (300202) 69.0 kV to 2GALLTN (300198) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT489 | Single Phase Fault with Stuck Breaker on 2KIDDER 69.000 (300203) 69 kV Bus a. Apply Fault at the 2KIDDER 69.000 (300203) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2KIDDER (300203) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2KIDDER (300203) 69.0 kV to 2MABELTP (300215) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT490 | Single Phase Fault with Stuck Breaker on 2PATBRG 69.000 (300209) 69 kV Bus a. Apply Fault at the 2PATBRG 69.000 (300209) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PATBRG (300209) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2PATBRG (300209) 69.0 kV to 2BETHNY (300220) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT491 | Single Phase Fault with Stuck Breaker on 2DRLNGT 69.000 (300248) 69 kV Bus a. Apply Fault at the 2DRLNGT 69.000 (300248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DRLNGT (300248) 69.0 kV to 2ALBNYTP (300245) 69.0 kV Transmission Circuit #1 b.2. 2DRLNGT (300248) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT492 | Single Phase Fault with Stuck Breaker on 5FAIRPTB1 161.00 (301564) 161 kV Bus a. Apply Fault at the 5FAIRPTB1 161.00 (301564) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FAIRPT (300249) 69.0 kV to 5FAIRPTB2 (300076) 161.0 kV Two Winding #2 b.2. 2FAIRPT (300249) 69.0 kV to 5FAIRPTB1 (301564) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT493 | Single Phase Fault with Stuck Breaker on 2CENTRV 69.000 (300323) 69 kV Bus a. Apply Fault at the 2CENTRV 69.000 (300323) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CENTRV (300323) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 b.2. 2CENTRV (300323) 69.0 kV to 2ROSEHL (300334) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT494 | Single Phase Fault with Stuck Breaker on 2RT Z 69.000 (300325) 69 kV Bus a. Apply Fault at the 2RT Z 69.000 (300325) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2RT Z (300325) 69.0 kV to 2ELM (300327) 69.0 kV Transmission Circuit #1 b.2. 2RT Z (300325) 69.0 kV to 2COLMBUS (300326) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT495 | Single Phase Fault with Stuck Breaker on 2ELM 69.000 (300327) 69 kV Bus a. Apply Fault at the 2ELM 69.000 (300327) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ELM (300327) 69.0 kV to 2RT Z (300325) 69.0 kV Transmission Circuit #1 b.2. 2ELM (300327) 69.0 kV to 2HOLDEN (300336) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT496 | Single Phase Fault with Stuck Breaker on 2ROSEHL 69.000 (300334) 69 kV Bus a. Apply Fault at the 2ROSEHL 69.000 (300334) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ROSEHL (300334) 69.0 kV to 2CENTRV (300323) 69.0 kV Transmission Circuit #1 b.2. 2ROSEHL (300334) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT497 | Single Phase Fault with Stuck Breaker on 2GEOGT2 69.000 (300530) 69 kV Bus a. Apply Fault at the 2GEOGT2 69.000 (300530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GEOGT2 (300530) 69.0 kV to 2GEORGE (300531) 69.0 kV Transmission Circuit #1 b.2. 2GEOGT2 (300530) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT498 | Single Phase Fault with Stuck Breaker on 2LINCLN 69.000 (300534) 69 kV Bus a. Apply Fault at the 2LINCLN 69.000 (300534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LINCLN (300534) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2LINCLN (300534) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT499 | Single Phase Fault with Stuck Breaker on 5SEDALA 161.00 (300117) 161 kV Bus a. Apply Fault at the 5SEDALA 161.00 (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SEDALI (300541) 69.0 kV to 5SEDALA (300117) 161.0 kV Two Winding #3 b.2. 2SEDALI (300541) 69.0 kV to 2SYLVAN (300545) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT500 | Single Phase Fault with Stuck Breaker on 2IVYBND 69.000 (300557) 69 kV Bus a. Apply Fault at the 2IVYBND 69.000 (300557) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2IVYBND (300557) 69.0 kV to 2MTHULD (300558) 69.0 kV Transmission Circuit #1 b.2. 2IVYBND (300557) 69.0 kV to 2VERSAL (300565) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT501 | Single Phase Fault with Stuck Breaker on 2MTHULD 69.000 (300558) 69 kV Bus a. Apply Fault at the 2MTHULD 69.000 (300558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTHULD (300558) 69.0 kV to 2LINCLN (300534) 69.0 kV Transmission Circuit #1 b.2. 2MTHULD (300558) 69.0 kV to 2IVYBND (300557) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT502 | Single Phase Fault with Stuck Breaker on 2APPLTN 69.000 (300687) 69 kV Bus a. Apply Fault at the 2APPLTN 69.000 (300687) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2APPLTN (300687) 69.0 kV to 2LADUE (300702) 69.0 kV Transmission Circuit #1 b.2. 2APPLTN (300687) 69.0 kV to 2TABORVL (300813) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT503 | Single Phase Fault with Stuck Breaker on 2AUSTIN 69.000 (300688) 69 kV Bus a. Apply Fault at the 2AUSTIN 69.000 (300688) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AUSTIN (300688) 69.0 kV to 2ELYNTP (300699) 69.0 kV Transmission Circuit #1 b.2. 2AUSTIN (300688) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT504 | Single Phase Fault with Stuck Breaker on 5BUTLER 161.00 (301342) 161 kV Bus a. Apply Fault at the 5BUTLER 161.00 (301342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BUTLER (300689) 69.0 kV to 5BUTLER (301342) 161.0 kV Two Winding #1 b.2. 2BUTLER (300689) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT505 | Single Phase Fault with Stuck Breaker on 2BUTLERE 69.000 (300690) 69 kV Bus a. Apply Fault at the 2BUTLERE 69.000 (300690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BUTLERE (300690) 69.0 kV to 2BUTLER (300689) 69.0 kV Transmission Circuit #1 b.2. 2BUTLERE (300690) 69.0 kV to 2PIPER (300706) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT506 | Single Phase Fault with Stuck Breaker on 5CLINTN 161.00 (300071) 161 kV Bus a. Apply Fault at the 5CLINTN 161.00 (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #3 b.2. 2CLINTN (300692) 69.0 kV to 5CLINTN (300071) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT507 | Single Phase Fault with Stuck Breaker on 2CREIGH 69.000 (300696) 69 kV Bus a. Apply Fault at the 2CREIGH 69.000 (300696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CREIGH (300696) 69.0 kV to 2LEETON (300703) 69.0 kV Transmission Circuit #1 b.2. 2CREIGH (300696) 69.0 kV to 2AUSTIN (300688) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT508 | Single Phase Fault with Stuck Breaker on 2GAINES 69.000 (300701) 69 kV Bus a. Apply Fault at the 2GAINES 69.000 (300701) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GAINES (300701) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2GAINES (300701) 69.0 kV to 2MTZION (300810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT509 | Single Phase Fault with Stuck Breaker on 2LADUE 69.000 (300702) 69 kV Bus a. Apply Fault at the 2LADUE 69.000 (300702) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LADUE (300702) 69.0 kV to 2CLINTNLD (301626) 69.0 kV Transmission Circuit #1 b.2. 2LADUE (300702) 69.0 kV to 2APPLTN (300687) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT510 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT511 | Single Phase Fault with Stuck Breaker on 2DAMSCUS 69.000 (300804) 69 kV Bus a. Apply Fault at the 2DAMSCUS 69.000 (300804) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DAMSCUS (300804) 69.0 kV to 2MTZION (300810) 69.0 kV Transmission Circuit #1 b.2. 2DAMSCUS (300804) 69.0 kV to 2OSCEOLA (300817) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT512 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT513 | Single Phase Fault with Stuck Breaker on 2AIDJCT 69.000 (301191) 69 kV Bus a. Apply Fault at the 2AIDJCT 69.000 (301191) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AIDJCT (301191) 69.0 kV to 2BLOOMF (301237) 69.0 kV Transmission Circuit #1 b.2. 2AIDJCT (301191) 69.0 kV to 2PUXICO (301221) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT514 | Single Phase Fault with Stuck Breaker on 2ADVANC 69.000 (301235) 69 kV Bus a. Apply Fault at the 2ADVANC 69.000 (301235) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ADVANC (301235) 69.0 kV to 2ARDEOLA (301257) 69.0 kV Transmission Circuit #1 b.2. 2ADVANC (301235) 69.0 kV to 2WHTWTR (301279) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT515 | Single Phase Fault with Stuck Breaker on 2ANNSTN 69.000 (301236) 69 kV Bus a. Apply Fault at the 2ANNSTN 69.000 (301236) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ANNSTN (301236) 69.0 kV to 2LILBRN (301246) 69.0 kV Transmission Circuit #1 b.2. 2ANNSTN (301236) 69.0 kV to 2DOGWOD (301239) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT516 | Single Phase Fault with Stuck Breaker on 2BLOOMF 69.000 (301237) 69 kV Bus a. Apply Fault at the 2BLOOMF 69.000 (301237) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BLOOMF (301237) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2BLOOMF (301237) 69.0 kV to 2AIDJCT (301191) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT517 | Single Phase Fault with Stuck Breaker on 2FRISCO 69.000 (301240) 69 kV Bus a. Apply Fault at the 2FRISCO 69.000 (301240) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2FRISCO (301240) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2FRISCO (301240) 69.0 kV to 2PARMA (301250) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT518 | Single Phase Fault with Stuck Breaker on IDALIA 5 161.00 (505434) 161 kV Bus a. Apply Fault at the IDALIA 5 161.00 (505434) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #1 b.2. 2IDALIA (301243) 69.0 kV to IDALIA 5 (505434) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT519 | Single Phase Fault with Stuck Breaker on 2IDALMA 69.000 (301244) 69 kV Bus a. Apply Fault at the 2IDALMA 69.000 (301244) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2IDALMA (301244) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2IDALMA (301244) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT520 | Single Phase Fault with Stuck Breaker on 2MOREHS 69.000 (301248) 69 kV Bus a. Apply Fault at the 2MOREHS 69.000 (301248) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOREHS (301248) 69.0 kV to 2MATHWS (301247) 69.0 kV Transmission Circuit #1 b.2. 2MOREHS (301248) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT521 | Single Phase Fault with Stuck Breaker on 2MOREJT 69.000 (301249) 69 kV Bus a. Apply Fault at the 2MOREJT 69.000 (301249) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MOREJT (301249) 69.0 kV to 2MOREHS (301248) 69.0 kV Transmission Circuit #1 b.2. 2MOREJT (301249) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT522 | Single Phase Fault with Stuck Breaker on 2PARMA 69.000 (301250) 69 kV Bus a. Apply Fault at the 2PARMA 69.000 (301250) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PARMA (301250) 69.0 kV to 2FRISCO (301240) 69.0 kV Transmission Circuit #1 b.2. 2PARMA (301250) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT523 | Single Phase Fault with Stuck Breaker on 2AVONKN 69.000 (301285) 69 kV Bus a. Apply Fault at the 2AVONKN 69.000 (301285) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2AVONKN (301285) 69.0 kV to 2BAELLS (301286) 69.0 kV Transmission Circuit #1 b.2. 2AVONKN (301285) 69.0 kV to 2GIDJCT (301293) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT524 | Single Phase Fault with Stuck Breaker on 5OSCEOKCTP 161.00 (301477) 161 kV Bus a. Apply Fault at the 5OSCEOKCTP 161.00 (301477) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOKCTP (301477) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOKCTP (301477) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT525 | Single Phase Fault with Stuck Breaker on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply Fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KELSO 1 (344847) 161.0 kV to 7KELSO 1 (344848) 345.0 kV Two Winding #1 b.2. 5KELSO 1 (344847) 161.0 kV to 5MINER 1 (345203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT526 | Single Phase Fault with Stuck Breaker on 5MINER 1 161.00 (345203) 161 kV Bus a. Apply Fault at the 5MINER 1 161.00 (345203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MINER 1 (345203) 161.0 kV to 5KELSO 1 (344847) 161.0 kV Transmission Circuit #1 b.2. 5MINER 1 (345203) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT527 | Single Phase Fault with Stuck Breaker on 5RIDGELY TN 161.00 (360521) 161 kV Bus a. Apply Fault at the 5RIDGELY TN 161.00 (360521) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5RIDGELY TN (360521) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 b.2. 5RIDGELY TN (360521) 161.0 kV to 5NAUVOO TN (360479) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT528 | Single Phase Fault with Stuck Breaker on 5TIPTONVL TN161.00 (361261) 161 kV Bus a. Apply Fault at the 5TIPTONVL TN161.00 (361261) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5TIPTONVL TN (361261) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5TIPTONVL TN (361261) 161.0 kV to 5RIDGELY TN (360521) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT529 | Single Phase Fault with Stuck Breaker on SIKETAP5 161.00 (505427) 161 kV Bus a. Apply Fault at the SIKETAP5 161.00 (505427) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIKETAP5 (505427) 161.0 kV to SIKESTN5 (505428) 161.0 kV Transmission Circuit #1 b.2. SIKETAP5 (505427) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT530 | Single Phase Fault with Stuck Breaker on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply Fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT531 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT532 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT533 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT534 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT535 | Single Phase Fault with Stuck Breaker on STRANGR7 345.00 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. STRANGR7 (532772) 345.0 kV to HOYT 7 (532765) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT536 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT537 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to GEN-2017-125 (761901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT538 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT539 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT540 | Single Phase Fault with Stuck Breaker on EXPED WF7 345.00 (532790) 345 kV Bus a. Apply Fault at the EXPED WF7 345.00 (532790) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPED WF7 (532790) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 b.2. EXPED WF7 (532790) 345.0 kV to E1 TX1 (534048) 34.5 kV to E1 TERT1 (534049) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT541 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT542 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT543 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT544 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT545 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT546 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT547 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT548 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT549 | Single Phase Fault with Stuck Breaker on EEUREKA3 115.00 (533302) 115 kV Bus a. Apply Fault at the EEUREKA3 115.00 (533302) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EEUREKA3 (533302) 115.0 kV to VAUGHN 3 (533308) 115.0 kV Transmission Circuit #1 b.2. EEUREKA3 (533302) 115.0 kV to OTTRCRK3 (533315) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT550 | Single Phase Fault with Stuck Breaker on BERG 3 115.00 (533367) 115 kV Bus a. Apply Fault at the BERG 3 115.00 (533367) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERG 3 (533367) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 b.2. BERG 3 (533367) 115.0 kV to SMOKYHLLS3 (533378) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT551 | Single Phase Fault with Stuck Breaker on MENTOR 3 115.00 (533374) 115 kV Bus a. Apply Fault at the MENTOR 3 115.00 (533374) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to SUMMIT 3 (533381) 115.0 kV Transmission Circuit #1 b.2. MENTOR 3 (533374) 115.0 kV to CORONAD3 (533394) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT552 | Single Phase Fault with Stuck Breaker on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply Fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUNDRG3 (533429) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. MOUNDRG3 (533429) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT553 | Single Phase Fault with Stuck Breaker on CLDWELL4 138.00 (539003) 138 kV Bus a. Apply Fault at the CLDWELL4 138.00 (539003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLDWELL4 (539003) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.2. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT554 | Single Phase Fault with Stuck Breaker on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply Fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILAN_GOAB (539008) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.2. MILAN_GOAB (539008) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT555 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT556 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT557 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT558 | Single Phase Fault with Stuck Breaker on ELMCREEK7 345.00 (539805) 345 kV Bus a. Apply Fault at the ELMCREEK7 345.00 (539805) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREEK7 (539805) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. ELMCREEK7 (539805) 345.0 kV to ELMCREK6 (539639) 230.0 kV to ELMCREEK1 (539806) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT559 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT560 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT561 | Single Phase Fault with Stuck Breaker on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 b.2. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT562 | Single Phase Fault with Stuck Breaker on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. SMTHVL 5 (541204) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT563 | Single Phase Fault with Stuck Breaker on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply Fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT564 | Single Phase Fault with Stuck Breaker on TWA 5 161.00 (541214) 161 kV Bus a. Apply Fault at the TWA 5 161.00 (541214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 b.2. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT565 | Single Phase Fault with Stuck Breaker on HLLMRK 5 161.00 (541215) 161 kV Bus a. Apply Fault at the HLLMRK 5 161.00 (541215) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HLLMRK 5 (541215) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 b.2. HLLMRK 5 (541215) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT566 | Single Phase Fault with Stuck Breaker on PLTCTY 5 161.00 (541221) 161 kV Bus a. Apply Fault at the PLTCTY 5 161.00 (541221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLTCTY 5 (541221) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. PLTCTY 5 (541221) 161.0 kV to KCI 5 (541212) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT567 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT568 | Single Phase Fault with Stuck Breaker on MARYVLE5 161.00 (541251) 161 kV Bus a. Apply Fault at the MARYVLE5 161.00 (541251) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARYVLE5 (541251) 161.0 kV to 5MARYVB2 (300097) 161.0 kV Transmission Circuit #1 b.2. MARYVLE5 (541251) 161.0 kV to BRADDYVILLE5 (635038) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT569 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT570 | Single Phase Fault with Stuck Breaker on EAST 5 161.00 (541254) 161 kV Bus a. Apply Fault at the EAST 5 161.00 (541254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EAST 5 (541254) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. EAST 5 (541254) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT571 | Single Phase Fault with Stuck Breaker on LAKE RD5 161.00 (541255) 161 kV Bus a. Apply Fault at the LAKE RD5 161.00 (541255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKE RD5 (541255) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 b.2. LAKE RD5 (541255) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT572 | Single Phase Fault with Stuck Breaker on IND PRK5 161.00 (541256) 161 kV Bus a. Apply Fault at the IND PRK5 161.00 (541256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IND PRK5 (541256) 161.0 kV to EASTOWN5 (541401) 161.0 kV Transmission Circuit #1 b.2. IND PRK5 (541256) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT573 | Single Phase Fault with Stuck Breaker on COOK 5 161.00 (541257) 161 kV Bus a. Apply Fault at the COOK 5 161.00 (541257) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOK 5 (541257) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. COOK 5 (541257) 161.0 kV to EDMOND5 (541355) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT574 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRDGE 2 (541260) 69.0 kV to RNRIDGE5 (541230) 161.0 kV Two Winding #1 b.2. RNRDGE 2 (541260) 69.0 kV to STALEY 2 (541261) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT575 | Single Phase Fault with Stuck Breaker on FREEMAN2 69.000 (541291) 69 kV Bus a. Apply Fault at the FREEMAN2 69.000 (541291) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FREEMAN2 (541291) 69.0 kV to S.HARP 2 (541343) 69.0 kV Transmission Circuit #1 b.2. FREEMAN2 (541291) 69.0 kV to ANCONDA2 (541292) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT576 | Single Phase Fault with Stuck Breaker on POSTOAK2 69.000 (541300) 69 kV Bus a. Apply Fault at the POSTOAK2 69.000 (541300) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTOAK2 (541300) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. POSTOAK2 (541300) 69.0 kV to WBURGP 2 (541268) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT577 | Single Phase Fault with Stuck Breaker on CLNTPLT2 69.000 (541301) 69 kV Bus a. Apply Fault at the CLNTPLT2 69.000 (541301) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTPLT2 (541301) 69.0 kV to CLNTN S2 (541320) 69.0 kV Transmission Circuit #1 b.2. CLNTPLT2 (541301) 69.0 kV to POSTOAK2 (541300) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT578 | Single Phase Fault with Stuck Breaker on CLNTGRN2 69.000 (541302) 69 kV Bus a. Apply Fault at the CLNTGRN2 69.000 (541302) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTGRN2 (541302) 69.0 kV to CLNTN N2 (541303) 69.0 kV Transmission Circuit #1 b.2. CLNTGRN2 (541302) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT579 | Single Phase Fault with Stuck Breaker on BELTONS5 161.00 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 161.00 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 b.2. BELTONS5 (541340) 161.0 kV to TURNER_RD5 (541259) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT580 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to ARCHIE 5 (541207) 161.0 kV Transmission Circuit #1 b.2. S.HARP 5 (541341) 161.0 kV to PECULRS5 (541344) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT581 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT582 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT583 | Single Phase Fault with Stuck Breaker on MIDWAY_5 161.00 (541369) 161 kV Bus a. Apply Fault at the MIDWAY_5 161.00 (541369) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDWAY_5 (541369) 161.0 kV to AVENUECTY 5 (541394) 161.0 kV Transmission Circuit #1 b.2. MIDWAY_5 (541369) 161.0 kV to MARYVLE5 (541251) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT584 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT585 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT586 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT587 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT588 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 b.2. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT589 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT590 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT591 | Single Phase Fault with Stuck Breaker on PFLUMM 5 161.00 (542979) 161 kV Bus a. Apply Fault at the PFLUMM 5 161.00 (542979) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PFLUMM 5 (542979) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. PFLUMM 5 (542979) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT592 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT593 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-121 : PTDF of 0.09072 - GEN-2017-131 : PTDF of 0.05985 - GEN-2017-188 : PTDF of 0.03266 - GEN-2017-220 : PTDF of 0.06960 - GEN-2017-221 : PTDF of 0.06960 - GEN-2017-226 : PTDF of 0.08239 - GEN-2017-227 : PTDF of 0.08239 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT594 | Single Phase Fault with Stuck Breaker on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply Fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT595 | Single Phase Fault with Stuck Breaker on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply Fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHTOWN5 (542993) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 b.2. STHTOWN5 (542993) 161.0 kV to BENDIX 5 (542992) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT596 | Single Phase Fault with Stuck Breaker on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply Fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT597 | Single Phase Fault with Stuck Breaker on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT598 | Single Phase Fault with Stuck Breaker on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 b.2. GLADSTN5 (543016) 161.0 kV to GLADSTN_CAP5 (542946) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT599 | Single Phase Fault with Stuck Breaker on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply Fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 b.2. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT600 | Single Phase Fault with Stuck Breaker on BARRY 5 161.00 (543019) 161 kV Bus a. Apply Fault at the BARRY 5 161.00 (543019) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRY 5 (543019) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. BARRY 5 (543019) 161.0 kV to BARRY_CAP 5 (542944) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT601 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.2. NASHUA-5 (543028) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT602 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT603 | Single Phase Fault with Stuck Breaker on OLATHE 5 161.00 (543036) 161 kV Bus a. Apply Fault at the OLATHE 5 161.00 (543036) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OLATHE 5 (543036) 161.0 kV to SWITZER5 (543045) 161.0 kV Transmission Circuit #1 b.2. OLATHE 5 (543036) 161.0 kV to COLLEGE5 (543048) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT604 | Single Phase Fault with Stuck Breaker on QUARRY 5 161.00 (543037) 161 kV Bus a. Apply Fault at the QUARRY 5 161.00 (543037) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUARRY 5 (543037) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 b.2. QUARRY 5 (543037) 161.0 kV to MURLEN 5 (543043) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT605 | Single Phase Fault with Stuck Breaker on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. LENEXA 5 (543038) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT606 | Single Phase Fault with Stuck Breaker on MOONLT 5 161.00 (543044) 161 kV Bus a. Apply Fault at the MOONLT 5 161.00 (543044) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLT 5 (543044) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. MOONLT 5 (543044) 161.0 kV to QUARRY 5 (543037) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT607 | Single Phase Fault with Stuck Breaker on OXFORD 5 161.00 (543046) 161 kV Bus a. Apply Fault at the OXFORD 5 161.00 (543046) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OXFORD 5 (543046) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 b.2. OXFORD 5 (543046) 161.0 kV to OLATHE 5 (543036) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT608 | Single Phase Fault with Stuck Breaker on SEOTTWA5 161.00 (543055) 161 kV Bus a. Apply Fault at the SEOTTWA5 161.00 (543055) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SEOTTWA5 (543055) 161.0 kV to PLSTVAL5 (543077) 161.0 kV Transmission Circuit #1 b.2. SEOTTWA5 (543055) 161.0 kV to S.OTTWA5 (543066) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT609 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT610 | Single Phase Fault with Stuck Breaker on CENTENL5 161.00 (543067) 161 kV Bus a. Apply Fault at the CENTENL5 161.00 (543067) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTENL5 (543067) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 b.2. CENTENL5 (543067) 161.0 kV to PAOLA 5 (543069) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT611 | Single Phase Fault with Stuck Breaker on ASB349 5 161.00 (547476) 161 kV Bus a. Apply Fault at the ASB349 5 161.00 (547476) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASB349 5 (547476) 161.0 kV to PUR421 5 (547491) 161.0 kV Transmission Circuit #1 b.2. ASB349 5 (547476) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT612 | Single Phase Fault with Stuck Breaker on JOP 59 2 69.000 (547525) 69 kV Bus a. Apply Fault at the JOP 59 2 69.000 (547525) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JOP 59 2 (547525) 69.0 kV to GAT258 2 (547551) 69.0 kV Transmission Circuit #1 b.2. JOP 59 2 (547525) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT613 | Single Phase Fault with Stuck Breaker on COL 94 2 69.000 (547530) 69 kV Bus a. Apply Fault at the COL 94 2 69.000 (547530) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL 94 2 (547530) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. COL 94 2 (547530) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT614 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT615 | Single Phase Fault with Stuck Breaker on G14-001-TAP 345.00 (562476) 345 kV Bus a. Apply Fault at the G14-001-TAP 345.00 (562476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G14-001-TAP (562476) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. G14-001-TAP (562476) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT616 | Single Phase Fault with Stuck Breaker on GEN-2016-111345.00 (587880) 345 kV Bus a. Apply Fault at the GEN-2016-111345.00 (587880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-111 (587880) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-111 (587880) 345.0 kV to G16-111XFMR1 (587881) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT617 | Single Phase Fault with Stuck Breaker on GEN-2017-004345.00 (588490) 345 kV Bus a. Apply Fault at the GEN-2017-004345.00 (588490) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-004 (588490) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-004 (588490) 345.0 kV to G17-004XFMR1 (588491) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT618 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT619 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT620 | Single Phase Fault with Stuck Breaker on GEN-2017-202161.00 (761418) 161 kV Bus a. Apply Fault at the GEN-2017-202161.00 (761418) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-202 (761418) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #1 b.2. GEN-2017-202 (761418) 161.0 kV to G17-202-TAP (761422) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT621 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2GIBSON (301291) 69.0 kV to 5GIBSON (300083) 161.0 kV Two Winding #1 b.2. 2GIBSON (301291) 69.0 kV to 2CAMBEL (301196) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT622 | Single Phase Fault with Stuck Breaker on 5HOLDENB2 161.00 (300124) 161 kV Bus a. Apply Fault at the 5HOLDENB2 161.00 (300124) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HOLDEN (300336) 69.0 kV to 5HOLDENB2 (300124) 161.0 kV Two Winding #1 b.2. 2HOLDEN (300336) 69.0 kV to 2CENTRV (300323) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT623 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT624 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 b.2. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT625 | Single Phase Fault with Stuck Breaker on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply Fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #1 b.2. 2ASHRVL (301194) 69.0 kV to ASHRVL5 (505441) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT626 | Single Phase Fault with Stuck Breaker on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply Fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NEWMADXF12 (301531) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #z1 b.2. 5NEWMADXF12 (301531) 161.0 kV to 7NEWMADXF12 (301530) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT627 | Single Phase Fault with Stuck Breaker on 7KELSO 1 345.00 (344848) 345 kV Bus a. Apply Fault at the 7KELSO 1 345.00 (344848) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7KELSO 1 (344848) 345.0 kV to 7MASS (348294) 345.0 kV Transmission Circuit #1 b.2. 7KELSO 1 (344848) 345.0 kV to 7KELSO 2 (344849) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT628 | Single Phase Fault with Stuck Breaker on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV to PRG X1 1 (505411) 13.8 kV Three Winding #1 b.2. PARAGLD2 (505414) 69.0 kV to PARAGLD5 (505412) 161.0 kV to PRG X2 1 (505413) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT629 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to DELWARE4 (510379) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to SCOFCTY4 (510378) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT630 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILL6 (532857) 230.0 kV to SWISVAL6 (532856) 230.0 kV Transmission Circuit #1 b.2. TECHILL6 (532857) 230.0 kV to TECHILE3 (533182) 115.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT631 | Single Phase Fault with Stuck Breaker on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply Fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT6 (532861) 230.0 kV to JEC 6 (532852) 230.0 kV Transmission Circuit #1 b.2. EMANHAT6 (532861) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT632 | Single Phase Fault with Stuck Breaker on TECHILL5 161.00 (532920) 161 kV Bus a. Apply Fault at the TECHILL5 161.00 (532920) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILL5 (532920) 161.0 kV to KELLY 5 (532913) 161.0 kV Transmission Circuit #1 b.2. TECHILL5 (532920) 161.0 kV to TECHILW3 (533181) 115.0 kV to TECHIL4X (533885) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT633 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK4 (532997) 138.0 kV to OTTRCRK3 (533315) 115.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 b.2. OTTRCRK4 (532997) 138.0 kV to BUTLER 4 (532987) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT634 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUND 4 (533013) 138.0 kV to MOUND 2 (533742) 69.0 kV to MOUND1X1 (533095) 13.2 kV Three Winding #1 b.2. MOUND 4 (533013) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT635 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to CRESWLN4 (532981) 138.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 b.2. CRESWLN2 (533543) 69.0 kV to OAK 2 (533547) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT636 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to TIMBJCT4 (532992) 138.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 b.2. TIMBJCT2 (533558) 69.0 kV to WINFLD 2 (533561) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT637 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN2 (533876) 69.0 kV to FRANKLIN5 (532938) 161.0 kV to FRANKLIN1 (533122) 12.5 kV Three Winding #1 b.2. FRANKLIN2 (533876) 69.0 kV to SHEFFLD2 (533774) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT638 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTN N2 (541303) 69.0 kV to CLNTGRN2 (541302) 69.0 kV Transmission Circuit #1 b.2. CLNTN N2 (541303) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT639 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLNTN S2 (541320) 69.0 kV to CLINTON5 (541242) 161.0 kV Two Winding #2 b.2. CLNTN S2 (541320) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT640 | Single Phase Fault with Stuck Breaker on S.HARP 5 161.00 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 161.00 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 2 (541343) 69.0 kV to S.HARP 5 (541341) 161.0 kV Two Winding #1 b.2. S.HARP 2 (541343) 69.0 kV to FREEMAN2 (541291) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT641 | Single Phase Fault with Stuck Breaker on EDMOND5 161.00 (541355) 161 kV Bus a. Apply Fault at the EDMOND5 161.00 (541355) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDMOND5 (541355) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. EDMOND5 (541355) 161.0 kV to LAKE RD5 (541255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT642 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT643 | Single Phase Fault with Stuck Breaker on WINDSR 5 161.00 (541217) 161 kV Bus a. Apply Fault at the WINDSR 5 161.00 (541217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDSR 5 (541217) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. WINDSR 5 (541217) 161.0 kV to 5SEDALA (300117) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT644 | Single Phase Fault with Stuck Breaker on CLINTON5 161.00 (541242) 161 kV Bus a. Apply Fault at the CLINTON5 161.00 (541242) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLINTON5 (541242) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #z1 b.2. CLINTON5 (541242) 161.0 kV to CLNTN N2 (541303) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT645 | Single Phase Fault with Stuck Breaker on G17-108-TAP 161.00 (761278) 161 kV Bus a. Apply Fault at the G17-108-TAP 161.00 (761278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-108-TAP (761278) 161.0 kV to 5CLINTN (300071) 161.0 kV Transmission Circuit #1 b.2. G17-108-TAP (761278) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT646 | Single Phase Fault with Stuck Breaker on 5NODWAY 161.00 (300104) 161 kV Bus a. Apply Fault at the 5NODWAY 161.00 (300104) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5NODWAY (300104) 161.0 kV to 5GENTRY (300073) 161.0 kV Transmission Circuit #1 b.2. 5NODWAY (300104) 161.0 kV to 5MARYVLB1 (301592) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT647 | Single Phase Fault with Stuck Breaker on 5WINSLOW 161.00 (301347) 161 kV Bus a. Apply Fault at the 5WINSLOW 161.00 (301347) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5WINSLOW (301347) 161.0 kV to 1WINSLOW (301356) 34.5 kV Two Winding #1 b.2. 5WINSLOW (301347) 161.0 kV to 1WINSLOW (301356) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT648 | Single Phase Fault with Stuck Breaker on 5FAIRPTB1 161.00 (301564) 161 kV Bus a. Apply Fault at the 5FAIRPTB1 161.00 (301564) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5FAIRPTB1 (301564) 161.0 kV to 5FAIRPTB2 (300076) 161.0 kV Transmission Circuit #z1 b.2. 5FAIRPTB1 (301564) 161.0 kV to 5OSBORN (300107) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT649 | Single Phase Fault with Stuck Breaker on 5COLLINS 161.00 (300816) 161 kV Bus a. Apply Fault at the 5COLLINS 161.00 (300816) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5COLLINS (300816) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 b.2. 5COLLINS (300816) 161.0 kV to STOCKTN5 (505498) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT650 | Single Phase Fault with Stuck Breaker on 5OSCEOL 161.00 (301040) 161 kV Bus a. Apply Fault at the 5OSCEOL 161.00 (301040) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5OSCEOL (301040) 161.0 kV to 5OSCEOLTP (300108) 161.0 kV Transmission Circuit #1 b.2. 5OSCEOL (301040) 161.0 kV to 2OSCEOL (300811) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT651 | Single Phase Fault with Stuck Breaker on 5HOLDENB1 161.00 (301561) 161 kV Bus a. Apply Fault at the 5HOLDENB1 161.00 (301561) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5HOLDENB1 (301561) 161.0 kV to 5HOLDENB2 (300124) 161.0 kV Transmission Circuit #z1 b.2. 5HOLDENB1 (301561) 161.0 kV to 5PITTSV (300110) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT652 | Single Phase Fault with Stuck Breaker on 2BAELLS 69.000 (301286) 69 kV Bus a. Apply Fault at the 2BAELLS 69.000 (301286) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BAELLS (301286) 69.0 kV to 2STJUDEW (300170) 69.0 kV Transmission Circuit #1 b.2. 2BAELLS (301286) 69.0 kV to 2AVONKN (301285) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT653 | Single Phase Fault with Stuck Breaker on 2KINGCT 69.000 (300257) 69 kV Bus a. Apply Fault at the 2KINGCT 69.000 (300257) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2KINGCT (300257) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2KINGCT (300257) 69.0 kV to 2FLGGSP (300251) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT654 | Single Phase Fault with Stuck Breaker on 2MAYSVL 69.000 (300259) 69 kV Bus a. Apply Fault at the 2MAYSVL 69.000 (300259) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MAYSVL (300259) 69.0 kV to 2FAIRPT (300249) 69.0 kV Transmission Circuit #1 b.2. 2MAYSVL (300259) 69.0 kV to 2STEWRV (300268) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT655 | Single Phase Fault with Stuck Breaker on 2SYLVAN 69.000 (300545) 69 kV Bus a. Apply Fault at the 2SYLVAN 69.000 (300545) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2SYLVAN (300545) 69.0 kV to 2SEDALI (300541) 69.0 kV Transmission Circuit #1 b.2. 2SYLVAN (300545) 69.0 kV to 2SMTHTN (300542) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT656 | Single Phase Fault with Stuck Breaker on 2PIPER 69.000 (300706) 69 kV Bus a. Apply Fault at the 2PIPER 69.000 (300706) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2PIPER (300706) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2PIPER (300706) 69.0 kV to 2BUTLERE (300690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT657 | Single Phase Fault with Stuck Breaker on 2LEETON 69.000 (300703) 69 kV Bus a. Apply Fault at the 2LEETON 69.000 (300703) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LEETON (300703) 69.0 kV to 2CREIGH (300696) 69.0 kV Transmission Circuit #1 b.2. 2LEETON (300703) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT658 | Single Phase Fault with Stuck Breaker on 2CLINTNLD 69.000 (301626) 69 kV Bus a. Apply Fault at the 2CLINTNLD 69.000 (301626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CLINTNLD (301626) 69.0 kV to 2CLINTN (300692) 69.0 kV Transmission Circuit #1 b.2. 2CLINTNLD (301626) 69.0 kV to 2LADUE (300702) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT659 | Single Phase Fault with Stuck Breaker on 2MTZION 69.000 (300810) 69 kV Bus a. Apply Fault at the 2MTZION 69.000 (300810) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2MTZION (300810) 69.0 kV to 2GAINES (300701) 69.0 kV Transmission Circuit #1 b.2. 2MTZION (300810) 69.0 kV to 2DAMSCUS (300804) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT660 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT661 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT662 | Single Phase Fault with Stuck Breaker on GI94_POI 345.00 (709400) 345 kV Bus a. Apply Fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 b.2. GI94_POI (709400) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT663 | Single Phase Fault with Stuck Breaker on 2ARDEOLA 69.000 (301257) 69 kV Bus a. Apply Fault at the 2ARDEOLA 69.000 (301257) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ARDEOLA (301257) 69.0 kV to 2IDALIA (301243) 69.0 kV Transmission Circuit #1 b.2. 2ARDEOLA (301257) 69.0 kV to 2ADVANC (301235) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT664 | Single Phase Fault with Stuck Breaker on 2DOGWOD 69.000 (301239) 69 kV Bus a. Apply Fault at the 2DOGWOD 69.000 (301239) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2DOGWOD (301239) 69.0 kV to 2MATHWS (301247) 69.0 kV Transmission Circuit #1 b.2. 2DOGWOD (301239) 69.0 kV to 2ANNSTN (301236) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT665 | Single Phase Fault with Stuck Breaker on 2LILBRN 69.000 (301246) 69 kV Bus a. Apply Fault at the 2LILBRN 69.000 (301246) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2LILBRN (301246) 69.0 kV to N MADRD2 (505402) 69.0 kV Transmission Circuit #1 b.2. 2LILBRN (301246) 69.0 kV to 2ANNSTN (301236) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT666 | Single Phase Fault with Stuck Breaker on 2VANDSR 69.000 (301251) 69 kV Bus a. Apply Fault at the 2VANDSR 69.000 (301251) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2VANDSR (301251) 69.0 kV to 2MORLEY (301255) 69.0 kV Transmission Circuit #1 b.2. 2VANDSR (301251) 69.0 kV to 2MOREJT (301249) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT667 | Single Phase Fault with Stuck Breaker on 5VIAD_TP 161.00 (345891) 161 kV Bus a. Apply Fault at the 5VIAD_TP 161.00 (345891) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5VIAD_TP (345891) 161.0 kV to 5VIADUCT 3 (345892) 161.0 kV Transmission Circuit #1 b.2. 5VIAD_TP (345891) 161.0 kV to 5CAPE GIR3 (344286) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT668 | Single Phase Fault with Stuck Breaker on 5POLK TP 161.00 (361596) 161 kV Bus a. Apply Fault at the 5POLK TP 161.00 (361596) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5POLK TP (361596) 161.0 kV to 5TIPTONVL TN (361261) 161.0 kV Transmission Circuit #1 b.2. 5POLK TP (361596) 161.0 kV to 5TROY TN (361422) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT669 | Single Phase Fault with Stuck Breaker on EXPEDITION7 345.00 (532803) 345 kV Bus a. Apply Fault at the EXPEDITION7 345.00 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPEDITION7 (532803) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. EXPEDITION7 (532803) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT670 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT671 | Single Phase Fault with Stuck Breaker on G17-004-TAP 345.00 (588494) 345 kV Bus a. Apply Fault at the G17-004-TAP 345.00 (588494) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-004-TAP (588494) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. G17-004-TAP (588494) 345.0 kV to ELMCREEK7 (539805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT672 | Single Phase Fault with Stuck Breaker on GEN-2017-125345.00 (761901) 345 kV Bus a. Apply Fault at the GEN-2017-125345.00 (761901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-125 (761901) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-125 (761901) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT673 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G17-086XFMR (589241) 34.5 kV Two Winding #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT674 | Single Phase Fault with Stuck Breaker on G17-209-TAP 345.00 (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP 345.00 (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT675 | Single Phase Fault with Stuck Breaker on G15-052T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15-052T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15-052T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT676 | Single Phase Fault with Stuck Breaker on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply Fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACKMAN5 (543126) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. LACKMAN5 (543126) 161.0 kV to SPRGHL 5 (532914) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT677 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT678 | Single Phase Fault with Stuck Breaker on VAUGHN 3 115.00 (533308) 115 kV Bus a. Apply Fault at the VAUGHN 3 115.00 (533308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VAUGHN 3 (533308) 115.0 kV to WEMPORI3 (533309) 115.0 kV Transmission Circuit #1 b.2. VAUGHN 3 (533308) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT679 | Single Phase Fault with Stuck Breaker on OTTRCRK4 138.00 (532997) 138 kV Bus a. Apply Fault at the OTTRCRK4 138.00 (532997) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OTTRCRK3 (533315) 115.0 kV to EEUREKA3 (533302) 115.0 kV Transmission Circuit #2 b.2. OTTRCRK3 (533315) 115.0 kV to OTTRCRK4 (532997) 138.0 kV to OTTRX1 1 (533115) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT680 | Single Phase Fault with Stuck Breaker on SCHILNG3 115.00 (533377) 115 kV Bus a. Apply Fault at the SCHILNG3 115.00 (533377) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCHILNG3 (533377) 115.0 kV to MENTOR 3 (533374) 115.0 kV Transmission Circuit #1 b.2. SCHILNG3 (533377) 115.0 kV to CRAWFRD3 (533364) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT681 | Single Phase Fault with Stuck Breaker on CHANTAP2 69.000 (533666) 69 kV Bus a. Apply Fault at the CHANTAP2 69.000 (533666) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHANTAP2 (533666) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 b.2. CHANTAP2 (533666) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT682 | Single Phase Fault with Stuck Breaker on ASHGRJ22 69.000 (533660) 69 kV Bus a. Apply Fault at the ASHGRJ22 69.000 (533660) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASHGRJ22 (533660) 69.0 kV to TIOGA 2 (533646) 69.0 kV Transmission Circuit #1 b.2. ASHGRJ22 (533660) 69.0 kV to CGENSUB2 (533662) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT683 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT684 | Single Phase Fault with Stuck Breaker on SOPITT 2 69.000 (533773) 69 kV Bus a. Apply Fault at the SOPITT 2 69.000 (533773) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOPITT 2 (533773) 69.0 kV to BAKER 2 (532926) 69.0 kV Transmission Circuit #1 b.2. SOPITT 2 (533773) 69.0 kV to LITCH S2 (533766) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT685 | Single Phase Fault with Stuck Breaker on ELMCREK6 230.00 (539639) 230 kV Bus a. Apply Fault at the ELMCREK6 230.00 (539639) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELMCREK6 (539639) 230.0 kV to CONCRD6 (539658) 230.0 kV Transmission Circuit #1 b.2. ELMCREK6 (539639) 230.0 kV to NMANHT6 (532865) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT686 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 4 (539674) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT687 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT688 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT689 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT690 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT691 | Single Phase Fault with Stuck Breaker on LBRTYWT5 161.00 (541247) 161 kV Bus a. Apply Fault at the LBRTYWT5 161.00 (541247) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYWT5 (541247) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 b.2. LBRTYWT5 (541247) 161.0 kV to HLLMRK 5 (541215) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT692 | Single Phase Fault with Stuck Breaker on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply Fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCONGRS5 (541318) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 b.2. NCONGRS5 (541318) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT693 | Single Phase Fault with Stuck Breaker on WESTON 5 161.00 (541351) 161 kV Bus a. Apply Fault at the WESTON 5 161.00 (541351) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTON 5 (541351) 161.0 kV to IATAN5 (541350) 161.0 kV Transmission Circuit #1 b.2. WESTON 5 (541351) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT694 | Single Phase Fault with Stuck Breaker on TIFFANY5 161.00 (543026) 161 kV Bus a. Apply Fault at the TIFFANY5 161.00 (543026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIFFANY5 (543026) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. TIFFANY5 (543026) 161.0 kV to WETHRBY5 (543017) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT695 | Single Phase Fault with Stuck Breaker on WOODBIN5 161.00 (541258) 161 kV Bus a. Apply Fault at the WOODBIN5 161.00 (541258) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODBIN5 (541258) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. WOODBIN5 (541258) 161.0 kV to EAST 5 (541254) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT696 | Single Phase Fault with Stuck Breaker on AVENUECTY 5 161.00 (541394) 161 kV Bus a. Apply Fault at the AVENUECTY 5 161.00 (541394) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVENUECTY 5 (541394) 161.0 kV to ST JOE 5 (541253) 161.0 kV Transmission Circuit #1 b.2. AVENUECTY 5 (541394) 161.0 kV to MIDWAY_5 (541369) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT697 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT698 | Single Phase Fault with Stuck Breaker on STALEY 2 69.000 (541261) 69 kV Bus a. Apply Fault at the STALEY 2 69.000 (541261) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STALEY 2 (541261) 69.0 kV to RNRDGE 2 (541260) 69.0 kV Transmission Circuit #1 b.2. STALEY 2 (541261) 69.0 kV to LIBERTY2 (541262) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT699 | Single Phase Fault with Stuck Breaker on URICHTP2 69.000 (541304) 69 kV Bus a. Apply Fault at the URICHTP2 69.000 (541304) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. URICHTP2 (541304) 69.0 kV to CLNTPLT2 (541301) 69.0 kV Transmission Circuit #1 b.2. URICHTP2 (541304) 69.0 kV to APCITY 2 (541306) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT700 | Single Phase Fault with Stuck Breaker on PECULRS5 161.00 (541344) 161 kV Bus a. Apply Fault at the PECULRS5 161.00 (541344) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULRS5 (541344) 161.0 kV to PECULR 5 (541342) 161.0 kV Transmission Circuit #1 b.2. PECULRS5 (541344) 161.0 kV to S.HARP 5 (541341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT701 | Single Phase Fault with Stuck Breaker on CEDRCRK5 161.00 (543049) 161 kV Bus a. Apply Fault at the CEDRCRK5 161.00 (543049) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDRCRK5 (543049) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. CEDRCRK5 (543049) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT702 | Single Phase Fault with Stuck Breaker on PLSTVAL5 161.00 (543077) 161 kV Bus a. Apply Fault at the PLSTVAL5 161.00 (543077) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSTVAL5 (543077) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. PLSTVAL5 (543077) 161.0 kV to SEOTTWA5 (543055) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT703 | Single Phase Fault with Stuck Breaker on BNSF 5 161.00 (543132) 161 kV Bus a. Apply Fault at the BNSF 5 161.00 (543132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BNSF 5 (543132) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. BNSF 5 (543132) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT704 | Single Phase Fault with Stuck Breaker on HICKMAN5 161.00 (542994) 161 kV Bus a. Apply Fault at the HICKMAN5 161.00 (542994) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HICKMAN5 (542994) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. HICKMAN5 (542994) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT705 | Single Phase Fault with Stuck Breaker on ANTIOCH5 161.00 (543050) 161 kV Bus a. Apply Fault at the ANTIOCH5 161.00 (543050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. ANTIOCH5 (543050) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT706 | Single Phase Fault with Stuck Breaker on REDEL 5 161.00 (543053) 161 kV Bus a. Apply Fault at the REDEL 5 161.00 (543053) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDEL 5 (543053) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. REDEL 5 (543053) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT707 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT708 | Single Phase Fault with Stuck Breaker on COLLEGE5 161.00 (543048) 161 kV Bus a. Apply Fault at the COLLEGE5 161.00 (543048) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLLEGE5 (543048) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. COLLEGE5 (543048) 161.0 kV to OLATHE 5 (543036) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT709 | Single Phase Fault with Stuck Breaker on OVERLPK5 161.00 (543047) 161 kV Bus a. Apply Fault at the OVERLPK5 161.00 (543047) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OVERLPK5 (543047) 161.0 kV to PFLUMM 5 (542979) 161.0 kV Transmission Circuit #1 b.2. OVERLPK5 (543047) 161.0 kV to BRKRIDG5 (543033) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT710 | Single Phase Fault with Stuck Breaker on FOREST 5 161.00 (543001) 161 kV Bus a. Apply Fault at the FOREST 5 161.00 (543001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOREST 5 (543001) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. FOREST 5 (543001) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT711 | Single Phase Fault with Stuck Breaker on BUNKRDG5 161.00 (543008) 161 kV Bus a. Apply Fault at the BUNKRDG5 161.00 (543008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUNKRDG5 (543008) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. BUNKRDG5 (543008) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT712 | Single Phase Fault with Stuck Breaker on WINJT S5 161.00 (543010) 161 kV Bus a. Apply Fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT S5 (543010) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT S5 (543010) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT713 | Single Phase Fault with Stuck Breaker on SHOLCRK5 161.00 (543029) 161 kV Bus a. Apply Fault at the SHOLCRK5 161.00 (543029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHOLCRK5 (543029) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. SHOLCRK5 (543029) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT714 | Single Phase Fault with Stuck Breaker on LINECRK5 161.00 (543025) 161 kV Bus a. Apply Fault at the LINECRK5 161.00 (543025) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINECRK5 (543025) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 b.2. LINECRK5 (543025) 161.0 kV to RIVRSID5 (543021) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT715 | Single Phase Fault with Stuck Breaker on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply Fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MERRIAM5 (543032) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. MERRIAM5 (543032) 161.0 kV to MERRIAM_CAP5 (542947) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT716 | Single Phase Fault with Stuck Breaker on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply Fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT717 | Single Phase Fault with Stuck Breaker on REEDER 5 161.00 (543052) 161 kV Bus a. Apply Fault at the REEDER 5 161.00 (543052) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REEDER 5 (543052) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 b.2. REEDER 5 (543052) 161.0 kV to KNLWRTH5 (543034) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT718 | Single Phase Fault with Stuck Breaker on S.OTTWA5 161.00 (543066) 161 kV Bus a. Apply Fault at the S.OTTWA5 161.00 (543066) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.OTTWA5 (543066) 161.0 kV to SEOTTWA5 (543055) 161.0 kV Transmission Circuit #1 b.2. S.OTTWA5 (543066) 161.0 kV to S.OTTWA21 (543121) 34.5 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT719 | Single Phase Fault with Stuck Breaker on WAGSTAF5 161.00 (543068) 161 kV Bus a. Apply Fault at the WAGSTAF5 161.00 (543068) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGSTAF5 (543068) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. WAGSTAF5 (543068) 161.0 kV to CENTENL5 (543067) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT720 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STL439 5 (547498) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. STL439 5 (547498) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT721 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT722 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT723 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to G14-001XFMR1 (583851) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT724 | Single Phase Fault with Stuck Breaker on G17-022-TAP 138.00 (588664) 138 kV Bus a. Apply Fault at the G17-022-TAP 138.00 (588664) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-022-TAP (588664) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. G17-022-TAP (588664) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT725 | Single Phase Fault with Stuck Breaker on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply Fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. WESTBORO 3 (635018) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT726 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER_ESST8 (640141) 69.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT727 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT728 | Single Phase Fault with Stuck Breaker on G17-120-TAP 115.00 (760007) 115 kV Bus a. Apply Fault at the G17-120-TAP 115.00 (760007) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-120-TAP (760007) 115.0 kV to NORTHVW3 (533371) 115.0 kV Transmission Circuit #1 b.2. G17-120-TAP (760007) 115.0 kV to AEC 3 (533361) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT729 | Single Phase Fault with Stuck Breaker on G17-202-TAP 161.00 (761422) 161 kV Bus a. Apply Fault at the G17-202-TAP 161.00 (761422) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-202-TAP (761422) 161.0 kV to N MADRD5 (505400) 161.0 kV Transmission Circuit #1 b.2. G17-202-TAP (761422) 161.0 kV to GEN-2017-202 (761418) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT730 | Single Phase Fault with Stuck Breaker on 5GIBSON 161.00 (300083) 161 kV Bus a. Apply Fault at the 5GIBSON 161.00 (300083) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5GIBSON (300083) 161.0 kV to 5NEWMAD (300103) 161.0 kV Transmission Circuit #1 b.2. 5GIBSON (300083) 161.0 kV to 2GIBSON (301291) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT731 | Single Phase Fault with Stuck Breaker on ASHRVL5 161.00 (505441) 161 kV Bus a. Apply Fault at the ASHRVL5 161.00 (505441) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ASHRVL5 (505441) 161.0 kV to IDALIA 5 (505434) 161.0 kV Transmission Circuit #1 b.2. ASHRVL5 (505441) 161.0 kV to POP BLF5 (505438) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT732 | Single Phase Fault with Stuck Breaker on 7NEWMADXF12 345.00 (301530) 345 kV Bus a. Apply Fault at the 7NEWMADXF12 345.00 (301530) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7NEWMADXF12 (301530) 345.0 kV to 7NEWMAD (300046) 345.0 kV Transmission Circuit #z1 b.2. 7NEWMADXF12 (301530) 345.0 kV to 5NEWMADXF12 (301531) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT733 | Single Phase Fault with Stuck Breaker on PARAGLD5 161.00 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 161.00 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD5 (505412) 161.0 kV to KENNETT5 (505410) 161.0 kV Transmission Circuit #1 b.2. PARAGLD5 (505412) 161.0 kV to CENTR H5 (505416) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT734 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT735 | Single Phase Fault with Stuck Breaker on MIDLAND6 230.00 (532855) 230 kV Bus a. Apply Fault at the MIDLAND6 230.00 (532855) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDLADN3 (533252) 115.0 kV to MIDLAND6 (532855) 230.0 kV to MIDLAND1 (532884) 18.0 kV Three Winding #1 b.2. MIDLADN3 (533252) 115.0 kV to MIDLADS3 (533260) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT736 | Single Phase Fault with Stuck Breaker on TECHILL6 230.00 (532857) 230 kV Bus a. Apply Fault at the TECHILL6 230.00 (532857) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILE3 (533182) 115.0 kV to TECHILL6 (532857) 230.0 kV to TECHILL1 (532886) 13.8 kV Three Winding #1 b.2. TECHILE3 (533182) 115.0 kV to 27CROCO3 (533187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT737 | Single Phase Fault with Stuck Breaker on EMANHAT6 230.00 (532861) 230 kV Bus a. Apply Fault at the EMANHAT6 230.00 (532861) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMANHAT3 (533326) 115.0 kV to EMANHAT6 (532861) 230.0 kV to EMANHAT1 (532888) 18.0 kV Three Winding #1 b.2. EMANHAT3 (533326) 115.0 kV to LEVEE 3 (533327) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT738 | Single Phase Fault with Stuck Breaker on SPRGHL 5 161.00 (532914) 161 kV Bus a. Apply Fault at the SPRGHL 5 161.00 (532914) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPRINGH3 (533267) 115.0 kV to SPRGHL 5 (532914) 161.0 kV to SPRINGH1 (532948) 12.5 kV Three Winding #1 b.2. SPRINGH3 (533267) 115.0 kV to BONITA 3 (533262) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT739 | Single Phase Fault with Stuck Breaker on TECHILW3 115.00 (533181) 115 kV Bus a. Apply Fault at the TECHILW3 115.00 (533181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to 6 GOLDN3 (533177) 115.0 kV Transmission Circuit #1 b.2. TECHILW3 (533181) 115.0 kV to TECHILE3 (533182) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT740 | Single Phase Fault with Stuck Breaker on CRESWLN4 138.00 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 138.00 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to CRESWLS2 (533573) 69.0 kV to CRESW2 1 (533081) 13.2 kV Three Winding #1 b.2. CRESWLN4 (532981) 138.0 kV to CRESWLN2 (533543) 69.0 kV to CRESW1 1 (533080) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT741 | Single Phase Fault with Stuck Breaker on TIMBJCT4 138.00 (532992) 138 kV Bus a. Apply Fault at the TIMBJCT4 138.00 (532992) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT4 (532992) 138.0 kV to SUMNER 4 (532984) 138.0 kV Transmission Circuit #1 b.2. TIMBJCT4 (532992) 138.0 kV to TIMBJCT2 (533558) 69.0 kV to TIMBJCT1 (533120) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT742 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT743 | Single Phase Fault with Stuck Breaker on FRANKLIN5 161.00 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 161.00 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 b.2. FRANKLIN5 (532938) 161.0 kV to LITCH 5 (532932) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT744 | Single Phase Fault with Stuck Breaker on 5CLINTN (300071) 161 kV Bus a. Apply Fault at the 5CLINTN (300071) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CLINTN (300071) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT745 | Single Phase Fault with Stuck Breaker on 5SEDALA (300117) 161 kV Bus a. Apply Fault at the 5SEDALA (300117) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SEDALA (300117) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT746 | Single Phase Fault with Stuck Breaker on 2HOLDEN (300336) 69 kV Bus a. Apply Fault at the 2HOLDEN (300336) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2HOLDEN (300336) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT747 | Single Phase Fault with Stuck Breaker on 2CENTRV (300323) 69 kV Bus a. Apply Fault at the 2CENTRV (300323) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2CENTRV (300323) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT748 | Single Phase Fault with Stuck Breaker on STILWEL5 (542969) 161 kV Bus a. Apply Fault at the STILWEL5 (542969) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT749 | Single Phase Fault with Stuck Breaker on STHTOWN5 (542993) 161 kV Bus a. Apply Fault at the STHTOWN5 (542993) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHTOWN5 (542993) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT750 | Single Phase Fault with Stuck Breaker on S.HARP 5 (541341) 161 kV Bus a. Apply Fault at the S.HARP 5 (541341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S.HARP 5 (541341) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT751 | Single Phase Fault with Stuck Breaker on W.GRDNR7 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT752 | Single Phase Fault with Stuck Breaker on PECULR 7 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT753 | Single Phase Fault with Stuck Breaker on PECULR 5 (541342) 161 kV Bus a. Apply Fault at the PECULR 5 (541342) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT754 | Single Phase Fault with Stuck Breaker on BELTONS5 (541340) 161 kV Bus a. Apply Fault at the BELTONS5 (541340) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELTONS5 (541340) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT755 | Single Phase Fault with Stuck Breaker on STILWEL7 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT756 | Single Phase Fault with Stuck Breaker on HOLT 7 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT757 | Single Phase Fault with Stuck Breaker on SIBLEY 7 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT758 | Single Phase Fault with Stuck Breaker on S3454 3 (645454) 345 kV Bus a. Apply Fault at the S3454 3 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT759 | Single Phase Fault with Stuck Breaker on NMANHT3 (533347) 115 kV Bus a. Apply Fault at the NMANHT3 (533347) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NMANHT3 (533347) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT760 | Single Phase Fault with Stuck Breaker on SUMMIT 7 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT761 | Single Phase Fault with Stuck Breaker on RENO 7 (532771) 345 kV Bus a. Apply Fault at the RENO 7 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT762 | Single Phase Fault with Stuck Breaker on GEARY 3 (533336) 115 kV Bus a. Apply Fault at the GEARY 3 (533336) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 3 (533336) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT763 | Single Phase Fault with Stuck Breaker on MCDOWEL3 (533335) 115 kV Bus a. Apply Fault at the MCDOWEL3 (533335) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCDOWEL3 (533335) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT764 | Single Phase Fault with Stuck Breaker on GEARY 7 (532767) 345 kV Bus a. Apply Fault at the GEARY 7 (532767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEARY 7 (532767) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT765 | Single Phase Fault with Stuck Breaker on SUMMIT 6 (532873) 230 kV Bus a. Apply Fault at the SUMMIT 6 (532873) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 6 (532873) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT766 | Single Phase Fault with Stuck Breaker on EMCPHER6 (532872) 230 kV Bus a. Apply Fault at the EMCPHER6 (532872) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMCPHER6 (532872) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT767 | Single Phase Fault with Stuck Breaker on SMOKYHL6 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT768 | Single Phase Fault with Stuck Breaker on UNIONRG6 (532874) 230 kV Bus a. Apply Fault at the UNIONRG6 (532874) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNIONRG6 (532874) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT769 | Single Phase Fault with Stuck Breaker on SUMMIT 3 (533381) 115 kV Bus a. Apply Fault at the SUMMIT 3 (533381) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 3 (533381) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT770 | Single Phase Fault with Stuck Breaker on MENTOR 3 (533374) 115 kV Bus a. Apply Fault at the MENTOR 3 (533374) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MENTOR 3 (533374) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT771 | Single Phase Fault with Stuck Breaker on NORTHVW3 (533371) 115 kV Bus a. Apply Fault at the NORTHVW3 (533371) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORTHVW3 (533371) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT772 | Single Phase Fault with Stuck Breaker on CRESWLN4 (532981) 138 kV Bus a. Apply Fault at the CRESWLN4 (532981) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN4 (532981) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT773 | Single Phase Fault with Stuck Breaker on TIMBJCT2 (533558) 69 kV Bus a. Apply Fault at the TIMBJCT2 (533558) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIMBJCT2 (533558) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT774 | Single Phase Fault with Stuck Breaker on CRESWLN2 (533543) 69 kV Bus a. Apply Fault at the CRESWLN2 (533543) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRESWLN2 (533543) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT775 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT776 | Single Phase Fault with Stuck Breaker on GILL 4 (533047) 138 kV Bus a. Apply Fault at the GILL 4 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT777 | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT778 | Single Phase Fault with Stuck Breaker on WICHITA7 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT779 | Single Phase Fault with Stuck Breaker on BENTON 7 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT780 | Single Phase Fault with Stuck Breaker on EVANS N4 (533040) 138 kV Bus a. Apply Fault at the EVANS N4 (533040) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT781 | Single Phase Fault with Stuck Breaker on RENFROW7 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT782 | Single Phase Fault with Stuck Breaker on RENFROW4 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT783 | Single Phase Fault with Stuck Breaker on WGARDNR5 (542966) 161 kV Bus a. Apply Fault at the WGARDNR5 (542966) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT784 | Single Phase Fault with Stuck Breaker on CEDRCRK5 (543049) 161 kV Bus a. Apply Fault at the CEDRCRK5 (543049) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CEDRCRK5 (543049) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT785 | Single Phase Fault with Stuck Breaker on CRAIG 7 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT786 | Single Phase Fault with Stuck Breaker on SWISVAL6 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT787 | Single Phase Fault with Stuck Breaker on EMPEC 7 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT788 | Single Phase Fault with Stuck Breaker on JEC N 7 (532766) 345 kV Bus a. Apply Fault at the JEC N 7 (532766) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JEC N 7 (532766) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT789 | Single Phase Fault with Stuck Breaker on MORRIS 6 (532863) 230 kV Bus a. Apply Fault at the MORRIS 6 (532863) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT790 | Single Phase Fault with Stuck Breaker on TECHILW3 (533181) 115 kV Bus a. Apply Fault at the TECHILW3 (533181) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TECHILW3 (533181) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT791 | Single Phase Fault with Stuck Breaker on LWRNCHL3 (533250) 115 kV Bus a. Apply Fault at the LWRNCHL3 (533250) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LWRNCHL3 (533250) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT792 | Single Phase Fault with Stuck Breaker on ALTOONA4 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT793 | Single Phase Fault with Stuck Breaker on TIOGA 2 (533646) 69 kV Bus a. Apply Fault at the TIOGA 2 (533646) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA 2 (533646) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT794 | Single Phase Fault with Stuck Breaker on ALTOO E2 (533673) 69 kV Bus a. Apply Fault at the ALTOO E2 (533673) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOO E2 (533673) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT795 | Single Phase Fault with Stuck Breaker on MONTGOM4 (533004) 138 kV Bus a. Apply Fault at the MONTGOM4 (533004) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONTGOM4 (533004) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT796 | Single Phase Fault with Stuck Breaker on NEOSHON4 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT797 | Single Phase Fault with Stuck Breaker on NEOSHO 4 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT798 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT799 | Single Phase Fault with Stuck Breaker on NEOSHOS2 (533778) 69 kV Bus a. Apply Fault at the NEOSHOS2 (533778) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT800 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT801 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT802 | Single Phase Fault with Stuck Breaker on DELWARE7 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT803 | Single Phase Fault with Stuck Breaker on NASHUA 7 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT804 | Single Phase Fault with Stuck Breaker on STRANGR7 (532772) 345 kV Bus a. Apply Fault at the STRANGR7 (532772) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR7 (532772) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT805 | Single Phase Fault with Stuck Breaker on STRANGR3 (533268) 115 kV Bus a. Apply Fault at the STRANGR3 (533268) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRANGR3 (533268) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT806 | Single Phase Fault with Stuck Breaker on SMTHVL 5 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT807 | Single Phase Fault with Stuck Breaker on NASHUA 5 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT808 | Single Phase Fault with Stuck Breaker on NASHUA-5 (543028) 161 kV Bus a. Apply Fault at the NASHUA-5 (543028) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT809 | Single Phase Fault with Stuck Breaker on RNRIDGE5 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT810 | Single Phase Fault with Stuck Breaker on HAWTHS5 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT811 | Single Phase Fault with Stuck Breaker on HAWTH 7 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT812 | Single Phase Fault with Stuck Breaker on EASTOWN7 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT813 | Single Phase Fault with Stuck Breaker on EASTOWN5 (541401) 161 kV Bus a. Apply Fault at the EASTOWN5 (541401) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT814 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT815 | Single Phase Fault with Stuck Breaker on ATCHSN 3 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT816 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT817 | Single Phase Fault with Stuck Breaker on MONOLITH 3 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT818 | Single Phase Fault with Stuck Breaker on ST JOE 5 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT819 | Single Phase Fault with Stuck Breaker on MIDWAY_5 (541369) 161 kV Bus a. Apply Fault at the MIDWAY_5 (541369) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDWAY_5 (541369) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT820 | Single Phase Fault with Stuck Breaker on LITCH 5 (532932) 161 kV Bus a. Apply Fault at the LITCH 5 (532932) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LITCH 5 (532932) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT821 | Single Phase Fault with Stuck Breaker on ORO110 5 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT822 | Single Phase Fault with Stuck Breaker on ORO110 2 (547534) 69 kV Bus a. Apply Fault at the ORO110 2 (547534) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 2 (547534) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT823 | Single Phase Fault with Stuck Breaker on FRANKLIN5 (532938) 161 kV Bus a. Apply Fault at the FRANKLIN5 (532938) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN5 (532938) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT824 | Single Phase Fault with Stuck Breaker on FRANKLIN2 (533876) 69 kV Bus a. Apply Fault at the FRANKLIN2 (533876) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FRANKLIN2 (533876) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT825 | Single Phase Fault with Stuck Breaker on AUBURN 6 (532851) 230 kV Bus a. Apply Fault at the AUBURN 6 (532851) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AUBURN 6 (532851) 230.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT826 | Single Phase Fault with Stuck Breaker on PLSTVAL5 (543077) 161 kV Bus a. Apply Fault at the PLSTVAL5 (543077) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSTVAL5 (543077) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT827 | Single Phase Fault with Stuck Breaker on MOONLT 5 (543044) 161 kV Bus a. Apply Fault at the MOONLT 5 (543044) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOONLT 5 (543044) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT828 | Single Phase Fault with Stuck Breaker on CRAIG 5 (542978) 161 kV Bus a. Apply Fault at the CRAIG 5 (542978) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT829 | Single Phase Fault with Stuck Breaker on 87TH 7 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT830 | Single Phase Fault with Stuck Breaker on 87TH 3 (533283) 115 kV Bus a. Apply Fault at the 87TH 3 (533283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 3 (533283) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT831 | Single Phase Fault with Stuck Breaker on SIKETAP5 (505427) 161 kV Bus a. Apply Fault at the SIKETAP5 (505427) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIKETAP5 (505427) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT832 | Single Phase Fault with Stuck Breaker on N MADRD2 (505402) 69 kV Bus a. Apply Fault at the N MADRD2 (505402) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD2 (505402) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT833 | Single Phase Fault with Stuck Breaker on N MADRD5 (505400) 161 kV Bus a. Apply Fault at the N MADRD5 (505400) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N MADRD5 (505400) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT834 | Single Phase Fault with Stuck Breaker on KENNETT5 (505410) 161 kV Bus a. Apply Fault at the KENNETT5 (505410) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENNETT5 (505410) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT835 | Single Phase Fault with Stuck Breaker on PARAGLD5 (505412) 161 kV Bus a. Apply Fault at the PARAGLD5 (505412) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARAGLD5 (505412) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT836 | Single Phase Fault with Stuck Breaker on 2BAELLS (301286) 69 kV Bus a. Apply Fault at the 2BAELLS (301286) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2BAELLS (301286) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT837 | Single Phase Fault with Stuck Breaker on 2ANNSTN (301236) 69 kV Bus a. Apply Fault at the 2ANNSTN (301236) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 2ANNSTN (301236) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT838 | Single Phase Fault with Stuck Breaker on RIV167 2 (547541) 69 kV Bus a. Apply Fault at the RIV167 2 (547541) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT839 | Single Phase Fault with Stuck Breaker on RIV4525 (547469) 161 kV Bus a. Apply Fault at the RIV4525 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT840 | Single Phase Fault with Stuck Breaker on MARMTNW5 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT841 | Single Phase Fault with Stuck Breaker on MARMATN2 (533639) 69 kV Bus a. Apply Fault at the MARMATN2 (533639) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT842 | Single Phase Fault with Stuck Breaker on NEOSHOS4 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 (533020) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT843 | Single Phase Fault with Stuck Breaker on SOPITT 2 (533773) 69 kV Bus a. Apply Fault at the SOPITT 2 (533773) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SOPITT 2 (533773) 69.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT844 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT845 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT846 | Single Phase Fault with Stuck Breaker on DGRASSE7 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT847 | Single Phase Fault with Stuck Breaker on DGRASSE4 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT848 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT849 | Single Phase Fault with Stuck Breaker on BUFFALO7 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT850 | Single Phase Fault with Stuck Breaker on EXPEDITION7 (532803) 345 kV Bus a. Apply Fault at the EXPEDITION7 (532803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EXPEDITION7 (532803) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT851 | Single Phase Fault with Stuck Breaker on BENTON 4 (532986) 138 kV Bus a. Apply Fault at the BENTON 4 (532986) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT852 | Single Phase Fault with Stuck Breaker on FLATRDG4 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT853 | Single Phase Fault with Stuck Breaker on CIRCLE 3 (533413) 115 kV Bus a. Apply Fault at the CIRCLE 3 (533413) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT854 | Single Phase Fault with Stuck Breaker on MOUNDRG3 (533429) 115 kV Bus a. Apply Fault at the MOUNDRG3 (533429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUNDRG3 (533429) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT855 | Single Phase Fault with Stuck Breaker on CHISHLM4 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_LOCAL_FAULT856 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT1 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT2 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT3 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT4 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT5 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT6 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT7 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT8 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT9 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT10 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT11 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WCGS U1 (532751) 25.0 kV to WOLFCRK7 (532797) 345.0 kV Two Winding #1 b.2. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT12 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to FRMRCTY B1 9 (635019) 34.5 kV Two Winding #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT13 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT14 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT15 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT16 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELAWAR1 (510370) 13.8 kV to DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT17 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT18 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT19 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT20 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT21 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT22 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT23 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER1 (531452) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT24 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-121 : PTDF of 0.09072 - GEN-2017-131 : PTDF of 0.05985 - GEN-2017-188 : PTDF of 0.03266 - GEN-2017-220 : PTDF of 0.06960 - GEN-2017-221 : PTDF of 0.06960 - GEN-2017-226 : PTDF of 0.08239 - GEN-2017-227 : PTDF of 0.08239 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT25 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT26 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT27 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT28 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. Present in the base case as well. The following CQ units were determined to be contingent on the upgrade: - GEN-2017-121 : PTDF of 0.09072 - GEN-2017-131 : PTDF of 0.05985 - GEN-2017-188 : PTDF of 0.03266 - GEN-2017-220 : PTDF of 0.06960 - GEN-2017-221 : PTDF of 0.06960 - GEN-2017-226 : PTDF of 0.08239 - GEN-2017-227 : PTDF of 0.08239 | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT29 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT30 | Single Phase Fault with Stuck Breaker on LATHAMS7 345.00 (532800) 345 kV Bus a. Apply Fault at the LATHAMS7 345.00 (532800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 b.3. LATHAMS7 (532800) 345.0 kV to ELKRVR17 (532801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT31 | Single Phase Fault with Stuck Breaker on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply Fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 b.2. WAVERLY7 (532799) 345.0 kV to WAVERTX7 (532802) 345.0 kV Transmission Circuit #1 b.3. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT32 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT33 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT34 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT35 | Single Phase Fault with Stuck Breaker on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply Fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT36 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGTER (531453) 13.8 kV to MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT37 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT38 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT39 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT40 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT41 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT42 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO3 (640325) 345.0 kV to REDWILO7 (640326) 115.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT43 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to AXTELL 7 (640066) 115.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT44 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT45 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT46 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT47 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT48 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 b.2. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT49 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT50 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT51 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT52 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE3 (640312) 345.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT53 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.5. COOPER 3 (640139) 345.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT54 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT55 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to DGRASSE4 (515853) 138.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT56 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT57 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT58 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to RENFROW4 (515544) 138.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT59 | Single Phase Fault with Stuck Breaker on 7HUBEN 345.00 (300042) 345 kV Bus a. Apply Fault at the 7HUBEN 345.00 (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to 5HUBEN (300088) 161.0 kV Two Winding #1 b.2. 7HUBEN (300042) 345.0 kV to 7FRANKSRCTP (300051) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT60 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 b.2. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT61 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT62 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT63 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT64 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT65 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT66 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT67 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT68 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT69 | Single Phase Fault with Stuck Breaker on 7MORGAN 345.00 (300045) 345 kV Bus a. Apply Fault at the 7MORGAN 345.00 (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to 7MORGAN (300045) 345.0 kV Two Winding #2 b.2. 5MORGANXF2 (301622) 161.0 kV to 5MORGAN (300101) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT70 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT71 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 b.2. REDWILO7 (640326) 115.0 kV to BEVERLY7 (640082) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT72 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT73 | Single Phase Fault with Stuck Breaker on G17-209-TAP 345.00 (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP 345.00 (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT74 | Single Phase Fault with Stuck Breaker on G15-052T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15-052T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15-052T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT75 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G17-086XFMR (589241) 34.5 kV Two Winding #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT76 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT77 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT78 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT79 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT80 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT81 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOL2X1 (532833) 13.8 kV Three Winding #2 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT82 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT83 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 b.2. ST JOE 5 (541253) 161.0 kV to ST JOE 7 (541199) 345.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT84 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT85 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. REDWILO3 (640325) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT86 | Single Phase Fault with Stuck Breaker on 7HUBEN (300042) 345 kV Bus a. Apply Fault at the 7HUBEN (300042) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7HUBEN (300042) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT87 | Single Phase Fault with Stuck Breaker on 7MORGAN (300045) 345 kV Bus a. Apply Fault at the 7MORGAN (300045) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT88 | Single Phase Fault with Stuck Breaker on BUFF_DUNES 7 (523118) 345 kV Bus a. Apply Fault at the BUFF_DUNES 7 (523118) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFF_DUNES 7 (523118) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT89 | Single Phase Fault with Stuck Breaker on FINNEY 7 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT90 | Single Phase Fault with Stuck Breaker on NEOSHO 7 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT91 | Single Phase Fault with Stuck Breaker on ROSEHIL7 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT92 | Single Phase Fault with Stuck Breaker on VIOLA 7 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT93 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT94 | Single Phase Fault with Stuck Breaker on THISTLE7 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT95 | Single Phase Fault with Stuck Breaker on ST JOE 7 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT96 | Single Phase Fault with Stuck Breaker on G16-050-TAP (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT97 | Single Phase Fault with Stuck Breaker on 5MORGANXF2 (301622) 161 kV Bus a. Apply Fault at the 5MORGANXF2 (301622) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5MORGANXF2 (301622) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT98 | Single Phase Fault with Stuck Breaker on COOPER 5 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT99 | Single Phase Fault with Stuck Breaker on REDWILO7 (640326) 115 kV Bus a. Apply Fault at the REDWILO7 (640326) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO7 (640326) 115.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT100 | Single Phase Fault with Stuck Breaker on GI-95_POI (709500) 345 kV Bus a. Apply Fault at the GI-95_POI (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT101 | Single Phase Fault with Stuck Breaker on LAMAR7 (599950) 345 kV Bus a. Apply Fault at the LAMAR7 (599950) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMAR7 (599950) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT102 | Single Phase Fault with Stuck Breaker on G17-209-TAP (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT103 | Single Phase Fault with Stuck Breaker on G15-052T (560053) 345 kV Bus a. Apply Fault at the G15-052T (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT104 | Single Phase Fault with Stuck Breaker on GEN-2016-153 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT105 | Single Phase Fault with Stuck Breaker on GEN-2017-018 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT106 | Single Phase Fault with Stuck Breaker on G17-183-TAP (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT107 | Single Phase Fault with Stuck Breaker on AXTELL 3 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT108 | Single Phase Fault with Stuck Breaker on NEOSHO 5 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT109 | Single Phase Fault with Stuck Breaker on ROSEHIL4 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT110 | Single Phase Fault with Stuck Breaker on VIOLA 4 (533075) 138 kV Bus a. Apply Fault at the VIOLA 4 (533075) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT111 | Single Phase Fault with Stuck Breaker on THISTLE4 (539804) 138 kV Bus a. Apply Fault at the THISTLE4 (539804) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT112 | Single Phase Fault with Stuck Breaker on ST JOE 5 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT113 | Single Phase Fault with Stuck Breaker on COOPER 3 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25W | Transfer | GROUP3_P4_REGIONAL_FAULT114 | Single Phase Fault with Stuck Breaker on REDWILO3 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDWILO3 (640325) 345.0 kV to remove bus # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 CENTRAL | DISIS-2017-002 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT689 | 3 Phase fault on 5JOPPA S TP1161.00 (347334) 161 kV Bus a. Apply fault at the 5JOPPA S TP1161.00 (347334) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA S TP1 (347334) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at Silk (505432) and New Madrid (300006, 300007) generating sites following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT690 | 3 Phase fault on 5JOPPA T3 161.00 (347335) 161 kV Bus a. Apply fault at the 5JOPPA T3 161.00 (347335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA T3 (347335) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at Silk (505432) and New Madrid (300006, 300007) generating sites following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25S | Base | GROUP3_P1_LOCAL_FAULT989 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Oscillatory response due to non-convergence following the event. | Contingent on the queued Multi - Sheldon - Monolith 115 kV upgrade. Stable response observed after the upgrade is in-service.
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT689 | 3 Phase fault on 5JOPPA S TP1161.00 (347334) 161 kV Bus a. Apply fault at the 5JOPPA S TP1161.00 (347334) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA S TP1 (347334) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at Silk (505432) and New Madrid (300006, 300007) generating sites following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT690 | 3 Phase fault on 5JOPPA T3 161.00 (347335) 161 kV Bus a. Apply fault at the 5JOPPA T3 161.00 (347335) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5JOPPA T3 (347335) 161.0 kV to 5MASS (348295) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at Silk (505432) and New Madrid (300006, 300007) generating sites following the event. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT722 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Simulations crashes due to non-convergence. | Remove reclosing.
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P1_LOCAL_FAULT989 | 3 Phase fault on SHELDON7 115.00 (640278) 115 kV Bus a. Apply fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MONOLITH 7 (640591) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | No | Yes | No | Yes | Yes | No | Oscillatory response due to non-convergence following the event. | Contingent on the queued Multi - Sheldon - Monolith 115 kV upgrade. Stable response observed after the upgrade is in-service.
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P4_LOCAL_FAULT350 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P4_LOCAL_FAULT378 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P4_LOCAL_FAULT593 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P4_REGIONAL_FAULT24 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. | Line - Wolf Creek - Blackberry 345 kV
03 CENTRAL | DISIS-2017-002 CF | 25W | Base | GROUP3_P4_REGIONAL_FAULT28 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Active power oscillations observed at WCGS U1 (532751) following the event. | Line - Wolf Creek - Blackberry 345 kV
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 3OLA_AR_3DANVLE_AR | 3 Phase fault on 3OLA AR (337900) 115 kV Bus a. Apply fault at the 3OLA AR (337900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3OLA AR 115.0 KV 337900 TO 3DANVLE AR 115.0 KV 337901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 3OLA_AR_3DANVLE_AR | 3 Phase fault on 3OLA AR (337900) 115 kV Bus a. Apply fault at the 3OLA AR (337900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3OLA AR 115.0 KV 337900 TO 3DANVLE AR 115.0 KV 337901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 4LUTHER_4LUTHERD | 3 Phase fault on 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138.0 KV 300135 TO 4LUTHERD 138.0 KV 301372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 4LUTHER_4LUTHERD | 3 Phase fault on 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138.0 KV 300135 TO 4LUTHERD 138.0 KV 301372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 4LUTHER_4MEMORALT | 3 Phase fault on 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138.0 KV 300135 TO 4MEMORALT 138.0 KV 300136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 4LUTHER_4MEMORALT | 3 Phase fault on 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138.0 KV 300135 TO 4MEMORALT 138.0 KV 300136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 4MEMORALT_4MEMORAL | 3 Phase fault on 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138.0 KV 300136 TO 4MEMORAL 138.0 KV 301541 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 4MEMORALT_4MEMORAL | 3 Phase fault on 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138.0 KV 300136 TO 4MEMORAL 138.0 KV 301541 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 4MEMORALT_JNSKAMO4 | 3 Phase fault on 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138.0 KV 300136 TO JNSKAMO4 138.0 KV 514906 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 4MEMORALT_JNSKAMO4 | 3 Phase fault on 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138.0 KV 300136 TO JNSKAMO4 138.0 KV 514906 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 53CACHE4_ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 53CACHE4_ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 53GARNT4_77MEMTP4 | 3 Phase fault on 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138.0 KV 509762 TO 77MEMTP4 138.0 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 53GARNT4_77MEMTP4 | 3 Phase fault on 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138.0 KV 509762 TO 77MEMTP4 138.0 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 53GARST4_53GARNS4 | 3 Phase fault on 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138.0 KV 509763 TO 53GARNS4 138.0 KV 509774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 53GARST4_53GARNS4 | 3 Phase fault on 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138.0 KV 509763 TO 53GARNS4 138.0 KV 509774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 53GARST4_TSE | 3 Phase fault on 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138.0 KV 509763 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 53GARST4_TSE | 3 Phase fault on 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138.0 KV 509763 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5CDRCRST_TAHLQH_5 | 3 Phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161.0 KV 301344 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5CDRCRST_TAHLQH_5 | 3 Phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161.0 KV 301344 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5DANVLE_AR_337901 | 3 Phase fault on 5DANVLE AR! (337902) 161 kV Bus a. Apply fault at the 5DANVLE AR!( 337902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5DANVLE AR! 337902 TO 3DANVLE AR 337901 TO 1DANVLE AR 337944 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5DANVLE_AR_337901 | 3 Phase fault on 5DANVLE AR! (337902) 161 kV Bus a. Apply fault at the 5DANVLE AR!( 337902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5DANVLE AR! 337902 TO 3DANVLE AR 337901 TO 1DANVLE AR 337944 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5DANVLE_AR_DARDANE5 | 3 Phase fault on 5DANVLE AR! (337902) 161 kV Bus a. Apply fault at the 5DANVLE AR! (337902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5DARDANELLE 161.0 KV 337903 TO DARDANE5 161.0 KV 505508 CKT 1 b.2. 5DANVLE AR! 161.0 KV 337902 TO 5DARDANELLE 161.0 KV 337903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5DANVLE_AR_DARDANE5 | 3 Phase fault on 5DANVLE AR! (337902) 161 kV Bus a. Apply fault at the 5DANVLE AR! (337902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5DARDANELLE 161.0 KV 337903 TO DARDANE5 161.0 KV 505508 CKT 1 b.2. 5DANVLE AR! 161.0 KV 337902 TO 5DARDANELLE 161.0 KV 337903 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5DANVLE_AR_MAGZREC5 | 3 Phase fault on 5DANVLE AR! (337902) 161 kV Bus a. Apply fault at the 5DANVLE AR! (337902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO MAGZREC5 161.0 KV 507195 CKT 1 b.2. LOAD A1 507195 b.3. 5DANVLE AR! 161.0 KV 337902 TO MAGZREC5 161.0 KV 507195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5DANVLE_AR_MAGZREC5 | 3 Phase fault on 5DANVLE AR! (337902) 161 kV Bus a. Apply fault at the 5DANVLE AR! (337902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO MAGZREC5 161.0 KV 507195 CKT 1 b.2. LOAD A1 507195 b.3. 5DANVLE AR! 161.0 KV 337902 TO MAGZREC5 161.0 KV 507195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5HILLTOP_DARDANE5 | 3 Phase fault on 5HILLTOP% (338110) 161 kV Bus a. Apply fault at the 5HILLTOP% (338110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HILLTOP% 161.0 KV 338110 TO DARDANE5 161.0 KV 505508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5HILLTOP_DARDANE5 | 3 Phase fault on 5HILLTOP% (338110) 161 kV Bus a. Apply fault at the 5HILLTOP% (338110) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5HILLTOP% 161.0 KV 338110 TO DARDANE5 161.0 KV 505508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5LBRTYTKM_LIBERTY5 | 3 Phase fault on 5LBRTYTKM (301557) 161 kV Bus a. Apply fault at the 5LBRTYTKM (301557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LBRTYTKM 161.0 KV 301557 TO LIBERTY5 161.0 KV 505524 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5LBRTYTKM_LIBERTY5 | 3 Phase fault on 5LBRTYTKM (301557) 161 kV Bus a. Apply fault at the 5LBRTYTKM (301557) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LBRTYTKM 161.0 KV 301557 TO LIBERTY5 161.0 KV 505524 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5PARK_TAHLQH_5 | 3 Phase fault on 5PARK (301307) 161 kV Bus a. Apply fault at the 5PARK (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161.0 KV 301307 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5PARK_TAHLQH_5 | 3 Phase fault on 5PARK (301307) 161 kV Bus a. Apply fault at the 5PARK (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161.0 KV 301307 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5RUSSELVL_DARDANE5 | 3 Phase fault on 5RUSSELVL.S (337904) 161 kV Bus a. Apply fault at the 5RUSSELVL.S (337904) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.S 161.0 KV 337904 TO DARDANE5 161.0 KV 505508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5RUSSELVL_DARDANE5 | 3 Phase fault on 5RUSSELVL.S (337904) 161 kV Bus a. Apply fault at the 5RUSSELVL.S (337904) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5RUSSELVL.S 161.0 KV 337904 TO DARDANE5 161.0 KV 505508 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5STIGLER_RS_KERR5 | 3 Phase fault on 5STIGLER (301550) 161 kV Bus a. Apply fault at the 5STIGLER (301550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STIGLER 161.0 KV 301550 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5STIGLER_RS_KERR5 | 3 Phase fault on 5STIGLER (301550) 161 kV Bus a. Apply fault at the 5STIGLER (301550) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5STIGLER 161.0 KV 301550 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 5TRIBES5_PECANCK5 | 3 Phase fault on 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161.0 KV 515228 TO PECANCK5 161.0 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 5TRIBES5_PECANCK5 | 3 Phase fault on 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161.0 KV 515228 TO PECANCK5 161.0 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 77MEM__77MEMTP4 | 3 Phase fault on 77MEM-E4 (509735) 138 kV Bus a. Apply fault at the 77MEM-E4 (509735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-E4 138.0 KV 509735 TO 77MEMTP4 138.0 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 77MEM__77MEMTP4 | 3 Phase fault on 77MEM-E4 (509735) 138 kV Bus a. Apply fault at the 77MEM-E4 (509735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-E4 138.0 KV 509735 TO 77MEMTP4 138.0 KV 509765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 8ANO_337912 | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO%( 337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 8ANO_337912 | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO%( 337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 8ANO_8PHILL | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 8P.HILL% 500.0 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 8ANO_8PHILL | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 8P.HILL% 500.0 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 8ANO_FTSMITH8 | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO FTSMITH8 500.0 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 8ANO_FTSMITH8 | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO FTSMITH8 500.0 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | 8HAPPYVALY_8ANO | 3 Phase fault on 8HAPPYVALY% (337811) 500 kV Bus a. Apply fault at the 8HAPPYVALY% (337811) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8ANO% 500.0 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | 8HAPPYVALY_8ANO | 3 Phase fault on 8HAPPYVALY% (337811) 500 kV Bus a. Apply fault at the 8HAPPYVALY% (337811) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8ANO% 500.0 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ACORN_4_JONESSB4 | 3 Phase fault on ACORN 4 (515459) 138 kV Bus a. Apply fault at the ACORN 4 (515459) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ACORN_4_JONESSB4 | 3 Phase fault on ACORN 4 (515459) 138 kV Bus a. Apply fault at the ACORN 4 (515459) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | AGENCY_5_PECANCK5 | 3 Phase fault on AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161.0 KV 515230 TO PECANCK5 161.0 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | AGENCY_5_PECANCK5 | 3 Phase fault on AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161.0 KV 515230 TO PECANCK5 161.0 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ALLEN_4_ALLEN_4 | 3 Phase fault on ALLEN 4 (505598) 138 kV Bus a. Apply fault at the ALLEN 4 (505598) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO ALLEN--4 138.0 KV 510916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ALLEN_4_ALLEN_4 | 3 Phase fault on ALLEN 4 (505598) 138 kV Bus a. Apply fault at the ALLEN 4 (505598) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO ALLEN--4 138.0 KV 510916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ALLEN_4_GERTY_4 | 3 Phase fault on ALLEN 4 (505598) 138 kV Bus a. Apply fault at the ALLEN 4 (505598) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO GERTY 4 138.0 KV 505650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ALLEN_4_GERTY_4 | 3 Phase fault on ALLEN 4 (505598) 138 kV Bus a. Apply fault at the ALLEN 4 (505598) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO GERTY 4 138.0 KV 505650 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ALLEN_4_TUPELO_4 | 3 Phase fault on ALLEN 4 (505598) 138 kV Bus a. Apply fault at the ALLEN 4 (505598) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO TUPELO 4 138.0 KV 505600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ALLEN_4_TUPELO_4 | 3 Phase fault on ALLEN 4 (505598) 138 kV Bus a. Apply fault at the ALLEN 4 (505598) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 4 138.0 KV 505598 TO TUPELO 4 138.0 KV 505600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ALLENGT4_EXPCOLT4 | 3 Phase fault on ALLENGT4 (510881) 138 kV Bus a. Apply fault at the ALLENGT4 (510881) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENGT4 138.0 KV 510881 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ALLENGT4_EXPCOLT4 | 3 Phase fault on ALLENGT4 (510881) 138 kV Bus a. Apply fault at the ALLENGT4 (510881) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENGT4 138.0 KV 510881 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ALLENNG4_EXPCOLT4 | 3 Phase fault on ALLENNG4 (510863) 138 kV Bus a. Apply fault at the ALLENNG4 (510863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENNG4 138.0 KV 510863 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ALLENNG4_EXPCOLT4 | 3 Phase fault on ALLENNG4 (510863) 138 kV Bus a. Apply fault at the ALLENNG4 (510863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLENNG4 138.0 KV 510863 TO EXPCOLT4 138.0 KV 510935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | AMBERTP4_AMBER_4 | 3 Phase fault on AMBERTP4 (520530) 138 kV Bus a. Apply fault at the AMBERTP4 (520530) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO AMBER 4 138.0 KV 520531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | AMBERTP4_AMBER_4 | 3 Phase fault on AMBERTP4 (520530) 138 kV Bus a. Apply fault at the AMBERTP4 (520530) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO AMBER 4 138.0 KV 520531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | AMBERTP4_BLANCHD4 | 3 Phase fault on AMBERTP4 (520530) 138 kV Bus a. Apply fault at the AMBERTP4 (520530) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | AMBERTP4_BLANCHD4 | 3 Phase fault on AMBERTP4 (520530) 138 kV Bus a. Apply fault at the AMBERTP4 (520530) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMBERTP4 138.0 KV 520530 TO BLANCHD4 138.0 KV 520828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ANADARK4_520810 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ANADARK4_520810 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ANADARK4_CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ANADARK4_CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ANADARK4_GEORGIA4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ANADARK4_GEORGIA4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | AOCPT_2_LULA_2 | 3 Phase fault on AOCPT 2 (515190) 69 kV Bus a. Apply fault at the AOCPT 2 (515190) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AOCPT 2 69.0 KV 515190 TO LULA 2 69.0 KV 515191 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | AOCPT_2_LULA_2 | 3 Phase fault on AOCPT 2 (515190) 69 kV Bus a. Apply fault at the AOCPT 2 (515190) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AOCPT 2 69.0 KV 515190 TO LULA 2 69.0 KV 515191 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARBUCKL4_VANOSTP4 | 3 Phase fault on ARBUCKL4 (515117) 138 kV Bus a. Apply fault at the ARBUCKL4 (515117) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138.0 KV 515117 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARBUCKL4_VANOSTP4 | 3 Phase fault on ARBUCKL4 (515117) 138 kV Bus a. Apply fault at the ARBUCKL4 (515117) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBUCKL4 138.0 KV 515117 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARBWIND4_HONEYCK4 | 3 Phase fault on ARBWIND4 (515575) 138 kV Bus a. Apply fault at the ARBWIND4 (515575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBWIND4 138.0 KV 515575 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARBWIND4_HONEYCK4 | 3 Phase fault on ARBWIND4 (515575) 138 kV Bus a. Apply fault at the ARBWIND4 (515575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARBWIND4 138.0 KV 515575 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARCADIA4_514907 | a. Apply single-phase fault on: a.1. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 a.2. LOAD 1 515461 a.3. RNDBARN4 138.0 KV 515461 TO BURGETT4 138.0 KV 514510 CKT 1 a.4. LOAD 1 514510 a.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1, b. with stuck breaker near ARCADIA4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. ARCADIA4 138.0 KV 514907 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARCADIA4_514907 | a. Apply single-phase fault on: a.1. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 a.2. LOAD 1 515461 a.3. RNDBARN4 138.0 KV 515461 TO BURGETT4 138.0 KV 514510 CKT 1 a.4. LOAD 1 514510 a.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1, b. with stuck breaker near ARCADIA4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. ARCADIA4 138.0 KV 514907 TO JNSKAMO4 138.0 KV 514906 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARCADIA4_514908 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4( 514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARCADIA4_514908 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4( 514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARCADIA4_DANFRTH4 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARCADIA4_DANFRTH4 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARCADIA4_HSL_4 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 b.2. LOAD 1 515465 b.3. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 b.4. LOAD 1 515465 b.5. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARCADIA4_HSL_4 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 b.2. LOAD 1 515465 b.3. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 b.4. LOAD 1 515465 b.5. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARCADIA7_514908 | a. Apply single-phase fault on: a.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1, b. with stuck breaker near ARCADIA7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARCADIA7_514908 | a. Apply single-phase fault on: a.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1, b. with stuck breaker near ARCADIA7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. ARCADIA7 345.0 KV 514908 TO NORTWST7 345.0 KV 514880 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARCADIA7_GEN_2017_132 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-132 345.0 KV 760032 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | No | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARCADIA7_GEN_2017_132 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-132 345.0 KV 760032 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARCADIA7_REDBUD_7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARCADIA7_REDBUD_7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARCADIA7_SEMINOL7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARCADIA7_SEMINOL7_6 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ARTVLTP4_ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ARTVLTP4_ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ASHLAND4_PITTSBG4 | 3 Phase fault on ASHLAND4 (520818) 138 kV Bus a. Apply fault at the ASHLAND4 (520818) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHLAND4 138.0 KV 520818 TO PITTSBG4 138.0 KV 521030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ASHLAND4_PITTSBG4 | 3 Phase fault on ASHLAND4 (520818) 138 kV Bus a. Apply fault at the ASHLAND4 (520818) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHLAND4 138.0 KV 520818 TO PITTSBG4 138.0 KV 521030 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ATOKA_2_510887 | 3 Phase fault on ATOKA--2 (510882) 69 kV Bus a. Apply fault at the ATOKA--2( 510882) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--2 510882 TO ATOKA--4 510887 TO ATOKA1-T 510860 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ATOKA_2_510887 | 3 Phase fault on ATOKA--2 (510882) 69 kV Bus a. Apply fault at the ATOKA--2( 510882) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--2 510882 TO ATOKA--4 510887 TO ATOKA1-T 510860 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ATOKA_4_BOGYDPT4 | 3 Phase fault on ATOKA--4 (510887) 138 kV Bus a. Apply fault at the ATOKA--4 (510887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO BOGYDPT4 138.0 KV 520448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ATOKA_4_BOGYDPT4 | 3 Phase fault on ATOKA--4 (510887) 138 kV Bus a. Apply fault at the ATOKA--4 (510887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO BOGYDPT4 138.0 KV 520448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ATOKA_4_LANE_4 | 3 Phase fault on ATOKA--4 (510887) 138 kV Bus a. Apply fault at the ATOKA--4 (510887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO LANE 4 138.0 KV 520968 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ATOKA_4_LANE_4 | 3 Phase fault on ATOKA--4 (510887) 138 kV Bus a. Apply fault at the ATOKA--4 (510887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO LANE 4 138.0 KV 520968 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | B1114_BA101ST4 | 3 Phase fault on B111---4 (509767) 138 kV Bus a. Apply fault at the B111---4 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138.0 KV 509767 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | B1114_BA101ST4 | 3 Phase fault on B111---4 (509767) 138 kV Bus a. Apply fault at the B111---4 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138.0 KV 509767 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BA.N_ST4_LLANETP4 | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO LLANETP4 138.0 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BA.N_ST4_LLANETP4 | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO LLANETP4 138.0 KV 509804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BA.N_ST4_ONETA_4 | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BA.N_ST4_ONETA_4 | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BA101_S4_BA101ST4 | 3 Phase fault on BA101 S4 (509737) 138 kV Bus a. Apply fault at the BA101 S4 (509737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101 S4 138.0 KV 509737 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BA101_S4_BA101ST4 | 3 Phase fault on BA101 S4 (509737) 138 kV Bus a. Apply fault at the BA101 S4 (509737) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101 S4 138.0 KV 509737 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BA101ST4_ONETA_4 | 3 Phase fault on BA101ST4 (509768) 138 kV Bus a. Apply fault at the BA101ST4 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138.0 KV 509768 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BA101ST4_ONETA_4 | 3 Phase fault on BA101ST4 (509768) 138 kV Bus a. Apply fault at the BA101ST4 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138.0 KV 509768 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BANNTAP4_E41ST_E4 | 3 Phase fault on BANNTAP4 (509785) 138 kV Bus a. Apply fault at the BANNTAP4 (509785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 138.0 KV 509785 TO E41ST_E4 138.0 KV 509861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BANNTAP4_E41ST_E4 | 3 Phase fault on BANNTAP4 (509785) 138 kV Bus a. Apply fault at the BANNTAP4 (509785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 138.0 KV 509785 TO E41ST_E4 138.0 KV 509861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BANO_S4__BANOST4 | 3 Phase fault on BA.NO-S4 (509721) 138 kV Bus a. Apply fault at the BA.NO-S4 (509721) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.NO-S4 138.0 KV 509721 TO BA.N-ST4 138.0 KV 509786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BANO_S4__BANOST4 | 3 Phase fault on BA.NO-S4 (509721) 138 kV Bus a. Apply fault at the BA.NO-S4 (509721) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.NO-S4 138.0 KV 509721 TO BA.N-ST4 138.0 KV 509786 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BARLING5_MASSARD5 | 3 Phase fault on BARLING5 (515311) 161 kV Bus a. Apply fault at the BARLING5 (515311) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARLING5 161.0 KV 515311 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BARLING5_MASSARD5 | 3 Phase fault on BARLING5 (515311) 161 kV Bus a. Apply fault at the BARLING5 (515311) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARLING5 161.0 KV 515311 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BENNGTN4_BENNSUB4 | 3 Phase fault on BENNGTN4 (520826) 138 kV Bus a. Apply fault at the BENNGTN4 (520826) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO BENNSUB4 138.0 KV 521115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BENNGTN4_BENNSUB4 | 3 Phase fault on BENNGTN4 (520826) 138 kV Bus a. Apply fault at the BENNGTN4 (520826) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO BENNSUB4 138.0 KV 521115 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BENNGTN4_DURANTP4 | 3 Phase fault on BENNGTN4 (520826) 138 kV Bus a. Apply fault at the BENNGTN4 (520826) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BENNGTN4_DURANTP4 | 3 Phase fault on BENNGTN4 (520826) 138 kV Bus a. Apply fault at the BENNGTN4 (520826) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BENNGTN4_UNGER_4 | 3 Phase fault on BENNGTN4 (520826) 138 kV Bus a. Apply fault at the BENNGTN4 (520826) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO UNGER 4 138.0 KV 521077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BENNGTN4_UNGER_4 | 3 Phase fault on BENNGTN4 (520826) 138 kV Bus a. Apply fault at the BENNGTN4 (520826) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENNGTN4 138.0 KV 520826 TO UNGER 4 138.0 KV 521077 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BENTON_7_532986_6 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7( 532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 532791 TO BENTON 4 532986 TO BENTN2 1 532822 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BENTON_7_532986_6 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7( 532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 532791 TO BENTON 4 532986 TO BENTN2 1 532822 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BENTON_7_ROSEHIL7_6 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 345.0 KV 532791 TO ROSEHIL7 345.0 KV 532794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BENTON_7_ROSEHIL7_6 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 345.0 KV 532791 TO ROSEHIL7 345.0 KV 532794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BENTON_7_WICHITA7_6 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 345.0 KV 532791 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BENTON_7_WICHITA7_6 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 345.0 KV 532791 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BENTON_7_WOLFCRK7_6 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 345.0 KV 532791 TO WOLFCRK7 345.0 KV 532797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BENTON_7_WOLFCRK7_6 | 3 Phase fault on BENTON 7 (532791) 345 kV Bus a. Apply fault at the BENTON 7 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 345.0 KV 532791 TO WOLFCRK7 345.0 KV 532797 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BEVYTAP5_FTSMTHE5 | 3 Phase fault on BEVYTAP5 (515299) 161 kV Bus a. Apply fault at the BEVYTAP5 (515299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161.0 KV 515299 TO FTSMTHE5 161.0 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BEVYTAP5_FTSMTHE5 | 3 Phase fault on BEVYTAP5 (515299) 161 kV Bus a. Apply fault at the BEVYTAP5 (515299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161.0 KV 515299 TO FTSMTHE5 161.0 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BLANCHD4_MAUD_4 | 3 Phase fault on BLANCHD4 (511508) 138 kV Bus a. Apply fault at the BLANCHD4 (511508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 511508 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BLANCHD4_MAUD_4 | 3 Phase fault on BLANCHD4 (511508) 138 kV Bus a. Apply fault at the BLANCHD4 (511508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 511508 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BLANCHD4_OU_SW_4 | 3 Phase fault on BLANCHD4 (520828) 138 kV Bus a. Apply fault at the BLANCHD4 (520828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BLANCHD4_OU_SW_4 | 3 Phase fault on BLANCHD4 (520828) 138 kV Bus a. Apply fault at the BLANCHD4 (520828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 520828 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BLUEBEL2_515242 | 3 Phase fault on BLUEBEL2 (515241) 69 kV Bus a. Apply fault at the BLUEBEL2( 515241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BLUEBEL2_515242 | 3 Phase fault on BLUEBEL2 (515241) 69 kV Bus a. Apply fault at the BLUEBEL2( 515241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BLUEBEL4_BOWDEN_4 | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138.0 KV 515242 TO BOWDEN 4 138.0 KV 515243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BLUEBEL4_BOWDEN_4 | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138.0 KV 515242 TO BOWDEN 4 138.0 KV 515243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BLUERIV4_PARKLN_4 | 3 Phase fault on BLUERIV4 (515133) 138 kV Bus a. Apply fault at the BLUERIV4 (515133) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138.0 KV 515133 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BLUERIV4_PARKLN_4 | 3 Phase fault on BLUERIV4 (515133) 138 kV Bus a. Apply fault at the BLUERIV4 (515133) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUERIV4 138.0 KV 515133 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BODLE_4_BUTRFLD4 | 3 Phase fault on BODLE 4 (515155) 138 kV Bus a. Apply fault at the BODLE 4 (515155) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO REBAR 4 138.0 KV 515408 CKT 1 b.2. LOAD 1 515408 b.3. BODLE 4 138.0 KV 515155 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BODLE_4_BUTRFLD4 | 3 Phase fault on BODLE 4 (515155) 138 kV Bus a. Apply fault at the BODLE 4 (515155) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTRFLD4 138.0 KV 515176 TO REBAR 4 138.0 KV 515408 CKT 1 b.2. LOAD 1 515408 b.3. BODLE 4 138.0 KV 515155 TO REBAR 4 138.0 KV 515408 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BODLE_4_COLBRTP4 | 3 Phase fault on BODLE 4 (515155) 138 kV Bus a. Apply fault at the BODLE 4 (515155) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BODLE_4_COLBRTP4 | 3 Phase fault on BODLE 4 (515155) 138 kV Bus a. Apply fault at the BODLE 4 (515155) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BODLE 4 138.0 KV 515155 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BOGYDPT4_BOGGY4 | 3 Phase fault on BOGYDPT4 (520448) 138 kV Bus a. Apply fault at the BOGYDPT4 (520448) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOGYDPT4 138.0 KV 520448 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BOGYDPT4_BOGGY4 | 3 Phase fault on BOGYDPT4 (520448) 138 kV Bus a. Apply fault at the BOGYDPT4 (520448) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOGYDPT4 138.0 KV 520448 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BOGYDPT4_BOGGYDP4 | 3 Phase fault on BOGYDPT4 (520448) 138 kV Bus a. Apply fault at the BOGYDPT4 (520448) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOGYDPT4 138.0 KV 520448 TO BOGGYDP4 138.0 KV 520527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BOGYDPT4_BOGGYDP4 | 3 Phase fault on BOGYDPT4 (520448) 138 kV Bus a. Apply fault at the BOGYDPT4 (520448) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOGYDPT4 138.0 KV 520448 TO BOGGYDP4 138.0 KV 520527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRANCH_2_515316_7 | 3 Phase fault on BRANCH 2 (515313) 69 kV Bus a. Apply fault at the BRANCH 2( 515313) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 515313 TO 515316 TO 515708 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRANCH_2_515316_7 | 3 Phase fault on BRANCH 2 (515313) 69 kV Bus a. Apply fault at the BRANCH 2( 515313) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 515313 TO 515316 TO 515708 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRANCH_2_PENDER_2 | 3 Phase fault on BRANCH 2 (515313) 69 kV Bus a. Apply fault at the BRANCH 2 (515313) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENDER 2 69.0 KV 515317 TO HELBERG2 69.0 KV 515325 CKT 1 b.2. LOAD 1 515325 b.3. 2 69.0 KV 515313 TO PENDER 2 69.0 KV 515317 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRANCH_2_PENDER_2 | 3 Phase fault on BRANCH 2 (515313) 69 kV Bus a. Apply fault at the BRANCH 2 (515313) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENDER 2 69.0 KV 515317 TO HELBERG2 69.0 KV 515325 CKT 1 b.2. LOAD 1 515325 b.3. 2 69.0 KV 515313 TO PENDER 2 69.0 KV 515317 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRANCH_2_WBOONVL2 | 3 Phase fault on BRANCH 2 (515313) 69 kV Bus a. Apply fault at the BRANCH 2 (515313) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONVIL2 69.0 KV 507183 TO 2 69.0 KV 515313 CKT 1 b.2. BOONEVIL 2 69.0 KV 504172 TO BOONVIL2 69.0 KV 507183 CKT 1 b.3. LOAD 1 507183 b.4. BOONEVIL 2 69.0 KV 504172 TO WBOONVL2 69.0 KV 507198 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRANCH_2_WBOONVL2 | 3 Phase fault on BRANCH 2 (515313) 69 kV Bus a. Apply fault at the BRANCH 2 (515313) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOONVIL2 69.0 KV 507183 TO 2 69.0 KV 515313 CKT 1 b.2. BOONEVIL 2 69.0 KV 504172 TO BOONVIL2 69.0 KV 507183 CKT 1 b.3. LOAD 1 507183 b.4. BOONEVIL 2 69.0 KV 504172 TO WBOONVL2 69.0 KV 507198 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRANCH_5_515316 | a. Apply single-phase fault on: a.1. BRANCH5 161.1 KV 515316 TO NMAGZIN5 161.0 KV 507190 CKT 1, b. with stuck breaker near BRANCH 5 161 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. BRANCH5 161.1 KV 515316 TO SHORTMT5 161.0 KV 515358 CKT 1 c.2. LOAD 1 515358 c.3. LOAD 2 515358 c.4. SHORTMT5 161.0 KV 515358 TO SUBIACT5 161.0 KV 515440 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRANCH_5_515316 | a. Apply single-phase fault on: a.1. BRANCH5 161.1 KV 515316 TO NMAGZIN5 161.0 KV 507190 CKT 1, b. with stuck breaker near BRANCH 5 161 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. BRANCH5 161.1 KV 515316 TO SHORTMT5 161.0 KV 515358 CKT 1 c.2. LOAD 1 515358 c.3. LOAD 2 515358 c.4. SHORTMT5 161.0 KV 515358 TO SUBIACT5 161.0 KV 515440 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRANCH_5_GEN_2017_231 | 3 Phase fault on BRANCH 5 (515316) 161 kV Bus a. Apply fault at the BRANCH 5 (515316) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5 161.0 KV 515316 TO GEN-2017-231 161.0 KV 760221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRANCH_5_GEN_2017_231 | 3 Phase fault on BRANCH 5 (515316) 161 kV Bus a. Apply fault at the BRANCH 5 (515316) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5 161.0 KV 515316 TO GEN-2017-231 161.0 KV 760221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRANCH_5_GRNDPRT5 | 3 Phase fault on BRANCH 5 (515316) 161 kV Bus a. Apply fault at the BRANCH 5 (515316) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5 161.0 KV 515316 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRANCH_5_GRNDPRT5 | 3 Phase fault on BRANCH 5 (515316) 161 kV Bus a. Apply fault at the BRANCH 5 (515316) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5 161.0 KV 515316 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRANCH_5_SUBIACT5 | 3 Phase fault on BRANCH 5 (515316) 161 kV Bus a. Apply fault at the BRANCH 5 (515316) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHORTMT5 161.0 KV 515358 TO SUBIACT5 161.0 KV 515440 CKT 1 b.2. 5 161.0 KV 515316 TO SHORTMT5 161.0 KV 515358 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRANCH_5_SUBIACT5 | 3 Phase fault on BRANCH 5 (515316) 161 kV Bus a. Apply fault at the BRANCH 5 (515316) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHORTMT5 161.0 KV 515358 TO SUBIACT5 161.0 KV 515440 CKT 1 b.2. 5 161.0 KV 515316 TO SHORTMT5 161.0 KV 515358 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRCKWND4_BRECKNR4 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRCKWND4_BRECKNR4 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRECKNR4_ENIDINT4 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRECKNR4_ENIDINT4 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRISTOW2_515035 | 3 Phase fault on BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2( 515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 515034 TO BRISTOW4 515035 TO BRISTOW1 515709 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRISTOW2_515035 | 3 Phase fault on BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2( 515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 515034 TO BRISTOW4 515035 TO BRISTOW1 515709 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRISTOW2_PRNCVLT2 | 3 Phase fault on BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2 (515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 69.0 KV 515034 TO PRNCVLT2 69.0 KV 515037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRISTOW2_PRNCVLT2 | 3 Phase fault on BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2 (515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 69.0 KV 515034 TO PRNCVLT2 69.0 KV 515037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRISTOW4_515035 | a. Apply single-phase fault on: a.1. BRISTOW4 138.0 KV 515035 TO BEGGS 4 138.0 KV 515249 CKT 1 a.2. LOAD 1 515249 a.3. BEGGS 4 138.0 KV 515249 TO PECANCK4 138.0 KV 515233 CKT 1, b. with stuck breaker near BRISTOW4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. GRNWOOD4 138.0 KV 515417 TO BRISTOW4 138.0 KV 515035 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRISTOW4_515035 | a. Apply single-phase fault on: a.1. BRISTOW4 138.0 KV 515035 TO BEGGS 4 138.0 KV 515249 CKT 1 a.2. LOAD 1 515249 a.3. BEGGS 4 138.0 KV 515249 TO PECANCK4 138.0 KV 515233 CKT 1, b. with stuck breaker near BRISTOW4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. GRNWOOD4 138.0 KV 515417 TO BRISTOW4 138.0 KV 515035 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRISTOW4_BEGGS_4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 138.0 KV 515233 TO BEGGS 4 138.0 KV 515249 CKT 1 b.2. LOAD 1 515249 b.3. BRISTOW4 138.0 KV 515035 TO BEGGS 4 138.0 KV 515249 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRISTOW4_BEGGS_4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 138.0 KV 515233 TO BEGGS 4 138.0 KV 515249 CKT 1 b.2. LOAD 1 515249 b.3. BRISTOW4 138.0 KV 515035 TO BEGGS 4 138.0 KV 515249 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRISTOW4_BLUEBEL4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRISTOW4_BLUEBEL4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BRISTOW4_GRNWOOD4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO GRNWOOD4 138.0 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BRISTOW4_GRNWOOD4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO GRNWOOD4 138.0 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BROWN_4_GEN_2016_030 | 3 Phase fault on BROWN 4 (515157) 138 kV Bus a. Apply fault at the BROWN 4 (515157) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2016-030 138.0 KV 587200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BROWN_4_GEN_2016_030 | 3 Phase fault on BROWN 4 (515157) 138 kV Bus a. Apply fault at the BROWN 4 (515157) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO GEN-2016-030 138.0 KV 587200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BROWN_4_STRRDTP4 | 3 Phase fault on BROWN 4 (515157) 138 kV Bus a. Apply fault at the BROWN 4 (515157) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BROWN_4_STRRDTP4 | 3 Phase fault on BROWN 4 (515157) 138 kV Bus a. Apply fault at the BROWN 4 (515157) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWN 4 138.0 KV 515157 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BROWNTP4_BODLE_4 | 3 Phase fault on BROWNTP4 (515152) 138 kV Bus a. Apply fault at the BROWNTP4 (515152) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO BODLE 4 138.0 KV 515155 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BROWNTP4_BODLE_4 | 3 Phase fault on BROWNTP4 (515152) 138 kV Bus a. Apply fault at the BROWNTP4 (515152) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO BODLE 4 138.0 KV 515155 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BROWNTP4_STRRDTP4 | 3 Phase fault on BROWNTP4 (515152) 138 kV Bus a. Apply fault at the BROWNTP4 (515152) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BROWNTP4_STRRDTP4 | 3 Phase fault on BROWNTP4 (515152) 138 kV Bus a. Apply fault at the BROWNTP4 (515152) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BROWNTP4 138.0 KV 515152 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BUFFALO7_GEN_2017_220 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2017-220 345.0 KV 760284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BUFFALO7_GEN_2017_220 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO GEN-2017-220 345.0 KV 760284 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BUFFALO7_KINGMAN7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO KINGMAN7 345.0 KV 532783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BUFFALO7_KINGMAN7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO KINGMAN7 345.0 KV 532783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BUFFALO7_THISTLES7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BUFFALO7_THISTLES7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BUFFALO7_WICHITA7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO WICHITA7 345.0 KV 532796 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BUFFALO7_WICHITA7_6 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO WICHITA7 345.0 KV 532796 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BULFOOT4_BULFTTP4 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BULFOOT4_BULFTTP4 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BULFTTP4_DOVERSW4 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BULFTTP4_DOVERSW4 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BUNCHCK4_BRECKNR4 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BUNCHCK4_BRECKNR4 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BUTRFLD4_COLBERT4 | 3 Phase fault on BUTRFLD4 (515176) 138 kV Bus a. Apply fault at the BUTRFLD4 (515176) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRT-4 138.0 KV 515193 TO COLBERT4 138.0 KV 520860 CKT 1 b.2. LOAD 1 520860 b.3. BUTRFLD4 138.0 KV 515176 TO COLBRT-4 138.0 KV 515193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BUTRFLD4_COLBERT4 | 3 Phase fault on BUTRFLD4 (515176) 138 kV Bus a. Apply fault at the BUTRFLD4 (515176) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRT-4 138.0 KV 515193 TO COLBERT4 138.0 KV 520860 CKT 1 b.2. LOAD 1 520860 b.3. BUTRFLD4 138.0 KV 515176 TO COLBRT-4 138.0 KV 515193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BYRONTP4_BYRON_4 | 3 Phase fault on BYRONTP4 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRONTP4 138.0 KV 520432 TO BYRON 4 138.0 KV 520477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BYRONTP4_BYRON_4 | 3 Phase fault on BYRONTP4 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRONTP4 138.0 KV 520432 TO BYRON 4 138.0 KV 520477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | BYRONTP4_DRIFTWD4 | 3 Phase fault on BYRONTP4 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRONTP4 138.0 KV 520432 TO DRIFTWD4 138.0 KV 521200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | BYRONTP4_DRIFTWD4 | 3 Phase fault on BYRONTP4 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRONTP4 138.0 KV 520432 TO DRIFTWD4 138.0 KV 521200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CALUMET4_KGFSHSW4 | 3 Phase fault on CALUMET4 (520839) 138 kV Bus a. Apply fault at the CALUMET4 (520839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO CONCHO 4 138.0 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. CALUMET4 138.0 KV 520839 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CALUMET4_KGFSHSW4 | 3 Phase fault on CALUMET4 (520839) 138 kV Bus a. Apply fault at the CALUMET4 (520839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO CONCHO 4 138.0 KV 520865 CKT 1 b.2. LOAD 1 520865 b.3. CALUMET4 138.0 KV 520839 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CAN_GAS4_JENSEN_4 | 3 Phase fault on CAN_GAS4 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CAN_GAS4_JENSEN_4 | 3 Phase fault on CAN_GAS4 (511540) 138 kV Bus a. Apply fault at the CAN_GAS4 (511540) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CAN_GAS4 138.0 KV 511540 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CANADN_4_CANADNS4 | 3 Phase fault on CANADN-4 (514947) 138 kV Bus a. Apply fault at the CANADN-4 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CANADN_4_CANADNS4 | 3 Phase fault on CANADN-4 (514947) 138 kV Bus a. Apply fault at the CANADN-4 (514947) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADN-4 138.0 KV 514947 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CANADN7_515606_6 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7( 515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 515605 TO CANDN11 515606 TO CANDNT1 515608 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CANADN7_515606_6 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7( 515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 515605 TO CANDN11 515606 TO CANDNT1 515608 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CANADN7_515607 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7( 515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 515605 TO CANDN12 515607 TO CANDNT2 515609 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CANADN7_515607 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7( 515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 515605 TO CANDN12 515607 TO CANDNT2 515609 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CANADN7_FSHRTAP7_6 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 345.0 KV 515605 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CANADN7_FSHRTAP7_6 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 345.0 KV 515605 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CANADNS4_520841 | 3 Phase fault on CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4( 520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CANADNS4_520841 | 3 Phase fault on CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4( 520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 520842 TO CANADNS2 520841 TO CANTERT 521164 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | No | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CANADNS4_GOLDSBY4 | 3 Phase fault on CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GOLDSBY4 138.0 KV 520924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CANADNS4_GOLDSBY4 | 3 Phase fault on CANADNS4 (520842) 138 kV Bus a. Apply fault at the CANADNS4 (520842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANADNS4 138.0 KV 520842 TO GOLDSBY4 138.0 KV 520924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CANEYCK4_LTLCITY4 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLCITY4 138.0 KV 515151 TO BROWNTP4 138.0 KV 515152 CKT 1 b.2. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CANEYCK4_LTLCITY4 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLCITY4 138.0 KV 515151 TO BROWNTP4 138.0 KV 515152 CKT 1 b.2. CANEYCK4 138.0 KV 515150 TO LTLCITY4 138.0 KV 515151 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CANEYCK4_TEXOMAJ4 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CANEYCK4_TEXOMAJ4 | 3 Phase fault on CANEYCK4 (515150) 138 kV Bus a. Apply fault at the CANEYCK4 (515150) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANEYCK4 138.0 KV 515150 TO TEXOMAJ4 138.0 KV 521067 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CARTER_4_CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CARTER_4_CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CARTER_4_HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CARTER_4_HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CARTRCO4_GEN_2017_027_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CARTRCO4_GEN_2017_027_7 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CARTRCO4_ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on frequency protection settings | Disabling frequency protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CARTRCO4_ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CDRDLTP4_OKEENE_4 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CDRDLTP4_OKEENE_4 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHAMSPR5_506944 | a. Apply single-phase fault on: a.1. CHAMSPR5 161.0 KV 506944 TO WEDINGTON 161.0 KV 506992 CKT 1, b. with stuck breaker near CHAMSPR5 161 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CHAMSPR5 161.0 KV 506944 TO TONTITN5 161.0 KV 506957 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHAMSPR5_506944 | a. Apply single-phase fault on: a.1. CHAMSPR5 161.0 KV 506944 TO WEDINGTON 161.0 KV 506992 CKT 1, b. with stuck breaker near CHAMSPR5 161 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CHAMSPR5 161.0 KV 506944 TO TONTITN5 161.0 KV 506957 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHAMSPR5_506945 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5( 506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 506944 TO CHAMSPR7 506945 TO CHAMSPR1 506919 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHAMSPR5_506945 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5( 506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 506944 TO CHAMSPR7 506945 TO CHAMSPR1 506919 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHAMSPR5_GEN_2017_076_7 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 161.0 KV 506944 TO GEN-2017-076 161.0 KV 589140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHAMSPR5_GEN_2017_076_7 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 161.0 KV 506944 TO GEN-2017-076 161.0 KV 589140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHAMSPR5_SILOAM_5 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 161.0 KV 506944 TO SILOAM 5 161.0 KV 506948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHAMSPR5_SILOAM_5 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 161.0 KV 506944 TO SILOAM 5 161.0 KV 506948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHAMSPR5_TONTITN5 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 161.0 KV 506944 TO TONTITN5 161.0 KV 506957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHAMSPR5_TONTITN5 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 161.0 KV 506944 TO TONTITN5 161.0 KV 506957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHAMSPR5_WEDINGTON_7 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 161.0 KV 506944 TO WEDINGTON 161.0 KV 506992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHAMSPR5_WEDINGTON_7 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5 (506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 161.0 KV 506944 TO WEDINGTON 161.0 KV 506992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHAMSPR7_CLARKSV7_6 | 3 Phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO CLARKSV7 345.0 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHAMSPR7_CLARKSV7_6 | 3 Phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO CLARKSV7 345.0 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHAMSPR7_TONTITN7_6 | 3 Phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO TONTITN7 345.0 KV 506959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHAMSPR7_TONTITN7_6 | 3 Phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO TONTITN7 345.0 KV 506959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHEEKTP4_CHEEK_4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHEEKTP4_CHEEK_4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHEEKTP4 138.0 KV 515415 TO CHEEK_4 138.0 KV 521125 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHEEKTP4_HLTNTAP4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138.0 KV 515142 TO WOLFCRK4 138.0 KV 515143 CKT 1 b.2. LOAD 1 515143 b.3. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 b.4. HLTNTAP4 138.0 KV 515141 TO DILLARD4 138.0 KV 515142 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHEEKTP4_HLTNTAP4 | 3 Phase fault on CHEEKTP4 (515415) 138 kV Bus a. Apply fault at the CHEEKTP4 (515415) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DILLARD4 138.0 KV 515142 TO WOLFCRK4 138.0 KV 515143 CKT 1 b.2. LOAD 1 515143 b.3. WOLFCRK4 138.0 KV 515143 TO CHEEKTP4 138.0 KV 515415 CKT 1 b.4. HLTNTAP4 138.0 KV 515141 TO DILLARD4 138.0 KV 515142 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHIKSAW2_515171 | 3 Phase fault on CHIKSAW2 (515170) 69 kV Bus a. Apply fault at the CHIKSAW2( 515170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKSAW2 515170 TO CHIKSAW4 515171 TO CHIKSA21 515711 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHIKSAW2_515171 | 3 Phase fault on CHIKSAW2 (515170) 69 kV Bus a. Apply fault at the CHIKSAW2( 515170) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHIKSAW2 515170 TO CHIKSAW4 515171 TO CHIKSA21 515711 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHSHLMV7_515479 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVE1 515479 TO CHSHMVET 515482 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHSHLMV7_515479 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVE1 515479 TO CHSHMVET 515482 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CHSHLMV7_515484 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVW1 515484 TO CHSHMVWT 515485 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CHSHLMV7_515484 | 3 Phase fault on CHSHLMV7 (515477) 345 kV Bus a. Apply fault at the CHSHLMV7( 515477) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHSHLMV7 515477 TO CHSHMVW1 515484 TO CHSHMVWT 515485 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CIMARON4_514901 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-178 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CIMARON4_514901 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CIMARON4_DVISION4 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO HAYMAKR4 138.0 KV 514863 CKT 1 b.2. LOAD 1 514863 b.3. HAYMAKR4 138.0 KV 514863 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CIMARON4_DVISION4 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO HAYMAKR4 138.0 KV 514863 CKT 1 b.2. LOAD 1 514863 b.3. HAYMAKR4 138.0 KV 514863 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CIMARON7_514901 | a. Apply single-phase fault on: a.1. NSUB345 345.0 KV 555234 TO CIMARON7 345.0 KV 514901 CKT 1, b. with stuck breaker near CIMARON7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. CIMARON7 345.0 KV 514901 TO MINCO 7 345.0 KV 514801 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CIMARON7_514901 | a. Apply single-phase fault on: a.1. NSUB345 345.0 KV 555234 TO CIMARON7 345.0 KV 514901 CKT 1, b. with stuck breaker near CIMARON7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. CIMARON7 345.0 KV 514901 TO MINCO 7 345.0 KV 514801 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-178 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CIMARON7_FSHRTAP7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CIMARON7_FSHRTAP7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CIMARON7_MATHWSN7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CIMARON7_MATHWSN7_6 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CIMARON7_NSUB345 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CIMARON7_NSUB345 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLARKSV5_LSPADRA5 | 3 Phase fault on CLARKSV5 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 161.0 KV 505514 TO LSPADRA5 161.0 KV 515319 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLARKSV5_LSPADRA5 | 3 Phase fault on CLARKSV5 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 161.0 KV 505514 TO LSPADRA5 161.0 KV 515319 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLARKSV5_OZARK_H5 | 3 Phase fault on CLARKSV5 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 161.0 KV 505514 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLARKSV5_OZARK_H5 | 3 Phase fault on CLARKSV5 (505514) 161 kV Bus a. Apply fault at the CLARKSV5 (505514) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARKSV5 161.0 KV 505514 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLARKSV7_509745 | a. Apply single-phase fault on: a.1. CLARKSV7 345.0 KV 509745 TO CHAMSPR7 345.0 KV 506945 CKT 1, b. with stuck breaker near CLARKSV7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLARKSV7_509745 | a. Apply single-phase fault on: a.1. CLARKSV7 345.0 KV 509745 TO CHAMSPR7 345.0 KV 506945 CKT 1, b. with stuck breaker near CLARKSV7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | No | Yes | Yes | High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLARKSV7_GEN_2017_140 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-140 345.0 KV 760389 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLARKSV7_GEN_2017_140 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-140 345.0 KV 760389 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLARKSV7_MUSKOGE7_6 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLARKSV7_MUSKOGE7_6 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLARKSV7_ONETA_7_6 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLARKSV7_ONETA_7_6 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLDWELL4_MILAN_GOAB | 3 Phase fault on CLDWELL4 (539003) 138 kV Bus a. Apply fault at the CLDWELL4 (539003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLDWELL4 138.0 KV 539003 TO MILAN_GOAB 138.0 KV 539008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLDWELL4_MILAN_GOAB | 3 Phase fault on CLDWELL4 (539003) 138 kV Bus a. Apply fault at the CLDWELL4 (539003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLDWELL4 138.0 KV 539003 TO MILAN_GOAB 138.0 KV 539008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLEARWT4_GILL_4 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 138.0 KV 533036 TO GILL 4 138.0 KV 533047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLEARWT4_GILL_4 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 138.0 KV 533036 TO GILL 4 138.0 KV 533047 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLEARWT4_VIOLA_4 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 138.0 KV 533036 TO VIOLA 4 138.0 KV 533075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLEARWT4_VIOLA_4 | 3 Phase fault on CLEARWT4 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 138.0 KV 533036 TO VIOLA 4 138.0 KV 533075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLEVLND7_512729 | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7( 512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLEVLND7_512729 | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7( 512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 512694 TO CLEVLND 4 512729 TO CLEVLND1 512817 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLEVLND7_G15_066T | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLEVLND7_G15_066T | 3 Phase fault on CLEVLND7 (512694) 345 kV Bus a. Apply fault at the CLEVLND7 (512694) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLEVLND7 345.0 KV 512694 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLVLDSW4_520508 | a. Apply single-phase fault on: a.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1, b. with stuck breaker near CLVLDSW4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLVLDSW4_520508 | a. Apply single-phase fault on: a.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1, b. with stuck breaker near CLVLDSW4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLVLDSW4_AMBERTP4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLVLDSW4_AMBERTP4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CLVLDSW4_ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CLVLDSW4_ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CMBLCRK4_CMBLTP_4 | 3 Phase fault on CMBLCRK4 (515930) 138 kV Bus a. Apply fault at the CMBLCRK4 (515930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138.0 KV 515930 TO CMBLTP 4 138.0 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CMBLCRK4_CMBLTP_4 | 3 Phase fault on CMBLCRK4 (515930) 138 kV Bus a. Apply fault at the CMBLCRK4 (515930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138.0 KV 515930 TO CMBLTP 4 138.0 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CMBLTP_4_FOURCTP4 | 3 Phase fault on CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO FOURCTP4 138.0 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CMBLTP_4_FOURCTP4 | 3 Phase fault on CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO FOURCTP4 138.0 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COALGAT4_COALGTP4 | 3 Phase fault on COALGAT4 (510862) 138 kV Bus a. Apply fault at the COALGAT4 (510862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGAT4 138.0 KV 510862 TO COALGTP4 138.0 KV 510880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COALGAT4_COALGTP4 | 3 Phase fault on COALGAT4 (510862) 138 kV Bus a. Apply fault at the COALGAT4 (510862) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGAT4 138.0 KV 510862 TO COALGTP4 138.0 KV 510880 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COALGTP4_ALLENGT4 | 3 Phase fault on COALGTP4 (510880) 138 kV Bus a. Apply fault at the COALGTP4 (510880) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COALGTP4_ALLENGT4 | 3 Phase fault on COALGTP4 (510880) 138 kV Bus a. Apply fault at the COALGTP4 (510880) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COALGTP4 138.0 KV 510880 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COALGTP4_LEHIGH4 | 3 Phase fault on COALGTP4 (510880) 138 kV Bus a. Apply fault at the COALGTP4 (510880) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO LEHIGH-4 138.0 KV 510895 CKT 1 b.2. LOAD 1 510895 b.3. COALGTP4 138.0 KV 510880 TO LEHIGH-4 138.0 KV 510895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COALGTP4_LEHIGH4 | 3 Phase fault on COALGTP4 (510880) 138 kV Bus a. Apply fault at the COALGTP4 (510880) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATOKA--4 138.0 KV 510887 TO LEHIGH-4 138.0 KV 510895 CKT 1 b.2. LOAD 1 510895 b.3. COALGTP4 138.0 KV 510880 TO LEHIGH-4 138.0 KV 510895 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COLBERT4_YUBA4 | 3 Phase fault on COLBERT4 (520860) 138 kV Bus a. Apply fault at the COLBERT4 (520860) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAWAY4 138.0 KV 520426 TO COLBERT4 138.0 KV 520860 CKT 1 b.2. LOAD 1 520860 b.3. SEAWAY4 138.0 KV 520426 TO TXI4 138.0 KV 520427 CKT 1 b.4. LOAD 1 520427 b.5. TXI4 138.0 KV 520427 TO YUBA4 138.0 KV 520428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COLBERT4_YUBA4 | 3 Phase fault on COLBERT4 (520860) 138 kV Bus a. Apply fault at the COLBERT4 (520860) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEAWAY4 138.0 KV 520426 TO COLBERT4 138.0 KV 520860 CKT 1 b.2. LOAD 1 520860 b.3. SEAWAY4 138.0 KV 520426 TO TXI4 138.0 KV 520427 CKT 1 b.4. LOAD 1 520427 b.5. TXI4 138.0 KV 520427 TO YUBA4 138.0 KV 520428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COLBRTP4_BUTRFLD4 | 3 Phase fault on COLBRTP4 (515159) 138 kV Bus a. Apply fault at the COLBRTP4 (515159) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRTP4 138.0 KV 515159 TO BUTRFLD4 138.0 KV 515176 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COLBRTP4_BUTRFLD4 | 3 Phase fault on COLBRTP4 (515159) 138 kV Bus a. Apply fault at the COLBRTP4 (515159) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBRTP4 138.0 KV 515159 TO BUTRFLD4 138.0 KV 515176 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COLE_4_OU_SW_4 | 3 Phase fault on COLE 4 (520861) 138 kV Bus a. Apply fault at the COLE 4 (520861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138.0 KV 520861 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COLE_4_OU_SW_4 | 3 Phase fault on COLE 4 (520861) 138 kV Bus a. Apply fault at the COLE 4 (520861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLE 4 138.0 KV 520861 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COLEMNT4_EXPLRPL4 | 3 Phase fault on COLEMNT4 (515153) 138 kV Bus a. Apply fault at the COLEMNT4 (515153) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMNT4 138.0 KV 515153 TO EXPLRPL4 138.0 KV 515154 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COLEMNT4_EXPLRPL4 | 3 Phase fault on COLEMNT4 (515153) 138 kV Bus a. Apply fault at the COLEMNT4 (515153) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMNT4 138.0 KV 515153 TO EXPLRPL4 138.0 KV 515154 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COLEMNT4_STRRDTP4 | 3 Phase fault on COLEMNT4 (515153) 138 kV Bus a. Apply fault at the COLEMNT4 (515153) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMNT4 138.0 KV 515153 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COLEMNT4_STRRDTP4 | 3 Phase fault on COLEMNT4 (515153) 138 kV Bus a. Apply fault at the COLEMNT4 (515153) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLEMNT4 138.0 KV 515153 TO STRRDTP4 138.0 KV 515944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COMANC2_LE2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COMANC2_LE2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COMANC4_112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COMANC4_112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COMANC4_COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COMANC4_COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COMANC4_LE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COMANC4_LE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COMMTAP4_OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COMMTAP4_OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | COWCRK_4_WRVALLY4 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | COWCRK_4_WRVALLY4 | 3 Phase fault on COWCRK 4 (514706) 138 kV Bus a. Apply fault at the COWCRK 4 (514706) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWCRK 4 138.0 KV 514706 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CRESENT4_GEN_2016_032 | 3 Phase fault on CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO GEN-2016-032 138.0 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CRESENT4_GEN_2016_032 | 3 Phase fault on CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO GEN-2016-032 138.0 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CRESENT4_TWNLKSW4 | 3 Phase fault on CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CRESENT4_TWNLKSW4 | 3 Phase fault on CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | C-RIVER_515422 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | C-RIVER_515422 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CRIVER_FIREWHL_TAP | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CRIVER_FIREWHL_TAP | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CRIVER_TALAWANDA | 3 Phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CRIVER_TALAWANDA | 3 Phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CTNWOOD4_514827 | a. Apply single-phase fault on: a.1. ARCADIA4 138.0 KV 514907 TO CTNWOOD4 138.0 KV 514827 CKT 1, b. with stuck breaker near CTNWOOD4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c.2. LOAD 1 515373 c.3. LBRTYLK4 138.0 KV 515373 TO WATRLOO4 138.0 KV 514831 CKT 1 c.4. LOAD 1 514831 c.5. WATRLOO4 138.0 KV 514831 TO WHITESB4 138.0 KV 515467 CKT 1 c.6. LOAD 1 515467 c.7. WHITESB4 138.0 KV 515467 TO MITCHSB4 138.0 KV 515466 CKT 1 c.8. LOAD 1 515466 c.9. MITCHSB4 138.0 KV 515466 TO KETCHTP4 138.0 KV 514828 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CTNWOOD4_514827 | a. Apply single-phase fault on: a.1. ARCADIA4 138.0 KV 514907 TO CTNWOOD4 138.0 KV 514827 CKT 1, b. with stuck breaker near CTNWOOD4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c.2. LOAD 1 515373 c.3. LBRTYLK4 138.0 KV 515373 TO WATRLOO4 138.0 KV 514831 CKT 1 c.4. LOAD 1 514831 c.5. WATRLOO4 138.0 KV 514831 TO WHITESB4 138.0 KV 515467 CKT 1 c.6. LOAD 1 515467 c.7. WHITESB4 138.0 KV 515467 TO MITCHSB4 138.0 KV 515466 CKT 1 c.8. LOAD 1 515466 c.9. MITCHSB4 138.0 KV 515466 TO KETCHTP4 138.0 KV 514828 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CTNWOOD4_ARCADIA4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CTNWOOD4_ARCADIA4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CTNWOOD4_CRESENT4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CTNWOOD4_CRESENT4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CTNWOOD4_KETCHTP4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. WATRLOO4 138.0 KV 514831 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138.0 KV 514831 TO WHITESB4 138.0 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138.0 KV 515466 TO WHITESB4 138.0 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138.0 KV 514828 TO MITCHSB4 138.0 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CTNWOOD4_KETCHTP4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.2. LOAD 1 515373 b.3. WATRLOO4 138.0 KV 514831 TO LBRTYLK4 138.0 KV 515373 CKT 1 b.4. LOAD 1 515373 b.5. WATRLOO4 138.0 KV 514831 TO WHITESB4 138.0 KV 515467 CKT 1 b.6. LOAD 1 515467 b.7. MITCHSB4 138.0 KV 515466 TO WHITESB4 138.0 KV 515467 CKT 1 b.8. LOAD 1 515467 b.9. KETCHTP4 138.0 KV 514828 TO MITCHSB4 138.0 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CTNWOOD4_KINZE_4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138.0 KV 514829 TO FITZGRD4 138.0 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138.0 KV 514830 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CTNWOOD4_KINZE_4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 b.2. LOAD 1 514829 b.3. LOAD 2 514829 b.4. PINE ST4 138.0 KV 514829 TO FITZGRD4 138.0 KV 514830 CKT 1 b.5. LOAD 1 514830 b.6. FITZGRD4 138.0 KV 514830 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CUSHING2_515033 | 3 Phase fault on CUSHING2 (515032) 69 kV Bus a. Apply fault at the CUSHING2( 515032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING2 515032 TO CUSHING4 515033 TO CUSHING1 515718 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CUSHING2_515033 | 3 Phase fault on CUSHING2 (515032) 69 kV Bus a. Apply fault at the CUSHING2( 515032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING2 515032 TO CUSHING4 515033 TO CUSHING1 515718 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CUSHING4_GRNWOOD4 | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 138.0 KV 515033 TO GRNWOOD4 138.0 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CUSHING4_GRNWOOD4 | 3 Phase fault on CUSHING4 (515033) 138 kV Bus a. Apply fault at the CUSHING4 (515033) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSHING4 138.0 KV 515033 TO GRNWOOD4 138.0 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | CZECHAL4_CIMARON4 | 3 Phase fault on CZECHAL4 (514894) 138 kV Bus a. Apply fault at the CZECHAL4 (514894) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CZECHAL4 138.0 KV 514894 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | CZECHAL4_CIMARON4 | 3 Phase fault on CZECHAL4 (514894) 138 kV Bus a. Apply fault at the CZECHAL4 (514894) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CZECHAL4 138.0 KV 514894 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DANFRTH4_KETCH_4 | 3 Phase fault on DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DANFRTH4_KETCH_4 | 3 Phase fault on DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DARDANE5_CLARKSV5 | 3 Phase fault on DARDANE5 (505508) 161 kV Bus a. Apply fault at the DARDANE5 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARDANE5 161.0 KV 505508 TO CLARKSV5 161.0 KV 505514 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DARDANE5_CLARKSV5 | 3 Phase fault on DARDANE5 (505508) 161 kV Bus a. Apply fault at the DARDANE5 (505508) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DARDANE5 161.0 KV 505508 TO CLARKSV5 161.0 KV 505514 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DELWARE4_510380 | 3 Phase fault on DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4( 510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DELWARE4_510380 | 3 Phase fault on DELWARE4 (510379) 138 kV Bus a. Apply fault at the DELWARE4( 510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 510379 TO DELWARE7 510380 TO DELAWAR1 510370 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DELWARE7_NE7_6 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DELWARE7_NE7_6 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DELWARE7_NEOSHO_7_6 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO NEOSHO 7 345.0 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DELWARE7_NEOSHO_7_6 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO NEOSHO 7 345.0 KV 532793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DOVER_4_DOVERSW4 | 3 Phase fault on DOVER 4 (520879) 138 kV Bus a. Apply fault at the DOVER 4 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DOVER_4_DOVERSW4 | 3 Phase fault on DOVER 4 (520879) 138 kV Bus a. Apply fault at the DOVER 4 (520879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DOVERSW4_520881 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DOVERSW4_520881 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DOVERSW4_GEN_2016_118 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DOVERSW4_GEN_2016_118 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DOVERSW4_OKEENE_4 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DOVERSW4_OKEENE_4 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_4_514934 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4( 514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 514933 TO DRAPER 7 514934 TO DRAPER21 515792 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_4_514934 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4( 514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 514933 TO DRAPER 7 514934 TO DRAPER21 515792 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_4_BARNES_4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_4_BARNES_4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_4_GM_4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_4_GM_4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_4_MIDWEST4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_4_MIDWEST4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_4_SOONRTP4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_4_SOONRTP4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_7_514934 | a. Apply single-phase fault on: a.1. DRAPER7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 2, b. with stuck breaker near DRAPER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. DRAPER7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_7_514934 | a. Apply single-phase fault on: a.1. DRAPER7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 2, b. with stuck breaker near DRAPER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. DRAPER7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_7_NSUB345 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NSUB345 345.0 KV 555234 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_7_NSUB345 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NSUB345 345.0 KV 555234 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DRAPER_7_SEMINOL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DRAPER_7_SEMINOL7_6 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DUNDEE_4_HLTNTAP4 | 3 Phase fault on DUNDEE 4 (515132) 138 kV Bus a. Apply fault at the DUNDEE 4 (515132) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNDEE 4 138.0 KV 515132 TO HLTNTAP4 138.0 KV 515141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DUNDEE_4_HLTNTAP4 | 3 Phase fault on DUNDEE 4 (515132) 138 kV Bus a. Apply fault at the DUNDEE 4 (515132) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNDEE 4 138.0 KV 515132 TO HLTNTAP4 138.0 KV 515141 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DUNJEE_4_HSL_4 | 3 Phase fault on DUNJEE 4 (514884) 138 kV Bus a. Apply fault at the DUNJEE 4 (514884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DUNJEE_4_HSL_4 | 3 Phase fault on DUNJEE 4 (514884) 138 kV Bus a. Apply fault at the DUNJEE 4 (514884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 138.0 KV 514884 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DURANT_4_DURANTP4 | 3 Phase fault on DURANT 4 (520483) 138 kV Bus a. Apply fault at the DURANT 4 (520483) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANT 4 138.0 KV 520483 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DURANT_4_DURANTP4 | 3 Phase fault on DURANT 4 (520483) 138 kV Bus a. Apply fault at the DURANT 4 (520483) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANT 4 138.0 KV 520483 TO DURANTP4 138.0 KV 520884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DURANTP4_SCLMNJC4 | 3 Phase fault on DURANTP4 (520884) 138 kV Bus a. Apply fault at the DURANTP4 (520884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANTP4 138.0 KV 520884 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DURANTP4_SCLMNJC4 | 3 Phase fault on DURANTP4 (520884) 138 kV Bus a. Apply fault at the DURANTP4 (520884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DURANTP4 138.0 KV 520884 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DVISION4_MUSTANG4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO MUSTANG4 138.0 KV 514861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DVISION4_MUSTANG4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO MUSTANG4 138.0 KV 514861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DVISION4_RICHRDS4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO RICHRDS4 138.0 KV 514862 CKT 1 b.2. LOAD 1 514862 b.3. RICHRDS4 138.0 KV 514862 TO PIEDMNT4 138.0 KV 514864 CKT 1 b.4. LOAD 1 514864 b.5. PIEDMNT4 138.0 KV 514864 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DVISION4_RICHRDS4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO RICHRDS4 138.0 KV 514862 CKT 1 b.2. LOAD 1 514862 b.3. RICHRDS4 138.0 KV 514862 TO PIEDMNT4 138.0 KV 514864 CKT 1 b.4. LOAD 1 514864 b.5. PIEDMNT4 138.0 KV 514864 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | DYESS_5_TONTITN5 | 3 Phase fault on DYESS 5 (506927) 161 kV Bus a. Apply fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DYESS 5 161.0 KV 506927 TO TONTITN5 161.0 KV 506957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | DYESS_5_TONTITN5 | 3 Phase fault on DYESS 5 (506927) 161 kV Bus a. Apply fault at the DYESS 5 (506927) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DYESS 5 161.0 KV 506927 TO TONTITN5 161.0 KV 506957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EARLSBORO_4_MAUD_4 | 3 Phase fault on EARLSBORO 4 (510948) 138 kV Bus a. Apply fault at the EARLSBORO 4 (510948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138.0 KV 510948 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EARLSBORO_4_MAUD_4 | 3 Phase fault on EARLSBORO 4 (510948) 138 kV Bus a. Apply fault at the EARLSBORO 4 (510948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138.0 KV 510948 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EASTERN4_MEMRIAL4 | 3 Phase fault on EASTERN4 (514832) 138 kV Bus a. Apply fault at the EASTERN4 (514832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.2. LOAD 1 515469 b.3. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EASTERN4_MEMRIAL4 | 3 Phase fault on EASTERN4 (514832) 138 kV Bus a. Apply fault at the EASTERN4 (514832) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.2. LOAD 1 515469 b.3. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EFITSTP4_EFITTS_4 | 3 Phase fault on EFITSTP4 (515699) 138 kV Bus a. Apply fault at the EFITSTP4 (515699) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EFITSTP4 138.0 KV 515699 TO EFITTS 4 138.0 KV 515809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EFITSTP4_EFITTS_4 | 3 Phase fault on EFITSTP4 (515699) 138 kV Bus a. Apply fault at the EFITSTP4 (515699) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EFITSTP4 138.0 KV 515699 TO EFITTS 4 138.0 KV 515809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EKNGFSH4_EKFSHTP4 | 3 Phase fault on EKNGFSH4 (520484) 138 kV Bus a. Apply fault at the EKNGFSH4 (520484) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138.0 KV 520484 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EKNGFSH4_EKFSHTP4 | 3 Phase fault on EKNGFSH4 (520484) 138 kV Bus a. Apply fault at the EKNGFSH4 (520484) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138.0 KV 520484 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EL_RENO4_520893 | a. Apply single-phase fault on: a.1. EL RENO4 138.0 KV 520893 TO MUSTANG4 138.0 KV 520412 CKT 1 a.2. LOAD 1 520412 a.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 a.4. LOAD 1 521005 a.5. SUNSHIN4 138.0 KV 521059 TO SARA RD4 138.0 KV 521005 CKT 1, b. with stuck breaker near EL RENO4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. EL RENO4 138.0 KV 520893 TO SCOTTSW4 138.0 KV 520899 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EL_RENO4_520893 | a. Apply single-phase fault on: a.1. EL RENO4 138.0 KV 520893 TO MUSTANG4 138.0 KV 520412 CKT 1 a.2. LOAD 1 520412 a.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 a.4. LOAD 1 521005 a.5. SUNSHIN4 138.0 KV 521059 TO SARA RD4 138.0 KV 521005 CKT 1, b. with stuck breaker near EL RENO4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. EL RENO4 138.0 KV 520893 TO SCOTTSW4 138.0 KV 520899 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EL_RENO4_GEN_2017_117_7 | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO GEN-2017-117 138.0 KV 588720 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EL_RENO4_GEN_2017_117_7 | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO GEN-2017-117 138.0 KV 588720 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EL_RENO4_SCOTTSW4 | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EL_RENO4_SCOTTSW4 | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL RENO4 138.0 KV 520893 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EL_RENO4_SUNSHIN4 | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 b.2. LOAD 1 520893 b.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.4. LOAD 1 521005 b.5. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EL_RENO4_SUNSHIN4 | 3 Phase fault on EL RENO4 (520893) 138 kV Bus a. Apply fault at the EL RENO4 (520893) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 520412 TO EL RENO4 138.0 KV 520893 CKT 1 b.2. LOAD 1 520893 b.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 b.4. LOAD 1 521005 b.5. SARA RD4 138.0 KV 521005 TO SUNSHIN4 138.0 KV 521059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ELGINJT2_511486_7 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ELGINJT2_511486_7 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ELGINJT4_ELSWORTH_4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ELGINJT4_ELSWORTH_4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ELMSPRGS_5_TONTITN5 | 3 Phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMSPRGS 5 161.0 KV 504010 TO TONTITN5 161.0 KV 506957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ELMSPRGS_5_TONTITN5 | 3 Phase fault on ELMSPRGS 5 (504010) 161 kV Bus a. Apply fault at the ELMSPRGS 5 (504010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELMSPRGS 5 161.0 KV 504010 TO TONTITN5 161.0 KV 506957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ELRENO__CIMARON | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ELRENO__CIMARON | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ELRENO__JENSENT4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ELRENO__JENSENT4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ELRENO__OMEGA4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ELRENO__OMEGA4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ELRENO_2_514819 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ELRENO_2_514819 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EMPEC_7_EXPEDITION7_6 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 345.0 KV 532768 TO EXPEDITION7 345.0 KV 532803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EMPEC_7_EXPEDITION7_6 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 345.0 KV 532768 TO EXPEDITION7 345.0 KV 532803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EMPEC_7_G14 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 345.0 KV 532768 TO G14-001-TAP 345.0 KV 562476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EMPEC_7_G14 | 3 Phase fault on EMPEC 7 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 345.0 KV 532768 TO G14-001-TAP 345.0 KV 562476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EVANS_N4_EVANS_S4 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO EVANS S4 138.0 KV 533041 CKT Z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EVANS_N4_EVANS_S4 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO EVANS S4 138.0 KV 533041 CKT Z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EVANS_N4_GEN_2017_068 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO GEN-2017-068 138.0 KV 589060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EVANS_N4_GEN_2017_068 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO GEN-2017-068 138.0 KV 589060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EVANS_N4_GEN_2017_226_7 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO GEN-2017-226 138.0 KV 760641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EVANS_N4_GEN_2017_226_7 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO GEN-2017-226 138.0 KV 760641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EVANS_N4_MAIZE_4 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO MAIZE 4 138.0 KV 533054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EVANS_N4_MAIZE_4 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO MAIZE 4 138.0 KV 533054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EVANS_N4_SG12COL4 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO SG12COL4 138.0 KV 533065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EVANS_N4_SG12COL4 | 3 Phase fault on EVANS N4 (533040) 138 kV Bus a. Apply fault at the EVANS N4 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 138.0 KV 533040 TO SG12COL4 138.0 KV 533065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EXPCOLT4_EXPCOLG4 | 3 Phase fault on EXPCOLT4 (510935) 138 kV Bus a. Apply fault at the EXPCOLT4 (510935) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPCOLT4 138.0 KV 510935 TO EXPCOLG4 138.0 KV 510936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EXPCOLT4_EXPCOLG4 | 3 Phase fault on EXPCOLT4 (510935) 138 kV Bus a. Apply fault at the EXPCOLT4 (510935) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPCOLT4 138.0 KV 510935 TO EXPCOLG4 138.0 KV 510936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EXPED_WF7_EXPEDITION7_6 | 3 Phase fault on EXPED WF7 (532790) 345 kV Bus a. Apply fault at the EXPED WF7 (532790) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EXPED WF7 345.0 KV 532790 TO EXPEDITION7 345.0 KV 532803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EXPED_WF7_EXPEDITION7_6 | 3 Phase fault on EXPED WF7 (532790) 345 kV Bus a. Apply fault at the EXPED WF7 (532790) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EXPED WF7 345.0 KV 532790 TO EXPEDITION7 345.0 KV 532803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EXPLOR_4_ALLEN_4 | 3 Phase fault on EXPLOR 4 (505596) 138 kV Bus a. Apply fault at the EXPLOR 4 (505596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLOR 4 138.0 KV 505596 TO ALLEN 4 138.0 KV 505598 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EXPLOR_4_ALLEN_4 | 3 Phase fault on EXPLOR 4 (505596) 138 kV Bus a. Apply fault at the EXPLOR 4 (505596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLOR 4 138.0 KV 505596 TO ALLEN 4 138.0 KV 505598 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | EXPLOR_4_HOLDEXP4 | 3 Phase fault on EXPLOR 4 (505596) 138 kV Bus a. Apply fault at the EXPLOR 4 (505596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLOR 4 138.0 KV 505596 TO HOLDEXP4 138.0 KV 510884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | EXPLOR_4_HOLDEXP4 | 3 Phase fault on EXPLOR 4 (505596) 138 kV Bus a. Apply fault at the EXPLOR 4 (505596) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLOR 4 138.0 KV 505596 TO HOLDEXP4 138.0 KV 510884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FARMNGTN_5_WEDINGTON_7 | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 161.0 KV 504020 TO WEDINGTON 161.0 KV 506992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FARMNGTN_5_WEDINGTON_7 | 3 Phase fault on FARMNGTN 5 (504020) 161 kV Bus a. Apply fault at the FARMNGTN 5 (504020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARMNGTN 5 161.0 KV 504020 TO WEDINGTON 161.0 KV 506992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FAY_4_WATONGA4 | 3 Phase fault on FAY 4 (520538) 138 kV Bus a. Apply fault at the FAY 4 (520538) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAY 4 138.0 KV 520538 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FAY_4_WATONGA4 | 3 Phase fault on FAY 4 (520538) 138 kV Bus a. Apply fault at the FAY 4 (520538) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAY 4 138.0 KV 520538 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FITZHUGH_5_ALTUS | 3 Phase fault on FITZHUGH 5 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO ALTUS 161.0 KV 515352 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FITZHUGH_5_ALTUS | 3 Phase fault on FITZHUGH 5 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO ALTUS 161.0 KV 515352 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FITZHUGH_5_HELBERG5 | 3 Phase fault on FITZHUGH 5 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO HELBERG5 161.0 KV 515327 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FITZHUGH_5_HELBERG5 | 3 Phase fault on FITZHUGH 5 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO HELBERG5 161.0 KV 515327 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FITZHUGH_5_OZARK_H5 | 3 Phase fault on FITZHUGH 5 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FITZHUGH_5_OZARK_H5 | 3 Phase fault on FITZHUGH 5 (503902) 161 kV Bus a. Apply fault at the FITZHUGH 5 (503902) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FITZHUGH 5 161.0 KV 503902 TO OZARK H5 161.0 KV 505516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FLE_TAP4_G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FLE_TAP4_G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FLE_TAP4_LE4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FLE_TAP4_LE4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FLETCHR4_FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FLETCHR4_FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FLINTCR5_SILOAM_5 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO SILOAM 5 161.0 KV 506948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FLINTCR5_SILOAM_5 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO SILOAM 5 161.0 KV 506948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FLINTCR5_TONTITN5 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO TONTITN5 161.0 KV 506957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FLINTCR5_TONTITN5 | 3 Phase fault on FLINTCR5 (506934) 161 kV Bus a. Apply fault at the FLINTCR5 (506934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLINTCR5 161.0 KV 506934 TO TONTITN5 161.0 KV 506957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FNDTION4_CHIKSAW4 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FNDTION4_CHIKSAW4 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FNDTION4_SPRNDAL4 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FNDTION4_SPRNDAL4 | 3 Phase fault on FNDTION4 (515162) 138 kV Bus a. Apply fault at the FNDTION4 (515162) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FR2EAST7__G16_153_TAP | 3 Phase fault on FR2EAST7 (532792) 345 kV Bus a. Apply fault at the FR2EAST7 (532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 345.0 KV 532792 TO G16-153-TAP 345.0 KV 588364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FR2EAST7__G16_153_TAP | 3 Phase fault on FR2EAST7 (532792) 345 kV Bus a. Apply fault at the FR2EAST7 (532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 345.0 KV 532792 TO G16-153-TAP 345.0 KV 588364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FR2EAST7_533131 | 3 Phase fault on FR2EAST7 (532792) 345 kV Bus a. Apply fault at the FR2EAST7( 532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 532792 TO FR2ELV11 533131 TO F2EAST11 533127 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FR2EAST7_533131 | 3 Phase fault on FR2EAST7 (532792) 345 kV Bus a. Apply fault at the FR2EAST7( 532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 532792 TO FR2ELV11 533131 TO F2EAST11 533127 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FR2EAST7_533132 | 3 Phase fault on FR2EAST7 (532792) 345 kV Bus a. Apply fault at the FR2EAST7( 532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 532792 TO FR2ELV21 533132 TO F2EAST21 533128 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FR2EAST7_533132 | 3 Phase fault on FR2EAST7 (532792) 345 kV Bus a. Apply fault at the FR2EAST7( 532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 532792 TO FR2ELV21 533132 TO F2EAST21 533128 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FR2EAST7_FR2WEST7_6 | 3 Phase fault on FR2EAST7 (532792) 345 kV Bus a. Apply fault at the FR2EAST7 (532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 345.0 KV 532792 TO FR2WEST7 345.0 KV 532795 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FR2EAST7_FR2WEST7_6 | 3 Phase fault on FR2EAST7 (532792) 345 kV Bus a. Apply fault at the FR2EAST7 (532792) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2EAST7 345.0 KV 532792 TO FR2WEST7 345.0 KV 532795 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FR2WEST7_533133 | 3 Phase fault on FR2WEST7 (532795) 345 kV Bus a. Apply fault at the FR2WEST7( 532795) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2WEST7 532795 TO FR2WLV11 533133 TO F2WEST11 533129 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FR2WEST7_533133 | 3 Phase fault on FR2WEST7 (532795) 345 kV Bus a. Apply fault at the FR2WEST7( 532795) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2WEST7 532795 TO FR2WLV11 533133 TO F2WEST11 533129 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FR2WEST7_533134 | 3 Phase fault on FR2WEST7 (532795) 345 kV Bus a. Apply fault at the FR2WEST7( 532795) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2WEST7 532795 TO FR2WLV21 533134 TO F2WEST21 533130 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FR2WEST7_533134 | 3 Phase fault on FR2WEST7 (532795) 345 kV Bus a. Apply fault at the FR2WEST7( 532795) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2WEST7 532795 TO FR2WLV21 533134 TO F2WEST21 533130 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FR2WEST7_FR3HV | 3 Phase fault on FR2WEST7 (532795) 345 kV Bus a. Apply fault at the FR2WEST7 (532795) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2WEST7 345.0 KV 532795 TO FR3HV 345.0 KV 578530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FR2WEST7_FR3HV | 3 Phase fault on FR2WEST7 (532795) 345 kV Bus a. Apply fault at the FR2WEST7 (532795) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FR2WEST7 345.0 KV 532795 TO FR3HV 345.0 KV 578530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FRANKLN4_FRNKLNS4 | 3 Phase fault on FRANKLN4 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138.0 KV 520913 TO FRNKLNS4 138.0 KV 520917 CKT 1 b.2. FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FRANKLN4_FRNKLNS4 | 3 Phase fault on FRANKLN4 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138.0 KV 520913 TO FRNKLNS4 138.0 KV 520917 CKT 1 b.2. FRANKLN4 138.0 KV 520913 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FRMNTAP4_BRECKNR4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.2. LOAD 1 515641 b.3. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.4. LOAD 1 514712 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FRMNTAP4_BRECKNR4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.2. LOAD 1 515641 b.3. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.4. LOAD 1 514712 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FRMNTAP4_SO4TH_4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FRMNTAP4_SO4TH_4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FRMNTAP4_WOODRNG4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FRMNTAP4_WOODRNG4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FRNKLNS4_520916_7 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4( 520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 520917 TO FRNKLNS2 520916 TO FRNKTERT 521169 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FRNKLNS4_520916_7 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4( 520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 520917 TO FRNKLNS2 520916 TO FRNKTERT 521169 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FRNKLNS4_520917 | a. Apply single-phase fault on: a.1. FRNKLNS4 138.0 KV 520917 TO MIDWEST4 138.0 KV 514946 CKT 1, b. with stuck breaker near FRNKLNS4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. FRNKLNS4 138.0 KV 520917 TO ACME 4 138.0 KV 520802 CKT 1 c.2. LOAD 1 520802 c.3. ACME 4 138.0 KV 520802 TO WNORMAN4 138.0 KV 521095 CKT 1 c.4. LOAD 1 521095 c.5. WNORMAN4 138.0 KV 521095 TO LAMAR4 138.0 KV 520403 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FRNKLNS4_520917 | a. Apply single-phase fault on: a.1. FRNKLNS4 138.0 KV 520917 TO MIDWEST4 138.0 KV 514946 CKT 1, b. with stuck breaker near FRNKLNS4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. FRNKLNS4 138.0 KV 520917 TO ACME 4 138.0 KV 520802 CKT 1 c.2. LOAD 1 520802 c.3. ACME 4 138.0 KV 520802 TO WNORMAN4 138.0 KV 521095 CKT 1 c.4. LOAD 1 521095 c.5. WNORMAN4 138.0 KV 521095 TO LAMAR4 138.0 KV 520403 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FRNKLNS4_CANADNS4 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 138.0 KV 520400 TO LIDDELL4 138.0 KV 520975 CKT 1 b.2. LOAD 1 520975 b.3. FRNKLNS4 138.0 KV 520917 TO LIDDELL4 138.0 KV 520975 CKT 1 b.4. LOAD 1 520975 b.5. NOBLE4 138.0 KV 520400 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FRNKLNS4_CANADNS4 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOBLE4 138.0 KV 520400 TO LIDDELL4 138.0 KV 520975 CKT 1 b.2. LOAD 1 520975 b.3. FRNKLNS4 138.0 KV 520917 TO LIDDELL4 138.0 KV 520975 CKT 1 b.4. LOAD 1 520975 b.5. NOBLE4 138.0 KV 520400 TO CANADNS4 138.0 KV 520842 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FRNKLNS4_OU_SW_4 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 138.0 KV 520802 TO FRNKLNS4 138.0 KV 520917 CKT 1 b.2. ACME 4 138.0 KV 520802 TO WNORMAN4 138.0 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. LAMAR4 138.0 KV 520403 TO WNORMAN4 138.0 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. LAMAR4 138.0 KV 520403 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FRNKLNS4_OU_SW_4 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 138.0 KV 520802 TO FRNKLNS4 138.0 KV 520917 CKT 1 b.2. ACME 4 138.0 KV 520802 TO WNORMAN4 138.0 KV 521095 CKT 1 b.3. LOAD 1 521095 b.4. LAMAR4 138.0 KV 520403 TO WNORMAN4 138.0 KV 521095 CKT 1 b.5. LOAD 1 521095 b.6. LAMAR4 138.0 KV 520403 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FTSMITH7_515305 | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7( 515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FTSMITH7_515305 | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7( 515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FTSMTHE5_515305 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5( 515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FTSMTHE5_515305 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5( 515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FTSMTHE5_COLONY_5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO COLONY 5 161.0 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FTSMTHE5_COLONY_5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO COLONY 5 161.0 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FTSMTHE5_FTSMTHW5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FTSMTHE5_FTSMTHW5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FTSMTHE5_QUANXTP5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FTSMTHE5_QUANXTP5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FTSMTHW5_515302 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5( 515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FTSMTHW5_515302 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5( 515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FTSMTHW5_515305 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5( 515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FTSMTHW5_515305 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5( 515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | FTSMTHW5_ARKOMA_5 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161.0 KV 515301 TO ARKOMA 5 161.0 KV 515306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | FTSMTHW5_ARKOMA_5 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161.0 KV 515301 TO ARKOMA 5 161.0 KV 515306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | G15_066T_GEN_2015_066_6 | 3 Phase fault on G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | G15_066T_GEN_2015_066_6 | 3 Phase fault on G15-066T (560056) 345 kV Bus a. Apply fault at the G15-066T (560056) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G15-066T 345.0 KV 560056 TO GEN-2015-066 345.0 KV 585040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | G16133G16146_G16133_345GS | 3 Phase fault on G16133G16146 (588039) 345 kV Bus a. Apply fault at the G16133G16146 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 345.0 KV 588039 TO G16133_345GS 345.0 KV 588040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | G16133G16146_G16133_345GS | 3 Phase fault on G16133G16146 (588039) 345 kV Bus a. Apply fault at the G16133G16146 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 345.0 KV 588039 TO G16133_345GS 345.0 KV 588040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | G17_151TAP_GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | G17_151TAP_GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GEN_2016_091_G16_091 | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GEN_2016_091_G16_091 | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GEN_2017_140_G17_140 | 3 Phase fault on GEN-2017-140 (760389) 345 kV Bus a. Apply fault at the GEN-2017-140 (760389) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-140 345.0 KV 760389 TO G17-140-345.0 KV 760393 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GEN_2017_140_G17_140 | 3 Phase fault on GEN-2017-140 (760389) 345 kV Bus a. Apply fault at the GEN-2017-140 (760389) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-140 345.0 KV 760389 TO G17-140-345.0 KV 760393 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GEN_2017_149_GEN_2017_154 | 3 Phase fault on GEN-2017-149 (760830) 345 kV Bus a. Apply fault at the GEN-2017-149 (760830) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-149 345.0 KV 760830 TO GEN-2017-154 345.0 KV 760851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GEN_2017_149_GEN_2017_154 | 3 Phase fault on GEN-2017-149 (760830) 345 kV Bus a. Apply fault at the GEN-2017-149 (760830) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-149 345.0 KV 760830 TO GEN-2017-154 345.0 KV 760851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GERBRTP5_NALCOTP5 | 3 Phase fault on GERBRTP5 (515326) 161 kV Bus a. Apply fault at the GERBRTP5 (515326) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO NALCOTP5 161.0 KV 515348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GERBRTP5_NALCOTP5 | 3 Phase fault on GERBRTP5 (515326) 161 kV Bus a. Apply fault at the GERBRTP5 (515326) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GERBRTP5 161.0 KV 515326 TO NALCOTP5 161.0 KV 515348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GILL_4_VIOLA_4 | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 138.0 KV 533047 TO VIOLA 4 138.0 KV 533075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GILL_4_VIOLA_4 | 3 Phase fault on GILL 4 (533047) 138 kV Bus a. Apply fault at the GILL 4 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 138.0 KV 533047 TO VIOLA 4 138.0 KV 533075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GILL_S_4_GILL_4 | 3 Phase fault on GILL S 4 (533046) 138 kV Bus a. Apply fault at the GILL S 4 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 138.0 KV 533046 TO GILL 4 138.0 KV 533047 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GILL_S_4_GILL_4 | 3 Phase fault on GILL S 4 (533046) 138 kV Bus a. Apply fault at the GILL S 4 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 138.0 KV 533046 TO GILL 4 138.0 KV 533047 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GILL_W_4_GILL_4 | 3 Phase fault on GILL W 4 (533045) 138 kV Bus a. Apply fault at the GILL W 4 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 138.0 KV 533045 TO GILL 4 138.0 KV 533047 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GILL_W_4_GILL_4 | 3 Phase fault on GILL W 4 (533045) 138 kV Bus a. Apply fault at the GILL W 4 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 138.0 KV 533045 TO GILL 4 138.0 KV 533047 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GOLDSBY4_OU_SW_4 | 3 Phase fault on GOLDSBY4 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDSBY4 138.0 KV 520924 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GOLDSBY4_OU_SW_4 | 3 Phase fault on GOLDSBY4 (520924) 138 kV Bus a. Apply fault at the GOLDSBY4 (520924) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GOLDSBY4 138.0 KV 520924 TO OU SW 4 138.0 KV 521104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT4_515800 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT4_515800 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT4_ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT4_ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN units trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN units prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT7_G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT7_G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT7_G16_091 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT7_G16_091 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRACMNT7_GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRACMNT7_GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRANDPR5_GRNDPRT5 | 3 Phase fault on GRANDPR5 (504192) 161 kV Bus a. Apply fault at the GRANDPR5 (504192) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANDPR5 161.0 KV 504192 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRANDPR5_GRNDPRT5 | 3 Phase fault on GRANDPR5 (504192) 161 kV Bus a. Apply fault at the GRANDPR5 (504192) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANDPR5 161.0 KV 504192 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRANTCO2_515546_7 | 3 Phase fault on GRANTCO2 (515547) 69 kV Bus a. Apply fault at the GRANTCO2( 515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 515547 TO GRANTCO4 515546 TO GRANTC11 515548 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRANTCO2_515546_7 | 3 Phase fault on GRANTCO2 (515547) 69 kV Bus a. Apply fault at the GRANTCO2( 515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRANTCO2 515547 TO GRANTCO4 515546 TO GRANTC11 515548 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRANTCO2_HILLSDT2 | 3 Phase fault on GRANTCO2 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 69.0 KV 514719 TO GRANTCO2 69.0 KV 515547 CKT 1 b.2. CLYDE 2 69.0 KV 514719 TO 4CORNER2 69.0 KV 514736 CKT 1 b.3. LOAD 1 514736 b.4. LOAD 2 514736 b.5. 4CORNER2 69.0 KV 514736 TO HILLSDT2 69.0 KV 515638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRANTCO2_HILLSDT2 | 3 Phase fault on GRANTCO2 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLYDE 2 69.0 KV 514719 TO GRANTCO2 69.0 KV 515547 CKT 1 b.2. CLYDE 2 69.0 KV 514719 TO 4CORNER2 69.0 KV 514736 CKT 1 b.3. LOAD 1 514736 b.4. LOAD 2 514736 b.5. 4CORNER2 69.0 KV 514736 TO HILLSDT2 69.0 KV 515638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRANTCO2_NUMAOGE2 | 3 Phase fault on GRANTCO2 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 69.0 KV 514739 TO GRANTCO2 69.0 KV 515547 CKT 1 b.2. MEDFORD2 69.0 KV 514739 TO NUMAOGE2 69.0 KV 514740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRANTCO2_NUMAOGE2 | 3 Phase fault on GRANTCO2 (515547) 69 kV Bus a. Apply fault at the GRANTCO2 (515547) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD2 69.0 KV 514739 TO GRANTCO2 69.0 KV 515547 CKT 1 b.2. MEDFORD2 69.0 KV 514739 TO NUMAOGE2 69.0 KV 514740 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GREASYC4_EXPLOR_4 | 3 Phase fault on GREASYC4 (505595) 138 kV Bus a. Apply fault at the GREASYC4 (505595) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREASYC4 138.0 KV 505595 TO EXPLOR 4 138.0 KV 505596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GREASYC4_EXPLOR_4 | 3 Phase fault on GREASYC4 (505595) 138 kV Bus a. Apply fault at the GREASYC4 (505595) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GREASYC4 138.0 KV 505595 TO EXPLOR 4 138.0 KV 505596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRNWOOD4_515416_7 | 3 Phase fault on GRNWOOD4 (515417) 138 kV Bus a. Apply fault at the GRNWOOD4( 515417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD4 515417 TO GRNWOOD2 515416 TO GRNWOD11 515418 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRNWOOD4_515416_7 | 3 Phase fault on GRNWOOD4 (515417) 138 kV Bus a. Apply fault at the GRNWOOD4( 515417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD4 515417 TO GRNWOOD2 515416 TO GRNWOD11 515418 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRNWOOD4_515417 | a. Apply single-phase fault on: a.1. GRNWOOD4 138.0 KV 515417 TO CUSHING4 138.0 KV 515033 CKT 1, b. with stuck breaker near GRNWOOD4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. GRNWOOD4 138.0 KV 515417 TO BRISTOW4 138.0 KV 515035 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRNWOOD4_515417 | a. Apply single-phase fault on: a.1. GRNWOOD4 138.0 KV 515417 TO CUSHING4 138.0 KV 515033 CKT 1, b. with stuck breaker near GRNWOOD4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. GRNWOOD4 138.0 KV 515417 TO BRISTOW4 138.0 KV 515035 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | GRNWOOD4_GEN_2017_071 | 3 Phase fault on GRNWOOD4 (515417) 138 kV Bus a. Apply fault at the GRNWOOD4 (515417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD4 138.0 KV 515417 TO GEN-2017-071 138.0 KV 589090 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | GRNWOOD4_GEN_2017_071 | 3 Phase fault on GRNWOOD4 (515417) 138 kV Bus a. Apply fault at the GRNWOOD4 (515417) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWOOD4 138.0 KV 515417 TO GEN-2017-071 138.0 KV 589090 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HAMMTAP4_LINCOLN4 | 3 Phase fault on HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HAMMTAP4_LINCOLN4 | 3 Phase fault on HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HARDEN_4_EFITSTP4 | 3 Phase fault on HARDEN 4 (515362) 138 kV Bus a. Apply fault at the HARDEN 4 (515362) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARDEN 4 138.0 KV 515362 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HARDEN_4_EFITSTP4 | 3 Phase fault on HARDEN 4 (515362) 138 kV Bus a. Apply fault at the HARDEN 4 (515362) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARDEN 4 138.0 KV 515362 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HARPER_4_MILANTP4 | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 138.0 KV 539668 TO MILANTP4 138.0 KV 539675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HARPER_4_MILANTP4 | 3 Phase fault on HARPER 4 (539668) 138 kV Bus a. Apply fault at the HARPER 4 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 138.0 KV 539668 TO MILANTP4 138.0 KV 539675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HAZLTAJ2_WAKITA_2 | 3 Phase fault on HAZLTAJ2 (520938) 69 kV Bus a. Apply fault at the HAZLTAJ2 (520938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKITA 2 69.0 KV 521085 TO HAZLTAJ2 69.0 KV 520938 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HAZLTAJ2_WAKITA_2 | 3 Phase fault on HAZLTAJ2 (520938) 69 kV Bus a. Apply fault at the HAZLTAJ2 (520938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKITA 2 69.0 KV 521085 TO HAZLTAJ2 69.0 KV 520938 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HELBERG2_515327 | 3 Phase fault on HELBERG2 (515325) 69 kV Bus a. Apply fault at the HELBERG2( 515325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELBERG2 515325 TO HELBERG5 515327 TO HELBERG1 515730 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HELBERG2_515327 | 3 Phase fault on HELBERG2 (515325) 69 kV Bus a. Apply fault at the HELBERG2( 515325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HELBERG2 515325 TO HELBERG5 515327 TO HELBERG1 515730 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HELBERG2_LSPADRA2 | 3 Phase fault on HELBERG2 (515325) 69 kV Bus a. Apply fault at the HELBERG2 (515325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVECOZK2 69.0 KV 515324 TO HELBERG2 69.0 KV 515325 CKT 1 b.2. LOAD 1 515325 b.3. COALHIL2 69.0 KV 515322 TO AVECOZK2 69.0 KV 515324 CKT 1 b.4. LOAD A1 515324 b.5. LSPADRA2 69.0 KV 515320 TO COALHIL2 69.0 KV 515322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HELBERG2_LSPADRA2 | 3 Phase fault on HELBERG2 (515325) 69 kV Bus a. Apply fault at the HELBERG2 (515325) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVECOZK2 69.0 KV 515324 TO HELBERG2 69.0 KV 515325 CKT 1 b.2. LOAD 1 515325 b.3. COALHIL2 69.0 KV 515322 TO AVECOZK2 69.0 KV 515324 CKT 1 b.4. LOAD A1 515324 b.5. LSPADRA2 69.0 KV 515320 TO COALHIL2 69.0 KV 515322 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HELBERG5_NITROTP5 | 3 Phase fault on HELBERG5 (515327) 161 kV Bus a. Apply fault at the HELBERG5 (515327) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO PUDDIN 5 161.0 KV 515346 CKT 1 b.2. LOAD A1 515346 b.3. HELBERG5 161.0 KV 515327 TO PUDDIN 5 161.0 KV 515346 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HELBERG5_NITROTP5 | 3 Phase fault on HELBERG5 (515327) 161 kV Bus a. Apply fault at the HELBERG5 (515327) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO PUDDIN 5 161.0 KV 515346 CKT 1 b.2. LOAD A1 515346 b.3. HELBERG5 161.0 KV 515327 TO PUDDIN 5 161.0 KV 515346 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HENESEY4_DOVERSW4 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HENESEY4_DOVERSW4 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HIGHLND4_PINK_SW4 | 3 Phase fault on HIGHLND4 (520941) 138 kV Bus a. Apply fault at the HIGHLND4 (520941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLND4 138.0 KV 520941 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HIGHLND4_PINK_SW4 | 3 Phase fault on HIGHLND4 (520941) 138 kV Bus a. Apply fault at the HIGHLND4 (520941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGHLND4 138.0 KV 520941 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HILLSDT2_HILLSDL2 | 3 Phase fault on HILLSDT2 (515638) 69 kV Bus a. Apply fault at the HILLSDT2 (515638) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILLSDT2 69.0 KV 515638 TO HILLSDL2 69.0 KV 515639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HILLSDT2_HILLSDL2 | 3 Phase fault on HILLSDT2 (515638) 69 kV Bus a. Apply fault at the HILLSDT2 (515638) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HILLSDT2 69.0 KV 515638 TO HILLSDL2 69.0 KV 515639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HLTNTAP2_515141 | 3 Phase fault on HLTNTAP2 (515140) 69 kV Bus a. Apply fault at the HLTNTAP2( 515140) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLTNTAP2 515140 TO HLTNTAP4 515141 TO HLTNTAP1 515729 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HLTNTAP2_515141 | 3 Phase fault on HLTNTAP2 (515140) 69 kV Bus a. Apply fault at the HLTNTAP2( 515140) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HLTNTAP2 515140 TO HLTNTAP4 515141 TO HLTNTAP1 515729 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HSL_4_DALE_4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO DALE 4 138.0 KV 514987 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HSL_4_DALE_4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO DALE 4 138.0 KV 514987 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HSL_4_HAMMTAP4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HSL_4_HAMMTAP4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HSL_4_JONESSB4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HSL_4_JONESSB4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HSL_4_MIDWAY_4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO MIDWAY 4 138.0 KV 514966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HSL_4_MIDWAY_4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO MIDWAY 4 138.0 KV 514966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HSL_4_SE15TH_4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HSL_4_SE15TH_4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HSLWEST2_514941 | 3 Phase fault on HSLWEST2 (514937) 69 kV Bus a. Apply fault at the HSLWEST2( 514937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HSLWEST2_514941 | 3 Phase fault on HSLWEST2 (514937) 69 kV Bus a. Apply fault at the HSLWEST2( 514937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HUGO_7_520560 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HUGO_7_520560 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HUGO_7_G16_063 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HUGO_7_G16_063 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HUGO4_VALIANT4 | 3 Phase fault on HUGO---4 (510901) 138 kV Bus a. Apply fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---4 138.0 KV 510901 TO VALIANT4 138.0 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HUGO4_VALIANT4 | 3 Phase fault on HUGO---4 (510901) 138 kV Bus a. Apply fault at the HUGO---4 (510901) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGO---4 138.0 KV 510901 TO VALIANT4 138.0 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HUGOITC4_HUGO_PP4 | 3 Phase fault on HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138.0 KV 520560 TO HUGO PP4 138.0 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HUGOITC4_HUGO_PP4 | 3 Phase fault on HUGOITC4 (520560) 138 kV Bus a. Apply fault at the HUGOITC4 (520560) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUGOITC4 138.0 KV 520560 TO HUGO PP4 138.0 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HUNTERS7_CHSHLMV7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO CHSHLMV7 345.0 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HUNTERS7_CHSHLMV7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO CHSHLMV7 345.0 KV 515477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HUNTERS7_RENFROW7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HUNTERS7_RENFROW7_6 | 3 Phase fault on HUNTERS7 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HWY59_5_HWY59TP5 | 3 Phase fault on HWY59 5 (504191) 161 kV Bus a. Apply fault at the HWY59 5 (504191) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY59 5 161.0 KV 504191 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HWY59_5_HWY59TP5 | 3 Phase fault on HWY59 5 (504191) 161 kV Bus a. Apply fault at the HWY59 5 (504191) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY59 5 161.0 KV 504191 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | HY99TAP2_GRNWOOD2 | 3 Phase fault on HY99TAP2 (515019) 69 kV Bus a. Apply fault at the HY99TAP2 (515019) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HY99TAP2 69.0 KV 515019 TO GRNWOOD2 69.0 KV 515416 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | HY99TAP2_GRNWOOD2 | 3 Phase fault on HY99TAP2 (515019) 69 kV Bus a. Apply fault at the HY99TAP2 (515019) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HY99TAP2 69.0 KV 515019 TO GRNWOOD2 69.0 KV 515416 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | IDABEL4_VALIANT4 | 3 Phase fault on IDABEL-4 (510886) 138 kV Bus a. Apply fault at the IDABEL-4 (510886) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDABEL-4 138.0 KV 510886 TO VALIANT4 138.0 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | IDABEL4_VALIANT4 | 3 Phase fault on IDABEL-4 (510886) 138 kV Bus a. Apply fault at the IDABEL-4 (510886) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IDABEL-4 138.0 KV 510886 TO VALIANT4 138.0 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | IGO_5_ALTUS | 3 Phase fault on IGO 5 (515355) 161 kV Bus a. Apply fault at the IGO 5 (515355) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOARK 5 161.0 KV 515354 TO IGO 5 161.0 KV 515355 CKT 1 b.2. LOAD 1 515355 b.3. GLCARBN 161.0 KV 515353 TO NOARK 5 161.0 KV 515354 CKT 1 b.4. LOAD A1 515354 b.5. ALTUS 161.0 KV 515352 TO GLCARBN 161.0 KV 515353 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | IGO_5_ALTUS | 3 Phase fault on IGO 5 (515355) 161 kV Bus a. Apply fault at the IGO 5 (515355) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOARK 5 161.0 KV 515354 TO IGO 5 161.0 KV 515355 CKT 1 b.2. LOAD 1 515355 b.3. GLCARBN 161.0 KV 515353 TO NOARK 5 161.0 KV 515354 CKT 1 b.4. LOAD A1 515354 b.5. ALTUS 161.0 KV 515352 TO GLCARBN 161.0 KV 515353 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | IGO_5_RAZRBAK5 | 3 Phase fault on IGO 5 (515355) 161 kV Bus a. Apply fault at the IGO 5 (515355) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAZRBAK5 161.0 KV 515357 TO SUBIACT5 161.0 KV 515440 CKT 1 b.2. IGO 5 161.0 KV 515355 TO RAZRBAK5 161.0 KV 515357 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | IGO_5_RAZRBAK5 | 3 Phase fault on IGO 5 (515355) 161 kV Bus a. Apply fault at the IGO 5 (515355) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAZRBAK5 161.0 KV 515357 TO SUBIACT5 161.0 KV 515440 CKT 1 b.2. IGO 5 161.0 KV 515355 TO RAZRBAK5 161.0 KV 515357 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JACKTWN4_LINCOLN4 | 3 Phase fault on JACKTWN4 (515051) 138 kV Bus a. Apply fault at the JACKTWN4 (515051) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138.0 KV 515051 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JACKTWN4_LINCOLN4 | 3 Phase fault on JACKTWN4 (515051) 138 kV Bus a. Apply fault at the JACKTWN4 (515051) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138.0 KV 515051 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JENSEN_4_EL_RENO4 | 3 Phase fault on JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JENSEN_4_EL_RENO4 | 3 Phase fault on JENSEN 4 (514821) 138 kV Bus a. Apply fault at the JENSEN 4 (514821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSEN 4 138.0 KV 514821 TO EL RENO4 138.0 KV 520893 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JENSENT4_CIMARON4 | 3 Phase fault on JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JENSENT4_CIMARON4 | 3 Phase fault on JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JENSENT4_JENSEN_4 | 3 Phase fault on JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JENSENT4_JENSEN_4 | 3 Phase fault on JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JNSKAMO4_ARCADIA4 | 3 Phase fault on JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JNSKAMO4_ARCADIA4 | 3 Phase fault on JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JNSKAMO4_HSL_4 | 3 Phase fault on JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JNSKAMO4_HSL_4 | 3 Phase fault on JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_4_514809 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_4_514809 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_4_CANEYCK4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_4_CANEYCK4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_4_RUSSET4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_4_RUSSET4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_4_SXMLCKT4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_4_SXMLCKT4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_7_514809 | a. Apply single-phase fault on: a.1. JOHNCO 7 345.0 KV 514809 TO PITTSB-7 345.0 KV 510907 CKT 1, b. with stuck breaker near JOHNCO 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. JOHNCO 7 345.0 KV 514809 TO SUMMYSD7 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_7_514809 | a. Apply single-phase fault on: a.1. JOHNCO 7 345.0 KV 514809 TO PITTSB-7 345.0 KV 510907 CKT 1, b. with stuck breaker near JOHNCO 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. JOHNCO 7 345.0 KV 514809 TO SUMMYSD7 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_7_DMNDSPG7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_7_DMNDSPG7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_7_GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_7_GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JOHNCO_7_SUNNYSD7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JOHNCO_7_SUNNYSD7_6 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | JONSON_5_MASSARD5 | 3 Phase fault on JONSON 5 (515293) 161 kV Bus a. Apply fault at the JONSON 5 (515293) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONSON 5 161.0 KV 515293 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | JONSON_5_MASSARD5 | 3 Phase fault on JONSON 5 (515293) 161 kV Bus a. Apply fault at the JONSON 5 (515293) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONSON 5 161.0 KV 515293 TO MASSARD5 161.0 KV 515343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KELLYAV4_MEMRIAL4 | 3 Phase fault on KELLYAV4 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138.0 KV 514501 TO MEMRIAL4 138.0 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KELLYAV4_MEMRIAL4 | 3 Phase fault on KELLYAV4 (514501) 138 kV Bus a. Apply fault at the KELLYAV4 (514501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138.0 KV 514501 TO MEMRIAL4 138.0 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KELLYVL4_BLUEBEL4 | 3 Phase fault on KELLYVL4 (515200) 138 kV Bus a. Apply fault at the KELLYVL4 (515200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYVL4 138.0 KV 515200 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KELLYVL4_BLUEBEL4 | 3 Phase fault on KELLYVL4 (515200) 138 kV Bus a. Apply fault at the KELLYVL4 (515200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYVL4 138.0 KV 515200 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KETCH_4_FAIRFLD4 | 3 Phase fault on KETCH 4 (514834) 138 kV Bus a. Apply fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138.0 KV 514834 TO FAIRFLD4 138.0 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KETCH_4_FAIRFLD4 | 3 Phase fault on KETCH 4 (514834) 138 kV Bus a. Apply fault at the KETCH 4 (514834) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCH 4 138.0 KV 514834 TO FAIRFLD4 138.0 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KETCHTP4_KETCH_4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KETCHTP4_KETCH_4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KETCHTP4_NORTWST4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KETCHTP4_NORTWST4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KGFSHSW4_CMBLTP_4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO REEDING4 138.0 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. KGFSHSW4 138.0 KV 520533 TO REEDING4 138.0 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KGFSHSW4_CMBLTP_4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO REEDING4 138.0 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. KGFSHSW4 138.0 KV 520533 TO REEDING4 138.0 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KGFSHSW4_EKFSHTP4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KGFSHSW4_EKFSHTP4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KGFSHSW4_OMEGA_4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKCOM4 138.0 KV 520475 TO KGFSHSW4 138.0 KV 520533 CKT 1 b.2. PARKCOM4 138.0 KV 520475 TO OMEGA 4 138.0 KV 520964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KGFSHSW4_OMEGA_4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKCOM4 138.0 KV 520475 TO KGFSHSW4 138.0 KV 520533 CKT 1 b.2. PARKCOM4 138.0 KV 520475 TO OMEGA 4 138.0 KV 520964 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KGFSJCT4_EKFSHTP4 | 3 Phase fault on KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KGFSJCT4_EKFSHTP4 | 3 Phase fault on KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KINZE_4_UNVRSTY4 | 3 Phase fault on KINZE 4 (515008) 138 kV Bus a. Apply fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138.0 KV 515008 TO UNVRSTY4 138.0 KV 515181 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KINZE_4_UNVRSTY4 | 3 Phase fault on KINZE 4 (515008) 138 kV Bus a. Apply fault at the KINZE 4 (515008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZE 4 138.0 KV 515008 TO UNVRSTY4 138.0 KV 515181 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KINZEGR4_KINZE_4 | 3 Phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KINZEGR4_KINZE_4 | 3 Phase fault on KINZEGR4 (512710) 138 kV Bus a. Apply fault at the KINZEGR4 (512710) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KINZEGR4 138.0 KV 512710 TO KINZE 4 138.0 KV 515008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KLGORE_2_VBI_2 | 3 Phase fault on KLGORE 2 (515335) 69 kV Bus a. Apply fault at the KLGORE 2 (515335) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KLGORE 2 69.0 KV 515335 TO VBI 2 69.0 KV 515336 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KLGORE_2_VBI_2 | 3 Phase fault on KLGORE 2 (515335) 69 kV Bus a. Apply fault at the KLGORE 2 (515335) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KLGORE 2 69.0 KV 515335 TO VBI 2 69.0 KV 515336 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KNGFSHR7_515855 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7( 515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 515600 TO KNGFSR11 515855 TO KNGFRT11 515857 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KNGFSHR7_515855 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7( 515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 515600 TO KNGFSR11 515855 TO KNGFRT11 515857 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KNGFSHR7_515856_6 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7( 515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 515600 TO KNGFSR21 515856 TO KNGFRT21 515858 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KNGFSHR7_515856_6 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7( 515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 515600 TO KNGFSR21 515856 TO KNGFRT21 515858 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KNGFSHR7_FSHRTAP7_6 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7 (515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 345.0 KV 515600 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KNGFSHR7_FSHRTAP7_6 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7 (515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 345.0 KV 515600 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | KREMLNT2_HILLSDT2 | 3 Phase fault on KREMLNT2 (515501) 69 kV Bus a. Apply fault at the KREMLNT2 (515501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KREMLNT2 69.0 KV 515501 TO HILLSDT2 69.0 KV 515638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | KREMLNT2_HILLSDT2 | 3 Phase fault on KREMLNT2 (515501) 69 kV Bus a. Apply fault at the KREMLNT2 (515501) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KREMLNT2 69.0 KV 515501 TO HILLSDT2 69.0 KV 515638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LAKESID4_DVISION4 | 3 Phase fault on LAKESID4 (514849) 138 kV Bus a. Apply fault at the LAKESID4 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKESID4 138.0 KV 514849 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LAKESID4_DVISION4 | 3 Phase fault on LAKESID4 (514849) 138 kV Bus a. Apply fault at the LAKESID4 (514849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKESID4 138.0 KV 514849 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LATTA_4_LATTAJT4 | 3 Phase fault on LATTA 4 (520970) 138 kV Bus a. Apply fault at the LATTA 4 (520970) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LATTA 4 138.0 KV 520970 TO LATTAJT4 138.0 KV 520971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LATTA_4_LATTAJT4 | 3 Phase fault on LATTA 4 (520970) 138 kV Bus a. Apply fault at the LATTA 4 (520970) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LATTA 4 138.0 KV 520970 TO LATTAJT4 138.0 KV 520971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LATTAJT4_LASALLE4 | 3 Phase fault on LATTAJT4 (520971) 138 kV Bus a. Apply fault at the LATTAJT4 (520971) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASALLE4 138.0 KV 520969 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. LASALLE4 138.0 KV 520969 TO LATTAJT4 138.0 KV 520971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LATTAJT4_LASALLE4 | 3 Phase fault on LATTAJT4 (520971) 138 kV Bus a. Apply fault at the LATTAJT4 (520971) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LASALLE4 138.0 KV 520969 TO STNWLTP4 138.0 KV 521075 CKT 1 b.2. LASALLE4 138.0 KV 520969 TO LATTAJT4 138.0 KV 520971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LATTAJT4_OILCRTP4 | 3 Phase fault on LATTAJT4 (520971) 138 kV Bus a. Apply fault at the LATTAJT4 (520971) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LATTAJT4 138.0 KV 520971 TO OILCRTP4 138.0 KV 521014 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LATTAJT4_OILCRTP4 | 3 Phase fault on LATTAJT4 (520971) 138 kV Bus a. Apply fault at the LATTAJT4 (520971) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LATTAJT4 138.0 KV 520971 TO OILCRTP4 138.0 KV 521014 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES2_511467 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES2_511467 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES2_LGORE | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES2_LGORE | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES2_LGORE | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES2_LGORE | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES4_511467 | a. Apply single-phase fault on: a.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 a.2. LOAD 1 511474 a.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, b. with stuck breaker near L.E.S.-4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. L.E.S.-4 138.0 KV 511467 TO LWSTAP 4 138.0 KV 511439 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES4_511467 | a. Apply single-phase fault on: a.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 a.2. LOAD 1 511474 a.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1, b. with stuck breaker near L.E.S.-4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. L.E.S.-4 138.0 KV 511467 TO LWSTAP 4 138.0 KV 511439 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES4_511468 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES4_511468 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES4_ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES4_ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES4_COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES4_COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES4_ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES4_ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES7_511468 | a. Apply single-phase fault on: a.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1, b. with stuck breaker near L.E.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. L.E.S.-7 345.0 KV 511468 TO O.K.U.-7 345.0 KV 511456 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES7_511468 | a. Apply single-phase fault on: a.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1, b. with stuck breaker near L.E.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. L.E.S.-7 345.0 KV 511468 TO O.K.U.-7 345.0 KV 511456 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES7_G16_091 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES7_G16_091 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LES7_G17_171 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LES7_G17_171 | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LIBERTY5_AKINS_E5 | 3 Phase fault on LIBERTY5 (505524) 161 kV Bus a. Apply fault at the LIBERTY5 (505524) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY5 161.0 KV 505524 TO AKINS E5 161.0 KV 505526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LIBERTY5_AKINS_E5 | 3 Phase fault on LIBERTY5 (505524) 161 kV Bus a. Apply fault at the LIBERTY5 (505524) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY5 161.0 KV 505524 TO AKINS E5 161.0 KV 505526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LINCOLN4_MEEKER_4 | 3 Phase fault on LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138.0 KV 515442 TO MEEKER 4 138.0 KV 520464 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LINCOLN4_MEEKER_4 | 3 Phase fault on LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138.0 KV 515442 TO MEEKER 4 138.0 KV 520464 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LINWOOD4_LNWOODT4 | 3 Phase fault on LINWOOD4 (515401) 138 kV Bus a. Apply fault at the LINWOOD4 (515401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 515401 TO LNWOODT4 138.0 KV 515453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LINWOOD4_LNWOODT4 | 3 Phase fault on LINWOOD4 (515401) 138 kV Bus a. Apply fault at the LINWOOD4 (515401) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 515401 TO LNWOODT4 138.0 KV 515453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LNWOODT4_GRNWOOD4 | 3 Phase fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTPLNS4 138.0 KV 515043 TO LNWOODT4 138.0 KV 515453 CKT 1 b.2. GRTPLNS4 138.0 KV 515043 TO GRNWOOD4 138.0 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LNWOODT4_GRNWOOD4 | 3 Phase fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTPLNS4 138.0 KV 515043 TO LNWOODT4 138.0 KV 515453 CKT 1 b.2. GRTPLNS4 138.0 KV 515043 TO GRNWOOD4 138.0 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LNWOODT4_TRYON_4 | 3 Phase fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 138.0 KV 515453 TO TRYON 4 138.0 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LNWOODT4_TRYON_4 | 3 Phase fault on LNWOODT4 (515453) 138 kV Bus a. Apply fault at the LNWOODT4 (515453) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNWOODT4 138.0 KV 515453 TO TRYON 4 138.0 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LSPADR21_515320 | 3 Phase fault on LSPADR21 (515779) 34.5 kV Bus a. Apply fault at the LSPADR21( 515779) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADR21 515779 TO LSPADRA2 515320 TO LSPADR31 515780 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LSPADR21_515320 | 3 Phase fault on LSPADR21 (515779) 34.5 kV Bus a. Apply fault at the LSPADR21( 515779) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADR21 515779 TO LSPADRA2 515320 TO LSPADR31 515780 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LSPADRA2_515319 | 3 Phase fault on LSPADRA2 (515320) 69 kV Bus a. Apply fault at the LSPADRA2( 515320) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA2 515320 TO LSPADRA5 515319 TO LSPADR41 515733 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LSPADRA2_515319 | 3 Phase fault on LSPADRA2 (515320) 69 kV Bus a. Apply fault at the LSPADRA2( 515320) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA2 515320 TO LSPADRA5 515319 TO LSPADR41 515733 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LSPADRA5_IGO_5 | 3 Phase fault on LSPADRA5 (515319) 161 kV Bus a. Apply fault at the LSPADRA5 (515319) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA5 161.0 KV 515319 TO IGO 5 161.0 KV 515355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LSPADRA5_IGO_5 | 3 Phase fault on LSPADRA5 (515319) 161 kV Bus a. Apply fault at the LSPADRA5 (515319) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSPADRA5 161.0 KV 515319 TO IGO 5 161.0 KV 515355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | No | Yes | Yes | High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | No | Yes | Yes | High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | No | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LT__WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LT__WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member_Submitted | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LULA_2_515192 | 3 Phase fault on LULA 2 (515191) 69 kV Bus a. Apply fault at the LULA 2( 515191) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 2 515191 TO LULA 4 515192 TO LULA 1 515734 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LULA_2_515192 | 3 Phase fault on LULA 2 (515191) 69 kV Bus a. Apply fault at the LULA 2( 515191) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 2 515191 TO LULA 4 515192 TO LULA 1 515734 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LULA_4_EFITSTP4 | 3 Phase fault on LULA 4 (515192) 138 kV Bus a. Apply fault at the LULA 4 (515192) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LULA_4_EFITSTP4 | 3 Phase fault on LULA 4 (515192) 138 kV Bus a. Apply fault at the LULA 4 (515192) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO EFITSTP4 138.0 KV 515699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LULA_4_STNWLSW4 | 3 Phase fault on LULA 4 (515192) 138 kV Bus a. Apply fault at the LULA 4 (515192) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LULA_4_STNWLSW4 | 3 Phase fault on LULA 4 (515192) 138 kV Bus a. Apply fault at the LULA 4 (515192) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LULA 4 138.0 KV 515192 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LWS_S4_LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LWS_S4_LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LWSTAP_4_LE4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LWSTAP_4_LE4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LWSTAP_4_RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LWSTAP_4_RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LYDIA_7_VALIANT7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LYDIA_7_VALIANT7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | LYDIA_7_WELSH_7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | LYDIA_7_WELSH_7_6 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MADINDT4_CANEYCK4 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MADINDT4_CANEYCK4 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MADINDT4_MADLIND4 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO MADLIND4 138.0 KV 515158 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MADINDT4_MADLIND4 | 3 Phase fault on MADINDT4 (515149) 138 kV Bus a. Apply fault at the MADINDT4 (515149) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADINDT4 138.0 KV 515149 TO MADLIND4 138.0 KV 515158 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MARIETA4_520987 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4( 520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MARIETA4_520987 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4( 520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 520988 TO MARIETA2 520987 TO MARSWTERT 521171 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MARIETA4_SWILSON4 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4 (520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MARIETA4_SWILSON4 | 3 Phase fault on MARIETA4 (520988) 138 kV Bus a. Apply fault at the MARIETA4 (520988) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARIETA4 138.0 KV 520988 TO SWILSON4 138.0 KV 521061 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MARSHL_4_CTNWOOD4 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MARSHL_4_CTNWOOD4 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MARSHL_4_MARSHAL4 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MARSHL_4_MARSHAL4 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MASSARD2_515343 | 3 Phase fault on MASSARD2 (515342) 69 kV Bus a. Apply fault at the MASSARD2( 515342) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 515342 TO MASSARD5 515343 TO MASSARD1 515735 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MASSARD2_515343 | 3 Phase fault on MASSARD2 (515342) 69 kV Bus a. Apply fault at the MASSARD2( 515342) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD2 515342 TO MASSARD5 515343 TO MASSARD1 515735 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MASSARD5_RYHLLTP5 | 3 Phase fault on MASSARD5 (515343) 161 kV Bus a. Apply fault at the MASSARD5 (515343) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MASSARD5_RYHLLTP5 | 3 Phase fault on MASSARD5 (515343) 161 kV Bus a. Apply fault at the MASSARD5 (515343) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MASSARD5 161.0 KV 515343 TO RYHLLTP5 161.0 KV 515523 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MATHWSN7_515497 | a. Apply single-phase fault on: a.1. MATHWSN7 345.0 KV 515497 TO TATONGA7 345.0 KV 515407 CKT 2, b. with stuck breaker near MATHWSN7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. MATHWSN7 345.0 KV 515497 TO TATONGA7 345.0 KV 515407 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MATHWSN7_515497 | a. Apply single-phase fault on: a.1. MATHWSN7 345.0 KV 515497 TO TATONGA7 345.0 KV 515407 CKT 2, b. with stuck breaker near MATHWSN7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. MATHWSN7 345.0 KV 515497 TO TATONGA7 345.0 KV 515407 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MATHWSN7_REDNGTN7_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MATHWSN7_REDNGTN7_6 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MATHWSN7_TRAVERSE3 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MATHWSN7_TRAVERSE3 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MAUD_4_515054 | 3 Phase fault on MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4( 515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MAUD_4_515054 | 3 Phase fault on MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4( 515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MAUD_4_FRSTHIL4 | 3 Phase fault on MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MAUD_4_FRSTHIL4 | 3 Phase fault on MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MAYO_S4_BANNTAP4 | 3 Phase fault on MAYO--S4 (509780) 138 kV Bus a. Apply fault at the MAYO--S4 (509780) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--S4 138.0 KV 509780 TO BANNTAP4 138.0 KV 509785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MAYO_S4_BANNTAP4 | 3 Phase fault on MAYO--S4 (509780) 138 kV Bus a. Apply fault at the MAYO--S4 (509780) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYO--S4 138.0 KV 509780 TO BANNTAP4 138.0 KV 509785 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MCCLAIN4_G17_152_TAP | 3 Phase fault on MCCLAIN4 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 138.0 KV 514902 TO G17-152_TAP 138.0 KV 914902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MCCLAIN4_G17_152_TAP | 3 Phase fault on MCCLAIN4 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 138.0 KV 514902 TO G17-152_TAP 138.0 KV 914902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MCCLAIN4_PLVALLY4 | 3 Phase fault on MCCLAIN4 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 138.0 KV 514902 TO PLVALLY4 138.0 KV 514929 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MCCLAIN4_PLVALLY4 | 3 Phase fault on MCCLAIN4 (514902) 138 kV Bus a. Apply fault at the MCCLAIN4 (514902) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCCLAIN4 138.0 KV 514902 TO PLVALLY4 138.0 KV 514929 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MDFRDTP4_MEDFORD4 | 3 Phase fault on MDFRDTP4 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDFRDTP4 138.0 KV 515569 TO MEDFORD4 138.0 KV 522397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MDFRDTP4_MEDFORD4 | 3 Phase fault on MDFRDTP4 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MDFRDTP4 138.0 KV 515569 TO MEDFORD4 138.0 KV 522397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MEDFORD4_PONDCRK4 | 3 Phase fault on MEDFORD4 (522397) 138 kV Bus a. Apply fault at the MEDFORD4 (522397) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD4 138.0 KV 522397 TO PONDCRK4 138.0 KV 522398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MEDFORD4_PONDCRK4 | 3 Phase fault on MEDFORD4 (522397) 138 kV Bus a. Apply fault at the MEDFORD4 (522397) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEDFORD4 138.0 KV 522397 TO PONDCRK4 138.0 KV 522398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MEMRIAL4_BRYANT_4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MEMRIAL4_BRYANT_4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MEMRIAL4_SKYLINE4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO SKYLINE4 138.0 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MEMRIAL4_SKYLINE4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO SKYLINE4 138.0 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MEMRIAL4_TENESTP4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MEMRIAL4_TENESTP4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MIDWEST4_FRNKLNS4 | 3 Phase fault on MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MIDWEST4_FRNKLNS4 | 3 Phase fault on MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MIDWEST4_HOLLYWD4 | 3 Phase fault on MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MIDWEST4_HOLLYWD4 | 3 Phase fault on MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MILAN_GOAB_MILAN_4 | 3 Phase fault on MILAN_GOAB (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILAN_GOAB 138.0 KV 539008 TO MILAN 4 138.0 KV 539676 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MILAN_GOAB_MILAN_4 | 3 Phase fault on MILAN_GOAB (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILAN_GOAB 138.0 KV 539008 TO MILAN 4 138.0 KV 539676 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MILLCKT4_SXMLCKT4 | 3 Phase fault on MILLCKT4 (515121) 138 kV Bus a. Apply fault at the MILLCKT4 (515121) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MILLCKT4_SXMLCKT4 | 3 Phase fault on MILLCKT4 (515121) 138 kV Bus a. Apply fault at the MILLCKT4 (515121) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLCKT4 138.0 KV 515121 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MILLERT4_SOONER_4 | 3 Phase fault on MILLERT4 (514704) 138 kV Bus a. Apply fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 138.0 KV 514704 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MILLERT4_SOONER_4 | 3 Phase fault on MILLERT4 (514704) 138 kV Bus a. Apply fault at the MILLERT4 (514704) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLERT4 138.0 KV 514704 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MINCO_7_514801 | a. Apply single-phase fault on: a.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1, b. with stuck breaker near MINCO 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MINCO_7_514801 | a. Apply single-phase fault on: a.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1, b. with stuck breaker near MINCO 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MINCO_7_CIMARON7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MINCO_7_CIMARON7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MINCO_7_GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MINCO_7_GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1. GEN-2016-095 trips on voltage protection settings 2. Minco units trip on frequency protection settings | 1. Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. 2. Disabling frequency protection settings for Minco units prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MINCO_7_GRACMNT7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MINCO_7_GRACMNT7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MINCO_7_MCNOWND7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MINCO_7_MCNOWND7_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MINCO_7_MNCWND37_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MINCO_7_MNCWND37_6 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MINCO_7_NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Minco Wind units trips on frequency protection settings | Disabling frequency protection settings for Minco units prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MINCO_7_NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | 1. GEN-2016-095 trips on voltage protection settings 2. Minco units trip on frequency protection settings | 1. Disabling instantaneous voltage protection settings for GEN-2016-095 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800. 2. Disabling frequency protection settings for Minco units prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MOORE_2_FRNKLNS2 | 3 Phase fault on MOORE 2 (520489) 69 kV Bus a. Apply fault at the MOORE 2 (520489) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 2 69.0 KV 520489 TO FRNKLNS2 69.0 KV 520916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MOORE_2_FRNKLNS2 | 3 Phase fault on MOORE 2 (520489) 69 kV Bus a. Apply fault at the MOORE 2 (520489) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 2 69.0 KV 520489 TO FRNKLNS2 69.0 KV 520916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MORRISN4_MORISNT4 | 3 Phase fault on MORRISN4 (515006) 138 kV Bus a. Apply fault at the MORRISN4 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 138.0 KV 515006 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MORRISN4_MORISNT4 | 3 Phase fault on MORRISN4 (515006) 138 kV Bus a. Apply fault at the MORRISN4 (515006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRISN4 138.0 KV 515006 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MRIETA_2_ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MRIETA_2_ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MRIETA_4_MARIETA4 | 3 Phase fault on MRIETA 4 (520455) 138 kV Bus a. Apply fault at the MRIETA 4 (520455) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MRIETA_4_MARIETA4 | 3 Phase fault on MRIETA 4 (520455) 138 kV Bus a. Apply fault at the MRIETA 4 (520455) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 4 138.0 KV 520455 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MUSKOGE7_515224 | a. Apply single-phase fault on: a.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1, b. with stuck breaker near MUSKOGE7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MUSKOGE7_515224 | a. Apply single-phase fault on: a.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1, b. with stuck breaker near MUSKOGE7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MUSKOGE7_FIREWHL | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MUSKOGE7_FIREWHL | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MUSKOGE7_FTSMITH7_6 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MUSKOGE7_FTSMITH7_6 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | MUSKOGE7_PECANCK7_6 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | MUSKOGE7_PECANCK7_6 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NASH_2_WAKITA_2 | 3 Phase fault on NASH 2 (521008) 69 kV Bus a. Apply fault at the NASH 2 (521008) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 2 69.0 KV 521008 TO WAKITA 2 69.0 KV 521085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NASH_2_WAKITA_2 | 3 Phase fault on NASH 2 (521008) 69 kV Bus a. Apply fault at the NASH 2 (521008) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 2 69.0 KV 521008 TO WAKITA 2 69.0 KV 521085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NHUNTNT5_WBOONVL5 | 3 Phase fault on NHUNTNT5 (507189) 161 kV Bus a. Apply fault at the NHUNTNT5 (507189) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT5 161.0 KV 507189 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NHUNTNT5_WBOONVL5 | 3 Phase fault on NHUNTNT5 (507189) 161 kV Bus a. Apply fault at the NHUNTNT5 (507189) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NHUNTNT5 161.0 KV 507189 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NITROTP5_NITROUS5 | 3 Phase fault on NITROTP5 (515329) 161 kV Bus a. Apply fault at the NITROTP5 (515329) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO NITROUS5 161.0 KV 515350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NITROTP5_NITROUS5 | 3 Phase fault on NITROTP5 (515329) 161 kV Bus a. Apply fault at the NITROTP5 (515329) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NITROTP5 161.0 KV 515329 TO NITROUS5 161.0 KV 515350 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NKNGFSH4_DOVERSW4 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NKNGFSH4_DOVERSW4 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NMAGZIN5_BRANCH_5 | 3 Phase fault on NMAGZIN5 (507190) 161 kV Bus a. Apply fault at the NMAGZIN5 (507190) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO 5 161.0 KV 515316 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NMAGZIN5_BRANCH_5 | 3 Phase fault on NMAGZIN5 (507190) 161 kV Bus a. Apply fault at the NMAGZIN5 (507190) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO 5 161.0 KV 515316 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NMAGZIN5_WBOONVL5 | 3 Phase fault on NMAGZIN5 (507190) 161 kV Bus a. Apply fault at the NMAGZIN5 (507190) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NMAGZIN5_WBOONVL5 | 3 Phase fault on NMAGZIN5 (507190) 161 kV Bus a. Apply fault at the NMAGZIN5 (507190) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NMAGZIN5 161.0 KV 507190 TO WBOONVL5 161.0 KV 507192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NORTWST4_514879 | a. Apply single-phase fault on: a.1. NORTWST4 138.0 KV 514879 TO BRADEN 4 138.0 KV 514854 CKT 1 a.2. LOAD 1 514854 a.3. BRADEN 4 138.0 KV 514854 TO SLVRLAK4 138.0 KV 514852 CKT 1, b. with stuck breaker near NORTWST4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. NORTWST4 138.0 KV 514879 TO LNEOAK 4 138.0 KV 514873 CKT 1 c.2. LOAD 1 514873 c.3. LNEOAK 4 138.0 KV 514873 TO QUAILCK4 138.0 KV 514851 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NORTWST4_514879 | a. Apply single-phase fault on: a.1. NORTWST4 138.0 KV 514879 TO BRADEN 4 138.0 KV 514854 CKT 1 a.2. LOAD 1 514854 a.3. BRADEN 4 138.0 KV 514854 TO SLVRLAK4 138.0 KV 514852 CKT 1, b. with stuck breaker near NORTWST4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. NORTWST4 138.0 KV 514879 TO LNEOAK 4 138.0 KV 514873 CKT 1 c.2. LOAD 1 514873 c.3. LNEOAK 4 138.0 KV 514873 TO QUAILCK4 138.0 KV 514851 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NORTWST4_514880 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-178 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NORTWST4_514880 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NORTWST4_QUAILCK4 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO LNEOAK 4 138.0 KV 514873 CKT 1 b.2. LOAD 1 514873 b.3. LNEOAK 4 138.0 KV 514873 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NORTWST4_QUAILCK4 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4 (514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO LNEOAK 4 138.0 KV 514873 CKT 1 b.2. LOAD 1 514873 b.3. LNEOAK 4 138.0 KV 514873 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NORTWST7_514880 | a. Apply single-phase fault on: a.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1, b. with stuck breaker near NORTWST7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NORTWST7_514880 | a. Apply single-phase fault on: a.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1, b. with stuck breaker near NORTWST7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-178 trips on voltage protection settings | Operational steady state fixes (existing caps/taps/gen set points).
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NORTWST7_ARCADIA7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NORTWST7_ARCADIA7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NORTWST7_CIMARON7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NORTWST7_CIMARON7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NORTWST7_MATHWSN7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NORTWST7_MATHWSN7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NORTWST7_SPRNGCK7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NORTWST7_SPRNGCK7_6 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NSUB345_555234 | a. Apply single-phase fault on: a.1. NSUB345 345.0 KV 555234 TO CIMARON7 345.0 KV 514901 CKT 1, b. with stuck breaker near NSUB345 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. NSUB345 345.0 KV 555234 TO MINCO 7 345.0 KV 514801 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NSUB345_555234 | a. Apply single-phase fault on: a.1. NSUB345 345.0 KV 555234 TO CIMARON7 345.0 KV 514901 CKT 1, b. with stuck breaker near NSUB345 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. NSUB345 345.0 KV 555234 TO MINCO 7 345.0 KV 514801 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NUMAOGE2_DEERCK_2 | 3 Phase fault on NUMAOGE2 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 69.0 KV 514740 TO DEERCK 2 69.0 KV 514741 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NUMAOGE2_DEERCK_2 | 3 Phase fault on NUMAOGE2 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 69.0 KV 514740 TO DEERCK 2 69.0 KV 514741 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NUMAOGE2_NUMA_2 | 3 Phase fault on NUMAOGE2 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 69.0 KV 514740 TO NUMA 2 69.0 KV 521013 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NUMAOGE2_NUMA_2 | 3 Phase fault on NUMAOGE2 (514740) 69 kV Bus a. Apply fault at the NUMAOGE2 (514740) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NUMAOGE2 69.0 KV 514740 TO NUMA 2 69.0 KV 521013 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NWTXARK4_508072 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NWTXARK4_508072 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NWTXARK7_LYDIA_7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NWTXARK7_LYDIA_7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NWTXARK7_VALIANT7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NWTXARK7_VALIANT7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | NWTXARK7_WELSH_7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | NWTXARK7_WELSH_7_6 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OAKGROV2_GRNWOOD2 | 3 Phase fault on OAKGROV2 (515021) 69 kV Bus a. Apply fault at the OAKGROV2 (515021) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKGROV2 69.0 KV 515021 TO GRNWOOD2 69.0 KV 515416 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OAKGROV2_GRNWOOD2 | 3 Phase fault on OAKGROV2 (515021) 69 kV Bus a. Apply fault at the OAKGROV2 (515021) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKGROV2 69.0 KV 515021 TO GRNWOOD2 69.0 KV 515416 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OKEENE_4_521015 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OKEENE_4_521015 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OKU7_G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OKU7_G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OKU7_GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OKU7_GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OKU7_LES7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OKU7_LES7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OKU7_OKLAUN_HVDC7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OKU7_OKLAUN_HVDC7_6 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ONETA_4_509806 | a. Apply single-phase fault on: a.1. ONETA--4 138.0 KV 509806 TO BA.N-ST4 138.0 KV 509786 CKT 1, b. with stuck breaker near ONETA--4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. ONETA--4 138.0 KV 509806 TO BA101-N4 138.0 KV 509769 CKT 1 c.2. LOAD 1 509769 c.3. BA101-N4 138.0 KV 509769 TO BA81---4 138.0 KV 509747 CKT 1 c.4. LOAD 1 509747 c.5. BA81---4 138.0 KV 509747 TO FORD---4 138.0 KV 509772 CKT 1 c.6. LOAD 1 509772 c.7. FORD---4 138.0 KV 509772 TO 53GARST4 138.0 KV 509763 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ONETA_4_509806 | a. Apply single-phase fault on: a.1. ONETA--4 138.0 KV 509806 TO BA.N-ST4 138.0 KV 509786 CKT 1, b. with stuck breaker near ONETA--4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. ONETA--4 138.0 KV 509806 TO BA101-N4 138.0 KV 509769 CKT 1 c.2. LOAD 1 509769 c.3. BA101-N4 138.0 KV 509769 TO BA81---4 138.0 KV 509747 CKT 1 c.4. LOAD 1 509747 c.5. BA81---4 138.0 KV 509747 TO FORD---4 138.0 KV 509772 CKT 1 c.6. LOAD 1 509772 c.7. FORD---4 138.0 KV 509772 TO 53GARST4 138.0 KV 509763 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ONETA_4_509807 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4( 509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ONETA_4_509807 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4( 509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ONETA_4_53GARST4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138.0 KV 509747 TO BA101-N4 138.0 KV 509769 CKT 1 b.2. LOAD 1 509769 b.3. BA101-N4 138.0 KV 509769 TO ONETA--4 138.0 KV 509806 CKT 1 b.4. LOAD 1 509806 b.5. BA81---4 138.0 KV 509747 TO FORD---4 138.0 KV 509772 CKT 1 b.6. LOAD 1 509772 b.7. 53GARST4 138.0 KV 509763 TO FORD---4 138.0 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ONETA_4_53GARST4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA81---4 138.0 KV 509747 TO BA101-N4 138.0 KV 509769 CKT 1 b.2. LOAD 1 509769 b.3. BA101-N4 138.0 KV 509769 TO ONETA--4 138.0 KV 509806 CKT 1 b.4. LOAD 1 509806 b.5. BA81---4 138.0 KV 509747 TO FORD---4 138.0 KV 509772 CKT 1 b.6. LOAD 1 509772 b.7. 53GARST4 138.0 KV 509763 TO FORD---4 138.0 KV 509772 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ONETA_4_77MEMTP4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO 121LYNN4 138.0 KV 509869 CKT 1 b.2. LOAD 1 509869 b.3. 121LYNN4 138.0 KV 509869 TO E_121ST4 138.0 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. 81GARN-4 138.0 KV 509855 TO E_121ST4 138.0 KV 509889 CKT 1 b.6. LOAD 1 509889 b.7. 77MEMTP4 138.0 KV 509765 TO 81GARN-4 138.0 KV 509855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ONETA_4_77MEMTP4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO 121LYNN4 138.0 KV 509869 CKT 1 b.2. LOAD 1 509869 b.3. 121LYNN4 138.0 KV 509869 TO E_121ST4 138.0 KV 509889 CKT 1 b.4. LOAD 1 509889 b.5. 81GARN-4 138.0 KV 509855 TO E_121ST4 138.0 KV 509889 CKT 1 b.6. LOAD 1 509889 b.7. 77MEMTP4 138.0 KV 509765 TO 81GARN-4 138.0 KV 509855 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ONETA_4_BANNTAP4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 138.0 KV 509785 TO BA_71ST4 138.0 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. ONETA--4 138.0 KV 509806 TO BA_71ST4 138.0 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ONETA_4_BANNTAP4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANNTAP4 138.0 KV 509785 TO BA_71ST4 138.0 KV 509891 CKT 1 b.2. LOAD 1 509891 b.3. ONETA--4 138.0 KV 509806 TO BA_71ST4 138.0 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ONETA_7_509807 | a. Apply single-phase fault on: a.1. ONETA--7 345.0 KV 509807 TO R.S.S.-7 345.0 KV 509782 CKT 1, b. with stuck breaker near ONETA--7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ONETA_7_509807 | a. Apply single-phase fault on: a.1. ONETA--7 345.0 KV 509807 TO R.S.S.-7 345.0 KV 509782 CKT 1, b. with stuck breaker near ONETA--7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ONETA_7_NE7_6 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ONETA_7_NE7_6 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ONETA_7_OEC_7_6 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ONETA_7_OEC_7_6 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OTTER_4_ARMFTWD4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OTTER_4_ARMFTWD4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OTTER_4_WOODRNG4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OTTER_4_WOODRNG4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OTTER_4_WRVALLY4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OTTER_4_WRVALLY4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OXFORD_4_SUMNER_4 | 3 Phase fault on OXFORD 4 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 4 138.0 KV 532982 TO SUMNER 4 138.0 KV 532984 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OXFORD_4_SUMNER_4 | 3 Phase fault on OXFORD 4 (532982) 138 kV Bus a. Apply fault at the OXFORD 4 (532982) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXFORD 4 138.0 KV 532982 TO SUMNER 4 138.0 KV 532984 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | OZARK_H5_VAN_BUR5 | 3 Phase fault on OZARK H5 (505516) 161 kV Bus a. Apply fault at the OZARK H5 (505516) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO VAN BUR5 161.0 KV 505522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | OZARK_H5_VAN_BUR5 | 3 Phase fault on OZARK H5 (505516) 161 kV Bus a. Apply fault at the OZARK H5 (505516) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OZARK H5 161.0 KV 505516 TO VAN BUR5 161.0 KV 505522 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PALIOGE2_515100 | 3 Phase fault on PALIOGE2 (515099) 69 kV Bus a. Apply fault at the PALIOGE2( 515099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 515099 TO PAOLI- 4 515100 TO PAOLI 1 515746 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PALIOGE2_515100 | 3 Phase fault on PALIOGE2 (515099) 69 kV Bus a. Apply fault at the PALIOGE2( 515099) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALIOGE2 515099 TO PAOLI- 4 515100 TO PAOLI 1 515746 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PAOLI_4_CHIGLEY4 | 3 Phase fault on PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO CHIGLEY4 138.0 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PAOLI_4_CHIGLEY4 | 3 Phase fault on PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO CHIGLEY4 138.0 KV 515114 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PAOLI_4_MAYSVIL4 | 3 Phase fault on PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO MAYSVIL4 138.0 KV 515124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PAOLI_4_MAYSVIL4 | 3 Phase fault on PAOLI- 4 (515100) 138 kV Bus a. Apply fault at the PAOLI- 4 (515100) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAOLI- 4 138.0 KV 515100 TO MAYSVIL4 138.0 KV 515124 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PARKLN_2_515178 | 3 Phase fault on PARKLN 2 (515177) 69 kV Bus a. Apply fault at the PARKLN 2( 515177) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PARKLN_2_515178 | 3 Phase fault on PARKLN 2 (515177) 69 kV Bus a. Apply fault at the PARKLN 2( 515177) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 2 515177 TO PARKLN 4 515178 TO PARKLN21 515748 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PARKLN_4_SOTHADA4 | 3 Phase fault on PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138.0 KV 515178 TO SOTHADA4 138.0 KV 515318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PARKLN_4_SOTHADA4 | 3 Phase fault on PARKLN 4 (515178) 138 kV Bus a. Apply fault at the PARKLN 4 (515178) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARKLN 4 138.0 KV 515178 TO SOTHADA4 138.0 KV 515318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PECANCK4_515234 | 3 Phase fault on PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4( 515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 515233 TO PECANCK5 515234 TO PECANC31 515750 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PECANCK4_515234 | 3 Phase fault on PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4( 515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 515233 TO PECANCK5 515234 TO PECANC31 515750 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PECANCK5_515235 | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5( 515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PECANCK5_515235 | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5( 515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PECANCK7_515235 | a. Apply single-phase fault on: a.1. PECANCK7 345.0 KV 515235 TO MUSKOGE7 345.0 KV 515224 CKT 1, b. with stuck breaker near PECANCK7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. PECANCK7 345.0 KV 515235 TO MUSKOGE7 345.0 KV 515224 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PECANCK7_515235 | a. Apply single-phase fault on: a.1. PECANCK7 345.0 KV 515235 TO MUSKOGE7 345.0 KV 515224 CKT 1, b. with stuck breaker near PECANCK7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. PECANCK7 345.0 KV 515235 TO MUSKOGE7 345.0 KV 515224 CKT 2 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PERRY_4_SOONER_4 | 3 Phase fault on PERRY 4 (514707) 138 kV Bus a. Apply fault at the PERRY 4 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 138.0 KV 514707 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PERRY_4_SOONER_4 | 3 Phase fault on PERRY 4 (514707) 138 kV Bus a. Apply fault at the PERRY 4 (514707) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERRY 4 138.0 KV 514707 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PINK_4_PINK_SW4 | 3 Phase fault on PINK 4 (520494) 138 kV Bus a. Apply fault at the PINK 4 (520494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK 4 138.0 KV 520494 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PINK_4_PINK_SW4 | 3 Phase fault on PINK 4 (520494) 138 kV Bus a. Apply fault at the PINK 4 (520494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK 4 138.0 KV 520494 TO PINK SW4 138.0 KV 521028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PINK_SW4_SHAWNEE4 | 3 Phase fault on PINK SW4 (521028) 138 kV Bus a. Apply fault at the PINK SW4 (521028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK SW4 138.0 KV 521028 TO SHAWNEE4 138.0 KV 521048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PINK_SW4_SHAWNEE4 | 3 Phase fault on PINK SW4 (521028) 138 kV Bus a. Apply fault at the PINK SW4 (521028) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINK SW4 138.0 KV 521028 TO SHAWNEE4 138.0 KV 521048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PINTAIL7_KINGWD_7_6 | 3 Phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PINTAIL7_KINGWD_7_6 | 3 Phase fault on PINTAIL7 (516010) 345 kV Bus a. Apply fault at the PINTAIL7 (516010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PINTAIL7 345.0 KV 516010 TO KINGWD 7 345.0 KV 516019 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PITTSB__CRIVER | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PITTSB__CRIVER | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PITTSB__JOHNCO | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PITTSB__JOHNCO | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PITTSB__KIOWA | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PITTSB__KIOWA | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PITTSB__SEMINOL | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PITTSB__SEMINOL | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PITTSB__VALIANT | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PITTSB__VALIANT | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PITTSB7_510907 | a. Apply single-phase fault on: a.1. VALIANT7 345.0 KV 510911 TO PITTSB-7 345.0 KV 510907 CKT 1, b. with stuck breaker near PITTSB-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PITTSB7_510907 | a. Apply single-phase fault on: a.1. VALIANT7 345.0 KV 510911 TO PITTSB-7 345.0 KV 510907 CKT 1, b. with stuck breaker near PITTSB-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PLVALLY4_555234 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4( 514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 514929 TO NSUB345 555234 TO NEWBUS13.8 750001 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PLVALLY4_555234 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4( 514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 514929 TO NSUB345 555234 TO NEWBUS13.8 750001 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | POOLVIL4_515130 | a. Apply single-phase fault on: a.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1, b. with stuck breaker near SUNNYSD7 345 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SUNNYSD7 345.0 KV 515136 TO TERRYRD7 345.0 KV 511568 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | POOLVIL4_515130 | a. Apply single-phase fault on: a.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1, b. with stuck breaker near SUNNYSD7 345 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SUNNYSD7 345.0 KV 515136 TO TERRYRD7 345.0 KV 511568 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | POOLVIL4_CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | POOLVIL4_CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PRATTV4_BLUEBEL4 | 3 Phase fault on PRATTV-4 (509758) 138 kV Bus a. Apply fault at the PRATTV-4 (509758) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138.0 KV 509758 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PRATTV4_BLUEBEL4 | 3 Phase fault on PRATTV-4 (509758) 138 kV Bus a. Apply fault at the PRATTV-4 (509758) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138.0 KV 509758 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | PRICESF4_HONEYCK4 | 3 Phase fault on PRICESF4 (514814) 138 kV Bus a. Apply fault at the PRICESF4 (514814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRICESF4 138.0 KV 514814 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | PRICESF4_HONEYCK4 | 3 Phase fault on PRICESF4 (514814) 138 kV Bus a. Apply fault at the PRICESF4 (514814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRICESF4 138.0 KV 514814 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | QUAILCK4_SLVRLAK4 | 3 Phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO SLVRLAK4 138.0 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | QUAILCK4_SLVRLAK4 | 3 Phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO SLVRLAK4 138.0 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RANCHRD7_FRNT2WD7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNT2WD7 345.0 KV 516066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RANCHRD7_FRNT2WD7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNT2WD7 345.0 KV 516066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RANCHRD7_FRNTWND7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RANCHRD7_FRNTWND7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO FRNTWND7 345.0 KV 515688 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RANCHRD7_OMCDLEC7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RANCHRD7_OMCDLEC7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OMCDLEC7 345.0 KV 529200 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RANCHRD7_OPENSKY7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RANCHRD7_OPENSKY7_6 | 3 Phase fault on RANCHRD7 (515576) 345 kV Bus a. Apply fault at the RANCHRD7 (515576) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RANCHRD7 345.0 KV 515576 TO OPENSKY7 345.0 KV 515621 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RATLIFF4_CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RATLIFF4_CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RDRUNNR4_COYOTE_4 | 3 Phase fault on RDRUNNR4 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 138.0 KV 515426 TO COYOTE 4 138.0 KV 515581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RDRUNNR4_COYOTE_4 | 3 Phase fault on RDRUNNR4 (515426) 138 kV Bus a. Apply fault at the RDRUNNR4 (515426) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 138.0 KV 515426 TO COYOTE 4 138.0 KV 515581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | REAGAN_4_RUSSETT4 | 3 Phase fault on REAGAN 4 (520465) 138 kV Bus a. Apply fault at the REAGAN 4 (520465) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REAGAN 4 138.0 KV 520465 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | REAGAN_4_RUSSETT4 | 3 Phase fault on REAGAN 4 (520465) 138 kV Bus a. Apply fault at the REAGAN 4 (520465) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REAGAN 4 138.0 KV 520465 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | REDBUD1S_514909 | 3 Phase fault on REDBUD1S (514899) 18 kV Bus a. Apply fault at the REDBUD1S( 514899) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | REDBUD1S_514909 | 3 Phase fault on REDBUD1S (514899) 18 kV Bus a. Apply fault at the REDBUD1S( 514899) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | REDBUD2S_514909 | 3 Phase fault on REDBUD2S (514900) 18 kV Bus a. Apply fault at the REDBUD2S( 514900) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD2S 514900 TO REDBUD 7 514909 TO REDBUD2G 514911 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | REDBUD2S_514909 | 3 Phase fault on REDBUD2S (514900) 18 kV Bus a. Apply fault at the REDBUD2S( 514900) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD2S 514900 TO REDBUD 7 514909 TO REDBUD2G 514911 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | REDBUD3S_514909 | 3 Phase fault on REDBUD3S (514905) 18 kV Bus a. Apply fault at the REDBUD3S( 514905) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | REDBUD3S_514909 | 3 Phase fault on REDBUD3S (514905) 18 kV Bus a. Apply fault at the REDBUD3S( 514905) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | REDBUD4S_514909 | 3 Phase fault on REDBUD4S (514940) 18 kV Bus a. Apply fault at the REDBUD4S( 514940) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | REDBUD4S_514909 | 3 Phase fault on REDBUD4S (514940) 18 kV Bus a. Apply fault at the REDBUD4S( 514940) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | REDCNTP4_CLVLDSW4 | 3 Phase fault on REDCNTP4 (520552) 138 kV Bus a. Apply fault at the REDCNTP4 (520552) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 b.2. LOAD 1 520859 b.3. REDCNTP4 138.0 KV 520552 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | REDCNTP4_CLVLDSW4 | 3 Phase fault on REDCNTP4 (520552) 138 kV Bus a. Apply fault at the REDCNTP4 (520552) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 b.2. LOAD 1 520859 b.3. REDCNTP4 138.0 KV 520552 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | REDCNTP4_SCOTTSW4 | 3 Phase fault on REDCNTP4 (520552) 138 kV Bus a. Apply fault at the REDCNTP4 (520552) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCNTP4 138.0 KV 520552 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | REDCNTP4_SCOTTSW4 | 3 Phase fault on REDCNTP4 (520552) 138 kV Bus a. Apply fault at the REDCNTP4 (520552) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCNTP4 138.0 KV 520552 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | REDCORN4_REDCNTP4 | 3 Phase fault on REDCORN4 (515314) 138 kV Bus a. Apply fault at the REDCORN4 (515314) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCORN4 138.0 KV 515314 TO REDCNTP4 138.0 KV 520552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | REDCORN4_REDCNTP4 | 3 Phase fault on REDCORN4 (515314) 138 kV Bus a. Apply fault at the REDCORN4 (515314) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDCORN4 138.0 KV 515314 TO REDCNTP4 138.0 KV 520552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | REDNGTN7_REDDIRT7_6 | 3 Phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345.0 KV 515875 TO REDDIRT7 345.0 KV 515877 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | REDNGTN7_REDDIRT7_6 | 3 Phase fault on REDNGTN7 (515875) 345 kV Bus a. Apply fault at the REDNGTN7 (515875) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REDNGTN7 345.0 KV 515875 TO REDDIRT7 345.0 KV 515877 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENFROW4_515543 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4( 515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 515544 TO RENFROW7 515543 TO RENFRO11 515545 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENFROW4_515543 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4( 515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 515544 TO RENFROW7 515543 TO RENFRO11 515545 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENFROW4_GRANTCO4 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO GRANTCO4 138.0 KV 515546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENFROW4_GRANTCO4 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO GRANTCO4 138.0 KV 515546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENFROW4_MDFRDTP4 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO MDFRDTP4 138.0 KV 515569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENFROW4_MDFRDTP4 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 138.0 KV 515544 TO MDFRDTP4 138.0 KV 515569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENFROW4_WAKTASW4 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFEC_RNFRO4 138.0 KV 520409 TO WAKTASW4 138.0 KV 520434 CKT 1 b.2. RENFROW4 138.0 KV 515544 TO WFEC_RNFRO4 138.0 KV 520409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENFROW4_WAKTASW4 | 3 Phase fault on RENFROW4 (515544) 138 kV Bus a. Apply fault at the RENFROW4 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFEC_RNFRO4 138.0 KV 520409 TO WAKTASW4 138.0 KV 520434 CKT 1 b.2. RENFROW4 138.0 KV 515544 TO WFEC_RNFRO4 138.0 KV 520409 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENFROW7_515453 | a. Apply single-phase fault on: a.1. RENFROW7 345.0 KV 515543 TO G17-185-TAP 345.0 KV 762262 CKT 1, b. with stuck breaker near RENFROW7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENFROW7_515453 | a. Apply single-phase fault on: a.1. RENFROW7 345.0 KV 515543 TO G17-185-TAP 345.0 KV 762262 CKT 1, b. with stuck breaker near RENFROW7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. HUNTERS7 345.0 KV 515476 TO RENFROW7 345.0 KV 515543 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENFROW7_GEN_2017_203 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GEN-2017-203 345.0 KV 760809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENFROW7_GEN_2017_203 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GEN-2017-203 345.0 KV 760809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENFROW7_GRNTWD_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GRNTWD 7 345.0 KV 515646 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENFROW7_GRNTWD_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO GRNTWD 7 345.0 KV 515646 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENFROW7_VIOLA_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO VIOLA 7 345.0 KV 532798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENFROW7_VIOLA_7_6 | 3 Phase fault on RENFROW7 (515543) 345 kV Bus a. Apply fault at the RENFROW7 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 345.0 KV 515543 TO VIOLA 7 345.0 KV 532798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENO_7_533416_6 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7( 532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 532771 TO RENO 3 533416 TO RENO 2X1 532810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENO_7_533416_6 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7( 532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 532771 TO RENO 3 533416 TO RENO 2X1 532810 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENO_7_G16_111 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 345.0 KV 532771 TO G16-111-TAP 345.0 KV 587884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENO_7_G16_111 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 345.0 KV 532771 TO G16-111-TAP 345.0 KV 587884 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RENO_7_WICHITA7_6 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 345.0 KV 532771 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RENO_7_WICHITA7_6 | 3 Phase fault on RENO 7 (532771) 345 kV Bus a. Apply fault at the RENO 7 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 345.0 KV 532771 TO WICHITA7 345.0 KV 532796 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ROCKYPT2_515164 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ROCKYPT2_515164 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ROCKYPT2_SCMMRCT2 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 69.0 KV 515163 TO SCMMRCT2 69.0 KV 515420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ROCKYPT2_SCMMRCT2 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2 (515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 69.0 KV 515163 TO SCMMRCT2 69.0 KV 515420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ROCKYPT4_515164 | a. Apply single-phase fault on: a.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1, b. with stuck breaker near ROCKYPT4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. ROCKYPT4 138.0 KV 515164 TO SUNNYSD4 138.0 KV 515135 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ROCKYPT4_515164 | a. Apply single-phase fault on: a.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1, b. with stuck breaker near ROCKYPT4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. ROCKYPT4 138.0 KV 515164 TO SUNNYSD4 138.0 KV 515135 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ROCKYPT4_MARIETA4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ROCKYPT4_MARIETA4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 b.2. MRIETA 2 138.0 KV 515160 TO MARIETA4 138.0 KV 520988 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | ROCKYPT4_SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | ROCKYPT4_SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RS_KERR5_SUNSTCN5 | 3 Phase fault on RS KERR5 (505582) 161 kV Bus a. Apply fault at the RS KERR5 (505582) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO SUNSTCN5 161.0 KV 515254 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RS_KERR5_SUNSTCN5 | 3 Phase fault on RS KERR5 (505582) 161 kV Bus a. Apply fault at the RS KERR5 (505582) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RS KERR5 161.0 KV 505582 TO SUNSTCN5 161.0 KV 515254 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS_509782 | a. Apply single-phase fault on: a.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1, b. with stuck breaker near R.S.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS_509782 | a. Apply single-phase fault on: a.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1, b. with stuck breaker near R.S.S.-7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS_T1_4_509782 | 3 Phase fault on RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4( 509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS_T1_4_509782 | 3 Phase fault on RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4( 509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS_T1_4_RSS4 | 3 Phase fault on RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138.0 KV 509773 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS_T1_4_RSS4 | 3 Phase fault on RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138.0 KV 509773 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS_T2_4_509782 | 3 Phase fault on RSS T2 4 (509875) 138 kV Bus a. Apply fault at the RSS T2 4( 509875) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS_T2_4_509782 | 3 Phase fault on RSS T2 4 (509875) 138 kV Bus a. Apply fault at the RSS T2 4( 509875) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS4_RSS_T2_4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS T2 4 138.0 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS4_RSS_T2_4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS T2 4 138.0 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS7_COGENT_7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO COGENT 7 345.0 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS7_COGENT_7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO COGENT 7 345.0 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS7_G16133G16146_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO G16133G16146 345.0 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS7_G16133G16146_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO G16133G16146 345.0 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS7_ONETA_7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS7_ONETA_7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS7_PECANCK7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS7_PECANCK7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS7_REDBUD_7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS7_REDBUD_7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RSS7_SAPLPRD7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RSS7_SAPLPRD7_6 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RUDY_5_NITROTP5 | 3 Phase fault on RUDY 5 (515337) 161 kV Bus a. Apply fault at the RUDY 5 (515337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.2. LOAD 1 515360 b.3. RUDY 5 161.0 KV 515337 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.4. LOAD 1 515360 b.5. ALMA 5 161.0 KV 515334 TO RUDY 5 161.0 KV 515337 CKT 1 b.6. LOAD A1 515337 b.7. DYER 5 161.0 KV 515333 TO ALMA 5 161.0 KV 515334 CKT 1 b.8. LOAD 1 515334 b.9. SIMMONS5 161.0 KV 515332 TO DYER 5 161.0 KV 515333 CKT 1 b.10. LOAD A1 515333 b.11. NITROTP5 161.0 KV 515329 TO SIMMONS5 161.0 KV 515332 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RUDY_5_NITROTP5 | 3 Phase fault on RUDY 5 (515337) 161 kV Bus a. Apply fault at the RUDY 5 (515337) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.2. LOAD 1 515360 b.3. RUDY 5 161.0 KV 515337 TO TWNBRDG5 161.0 KV 515360 CKT 1 b.4. LOAD 1 515360 b.5. ALMA 5 161.0 KV 515334 TO RUDY 5 161.0 KV 515337 CKT 1 b.6. LOAD A1 515337 b.7. DYER 5 161.0 KV 515333 TO ALMA 5 161.0 KV 515334 CKT 1 b.8. LOAD 1 515334 b.9. SIMMONS5 161.0 KV 515332 TO DYER 5 161.0 KV 515333 CKT 1 b.10. LOAD A1 515333 b.11. NITROTP5 161.0 KV 515329 TO SIMMONS5 161.0 KV 515332 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RUSSET4_MADINDT4 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASSES4 138.0 KV 515147 TO MADINDT4 138.0 KV 515149 CKT 1 b.2. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RUSSET4_MADINDT4 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASSES4 138.0 KV 515147 TO MADINDT4 138.0 KV 515149 CKT 1 b.2. RUSSET-4 138.0 KV 515120 TO GLASSES4 138.0 KV 515147 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RUSSET4_RUSSETT4 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RUSSET4_RUSSETT4 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSET-4 138.0 KV 515120 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | RUSSET4_SPRNDAL4 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRPSPRG4 138.0 KV 515873 TO STIRLNG4 138.0 KV 515932 CKT 1 b.2. LOAD 1 515932 b.3. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 b.4. LOAD 1 515932 b.5. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | RUSSET4_SPRNDAL4 | 3 Phase fault on RUSSET-4 (515120) 138 kV Bus a. Apply fault at the RUSSET-4 (515120) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRPSPRG4 138.0 KV 515873 TO STIRLNG4 138.0 KV 515932 CKT 1 b.2. LOAD 1 515932 b.3. RUSSET-4 138.0 KV 515120 TO STIRLNG4 138.0 KV 515932 CKT 1 b.4. LOAD 1 515932 b.5. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | S_BROWN4_505602 | a. Apply single-phase fault on: a.1. S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1, b. with stuck breaker near S BROWN4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. S BROWN4 138.0 KV 505602 TO COLBRTP4 138.0 KV 515159 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | S_BROWN4_505602 | a. Apply single-phase fault on: a.1. S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1, b. with stuck breaker near S BROWN4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. S BROWN4 138.0 KV 505602 TO COLBRTP4 138.0 KV 515159 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | S_BROWN4_BROWN_4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | S_BROWN4_BROWN_4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO BROWN 4 138.0 KV 515157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | S_BROWN4_COLBRTP4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | S_BROWN4_COLBRTP4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO COLBRTP4 138.0 KV 515159 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | S_BROWN4_DENISON4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO DENISON4 138.0 KV 505604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | S_BROWN4_DENISON4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO DENISON4 138.0 KV 505604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | S_BROWN4_KIERSEY4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBERT4 138.0 KV 520860 TO KIERSEY4 138.0 KV 520963 CKT 1 b.2. LOAD 1 520963 b.3. LOAD 2 520963 b.4. S BROWN4 138.0 KV 505602 TO KIERSEY4 138.0 KV 520963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | S_BROWN4_KIERSEY4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLBERT4 138.0 KV 520860 TO KIERSEY4 138.0 KV 520963 CKT 1 b.2. LOAD 1 520963 b.3. LOAD 2 520963 b.4. S BROWN4 138.0 KV 505602 TO KIERSEY4 138.0 KV 520963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | S_BROWN4_RUSSETT4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | S_BROWN4_RUSSETT4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO RUSSETT4 138.0 KV 521044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | S_BROWN4_SCLMNJC4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | S_BROWN4_SCLMNJC4 | 3 Phase fault on S BROWN4 (505602) 138 kV Bus a. Apply fault at the S BROWN4 (505602) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S BROWN4 138.0 KV 505602 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SALTCRK4_SALTTP_4 | 3 Phase fault on SALTCRK4 (515934) 138 kV Bus a. Apply fault at the SALTCRK4 (515934) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTCRK4 138.0 KV 515934 TO SALTTP 4 138.0 KV 520551 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SALTCRK4_SALTTP_4 | 3 Phase fault on SALTCRK4 (515934) 138 kV Bus a. Apply fault at the SALTCRK4 (515934) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTCRK4 138.0 KV 515934 TO SALTTP 4 138.0 KV 520551 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SALTTP_4_ASHLAND4 | 3 Phase fault on SALTTP 4 (520551) 138 kV Bus a. Apply fault at the SALTTP 4 (520551) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTTP 4 138.0 KV 520551 TO ASHLAND4 138.0 KV 520818 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SALTTP_4_ASHLAND4 | 3 Phase fault on SALTTP 4 (520551) 138 kV Bus a. Apply fault at the SALTTP 4 (520551) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALTTP 4 138.0 KV 520551 TO ASHLAND4 138.0 KV 520818 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SAPLPRD4_509870 | 3 Phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4( 509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SAPLPRD4_509870 | 3 Phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4( 509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SARA_4_CIMARON4 | 3 Phase fault on SARA 4 (514895) 138 kV Bus a. Apply fault at the SARA 4 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138.0 KV 514895 TO CIMARON4 138.0 KV 514898 CKT 1 b.2. SARA 4 138.0 KV 514895 TO MCCLAIN4 138.0 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SARA_4_CIMARON4 | 3 Phase fault on SARA 4 (514895) 138 kV Bus a. Apply fault at the SARA 4 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138.0 KV 514895 TO CIMARON4 138.0 KV 514898 CKT 1 b.2. SARA 4 138.0 KV 514895 TO MCCLAIN4 138.0 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SCOLEMN4_SCLMNJC4 | 3 Phase fault on SCOLEMN4 (520463) 138 kV Bus a. Apply fault at the SCOLEMN4 (520463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOLEMN4 138.0 KV 520463 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SCOLEMN4_SCLMNJC4 | 3 Phase fault on SCOLEMN4 (520463) 138 kV Bus a. Apply fault at the SCOLEMN4 (520463) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOLEMN4 138.0 KV 520463 TO SCLMNJC4 138.0 KV 521049 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SCOTTSW4_CALUMET4 | 3 Phase fault on SCOTTSW4 (520899) 138 kV Bus a. Apply fault at the SCOTTSW4 (520899) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138.0 KV 520502 TO CALUMET4 138.0 KV 520839 CKT 1 b.2. LOAD 1 520839 b.3. CANA 4 138.0 KV 520502 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SCOTTSW4_CALUMET4 | 3 Phase fault on SCOTTSW4 (520899) 138 kV Bus a. Apply fault at the SCOTTSW4 (520899) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138.0 KV 520502 TO CALUMET4 138.0 KV 520839 CKT 1 b.2. LOAD 1 520839 b.3. CANA 4 138.0 KV 520502 TO SCOTTSW4 138.0 KV 520899 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL4_515044 | a. Apply single-phase fault on: a.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 a.2. LOAD 1 515977 a.3. LKKONWA4 138.0 KV 515977 TO PARKLN 4 138.0 KV 515178 CKT 1, b. with stuck breaker near SEMINOL4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL4_515044 | a. Apply single-phase fault on: a.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 a.2. LOAD 1 515977 a.3. LKKONWA4 138.0 KV 515977 TO PARKLN 4 138.0 KV 515178 CKT 1, b. with stuck breaker near SEMINOL4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL4_515045 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL4_515045 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL4_MAUD_4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL4_MAUD_4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL4_PAOLI_4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL4_PAOLI_4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL4_PARKLN_4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 b.2. LOAD 1 515977 b.3. PARKLN 4 138.0 KV 515178 TO LKKONWA4 138.0 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL4_PARKLN_4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 b.2. LOAD 1 515977 b.3. PARKLN 4 138.0 KV 515178 TO LKKONWA4 138.0 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL4_VANOSTP4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL4_VANOSTP4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL7_515045 | a. Apply single-phase fault on: a.1. SEMINOL7 345.0 KV 515045 TO PITTSB-7 345.0 KV 510907 CKT 1, b. with stuck breaker near SEMINOL7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. SEMINOL7 345.0 KV 515045 TO ARCADIA7 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL7_515045 | a. Apply single-phase fault on: a.1. SEMINOL7 345.0 KV 515045 TO PITTSB-7 345.0 KV 510907 CKT 1, b. with stuck breaker near SEMINOL7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. SEMINOL7 345.0 KV 515045 TO ARCADIA7 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SEMINOL7_MUSKOGE7_6 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SEMINOL7_MUSKOGE7_6 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SEQUOYAHJ4_ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SEQUOYAHJ4_ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SILOAM_2_506948 | 3 Phase fault on SILOAM 2 (506973) 69 kV Bus a. Apply fault at the SILOAM 2( 506973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM 2 506973 TO SILOAM 5 506948 TO SILOAM-1 506917 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | No | Yes | Yes | High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SILOAM_2_506948 | 3 Phase fault on SILOAM 2 (506973) 69 kV Bus a. Apply fault at the SILOAM 2( 506973) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM 2 506973 TO SILOAM 5 506948 TO SILOAM-1 506917 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | No | Yes | Yes | High Voltage issues observed. | Operational steady state fixes (existing caps/taps/gen set points)
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SILOAM_5_SILMCTY5 | 3 Phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM 5 161.0 KV 506948 TO SILMCTY5 161.0 KV 512643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SILOAM_5_SILMCTY5 | 3 Phase fault on SILOAM 5 (506948) 161 kV Bus a. Apply fault at the SILOAM 5 (506948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAM 5 161.0 KV 506948 TO SILMCTY5 161.0 KV 512643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SILOAMSP_5_CHAMSPR5 | 3 Phase fault on SILOAMSP 5 (504202) 161 kV Bus a. Apply fault at the SILOAMSP 5 (504202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAMSP 5 161.0 KV 504202 TO CHAMSPR5 161.0 KV 506944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SILOAMSP_5_CHAMSPR5 | 3 Phase fault on SILOAMSP 5 (504202) 161 kV Bus a. Apply fault at the SILOAMSP 5 (504202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAMSP 5 161.0 KV 504202 TO CHAMSPR5 161.0 KV 506944 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SILOAMSP_5_FLINTCR5 | 3 Phase fault on SILOAMSP 5 (504202) 161 kV Bus a. Apply fault at the SILOAMSP 5 (504202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAMSP 5 161.0 KV 504202 TO FLINTCR5 161.0 KV 506934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SILOAMSP_5_FLINTCR5 | 3 Phase fault on SILOAMSP 5 (504202) 161 kV Bus a. Apply fault at the SILOAMSP 5 (504202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SILOAMSP 5 161.0 KV 504202 TO FLINTCR5 161.0 KV 506934 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SKYLINE4_QUAILCK4 | 3 Phase fault on SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SKYLINE4_QUAILCK4 | 3 Phase fault on SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SLVRLAK4_BRADEN_4 | 3 Phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO BRADEN 4 138.0 KV 514854 CKT 1 b.2. LOAD 1 514854 b.3. BRADEN 4 138.0 KV 514854 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SLVRLAK4_BRADEN_4 | 3 Phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO BRADEN 4 138.0 KV 514854 CKT 1 b.2. LOAD 1 514854 b.3. BRADEN 4 138.0 KV 514854 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SLVRLAK4_DVISION4 | 3 Phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SLVRLAK4_DVISION4 | 3 Phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SNRPMPT4_SOONER_4 | 3 Phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 138.0 KV 514798 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SNRPMPT4_SOONER_4 | 3 Phase fault on SNRPMPT4 (514798) 138 kV Bus a. Apply fault at the SNRPMPT4 (514798) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SNRPMPT4 138.0 KV 514798 TO SOONER 4 138.0 KV 514802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SO4TH_2_514731 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SO4TH_2_514731 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SO4TH_4_BRECKNR4 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SO4TH_4_BRECKNR4 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SO4TH_4_IMO_4 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SO4TH_4_IMO_4 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SOCPUMP2_LULA_2 | 3 Phase fault on SOCPUMP2 (515183) 69 kV Bus a. Apply fault at the SOCPUMP2 (515183) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOCPUMP2 69.0 KV 515183 TO LULA 2 69.0 KV 515191 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SOCPUMP2_LULA_2 | 3 Phase fault on SOCPUMP2 (515183) 69 kV Bus a. Apply fault at the SOCPUMP2 (515183) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOCPUMP2 69.0 KV 515183 TO LULA 2 69.0 KV 515191 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SOONER_4_514803 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4( 514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SOONER_4_514803 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4( 514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 514802 TO SOONER 7 514803 TO SOONER 1 515760 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SOONER_4_MORISNT4 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 138.0 KV 514802 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SOONER_4_MORISNT4 | 3 Phase fault on SOONER 4 (514802) 138 kV Bus a. Apply fault at the SOONER 4 (514802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOONER 4 138.0 KV 514802 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SOONER_7_514803 | a. Apply single-phase fault on: a.1. G15-066T 345.0 KV 560056 TO SOONER 7 345.0 KV 514803 CKT 1, b. with stuck breaker near SOONER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. SOONER 7 345.0 KV 514803 TO WEKIWA-7 345.0 KV 509755 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SOONER_7_514803 | a. Apply single-phase fault on: a.1. G15-066T 345.0 KV 560056 TO SOONER 7 345.0 KV 514803 CKT 1, b. with stuck breaker near SOONER 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. SOONER 7 345.0 KV 514803 TO WEKIWA-7 345.0 KV 509755 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SOONER_7_G15_066T | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SOONER_7_G15_066T | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G15-066T 345.0 KV 560056 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SOONER_7_G16_119 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SOONER_7_G16_119 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SOONER_7_PINTAIL7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SOONER_7_PINTAIL7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SOONER_7_RANCHRD7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SOONER_7_RANCHRD7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO RANCHRD7 345.0 KV 515576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SOONER_7_THUNDER7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SOONER_7_THUNDER7_6 | 3 Phase fault on SOONER 7 (514803) 345 kV Bus a. Apply fault at the SOONER 7 (514803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SOONER 7 345.0 KV 514803 TO THUNDER7 345.0 KV 515894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SPGVLLY4_CUSHING4 | 3 Phase fault on SPGVLLY4 (515574) 138 kV Bus a. Apply fault at the SPGVLLY4 (515574) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAYNESB4 138.0 KV 515039 TO SPGVLLY4 138.0 KV 515574 CKT 1 b.2. CUSHING4 138.0 KV 515033 TO PAYNESB4 138.0 KV 515039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SPGVLLY4_CUSHING4 | 3 Phase fault on SPGVLLY4 (515574) 138 kV Bus a. Apply fault at the SPGVLLY4 (515574) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAYNESB4 138.0 KV 515039 TO SPGVLLY4 138.0 KV 515574 CKT 1 b.2. CUSHING4 138.0 KV 515033 TO PAYNESB4 138.0 KV 515039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SPRNDAL4_CHIKSAW4 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 b.2. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SPRNDAL4_CHIKSAW4 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FNDTION4 138.0 KV 515162 TO SPRNDAL4 138.0 KV 515172 CKT 1 b.2. FNDTION4 138.0 KV 515162 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SPRNDAL4_DRPSPRG4 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SPRNDAL4_DRPSPRG4 | 3 Phase fault on SPRNDAL4 (515172) 138 kV Bus a. Apply fault at the SPRNDAL4 (515172) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRNDAL4 138.0 KV 515172 TO DRPSPRG4 138.0 KV 515873 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SPRNGCK7_G16_119 | 3 Phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SPRNGCK7_G16_119 | 3 Phase fault on SPRNGCK7 (514881) 345 kV Bus a. Apply fault at the SPRNGCK7 (514881) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRNGCK7 345.0 KV 514881 TO G16-119-TAP 345.0 KV 587804 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2016-119 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | STILWTR4_KINZE_4 | 3 Phase fault on STILWTR4 (515011) 138 kV Bus a. Apply fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCELROY4 138.0 KV 515009 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.2. LOAD 1 515181 b.3. MCELROY4 138.0 KV 515009 TO STILWTR4 138.0 KV 515011 CKT 1 b.4. KINZE 4 138.0 KV 515008 TO UNVRSTY4 138.0 KV 515181 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | STILWTR4_KINZE_4 | 3 Phase fault on STILWTR4 (515011) 138 kV Bus a. Apply fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCELROY4 138.0 KV 515009 TO UNVRSTY4 138.0 KV 515181 CKT 1 b.2. LOAD 1 515181 b.3. MCELROY4 138.0 KV 515009 TO STILWTR4 138.0 KV 515011 CKT 1 b.4. KINZE 4 138.0 KV 515008 TO UNVRSTY4 138.0 KV 515181 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | STILWTR4_MORISNT4 | 3 Phase fault on STILWTR4 (515011) 138 kV Bus a. Apply fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | STILWTR4_MORISNT4 | 3 Phase fault on STILWTR4 (515011) 138 kV Bus a. Apply fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO MORISNT4 138.0 KV 515447 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | STILWTR4_SPGVLLY4 | 3 Phase fault on STILWTR4 (515011) 138 kV Bus a. Apply fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO SPGVLLY4 138.0 KV 515574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | STILWTR4_SPGVLLY4 | 3 Phase fault on STILWTR4 (515011) 138 kV Bus a. Apply fault at the STILWTR4 (515011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWTR4 138.0 KV 515011 TO SPGVLLY4 138.0 KV 515574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | STNWLSW4_STNWLTP4 | 3 Phase fault on STNWLSW4 (521071) 138 kV Bus a. Apply fault at the STNWLSW4 (521071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWLSW4 138.0 KV 521071 TO STNWLTP4 138.0 KV 521075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | STNWLSW4_STNWLTP4 | 3 Phase fault on STNWLSW4 (521071) 138 kV Bus a. Apply fault at the STNWLSW4 (521071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWLSW4 138.0 KV 521071 TO STNWLTP4 138.0 KV 521075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | STNWLTP4_WAPANUCKA_4 | 3 Phase fault on STNWLTP4 (521075) 138 kV Bus a. Apply fault at the STNWLTP4 (521075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAPANUCKA 4 138.0 KV 510949 TO BOGGY4 138.0 KV 521074 CKT 1 b.2. WAPANUCKA 4 138.0 KV 510949 TO STNWLTP4 138.0 KV 521075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | STNWLTP4_WAPANUCKA_4 | 3 Phase fault on STNWLTP4 (521075) 138 kV Bus a. Apply fault at the STNWLTP4 (521075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAPANUCKA 4 138.0 KV 510949 TO BOGGY4 138.0 KV 521074 CKT 1 b.2. WAPANUCKA 4 138.0 KV 510949 TO STNWLTP4 138.0 KV 521075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUBIACT5_SUBIACO5 | 3 Phase fault on SUBIACT5 (515440) 161 kV Bus a. Apply fault at the SUBIACT5 (515440) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUBIACT5 161.0 KV 515440 TO SUBIACO5 161.0 KV 515441 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUBIACT5_SUBIACO5 | 3 Phase fault on SUBIACT5 (515440) 161 kV Bus a. Apply fault at the SUBIACT5 (515440) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUBIACT5 161.0 KV 515440 TO SUBIACO5 161.0 KV 515441 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUMNER_4_GEN_2017_121 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 138.0 KV 532984 TO GEN-2017-121 138.0 KV 761838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUMNER_4_GEN_2017_121 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 138.0 KV 532984 TO GEN-2017-121 138.0 KV 761838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUMNER_4_SC10BEL4 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 138.0 KV 532984 TO SC10BEL4 138.0 KV 533063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUMNER_4_SC10BEL4 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 138.0 KV 532984 TO SC10BEL4 138.0 KV 533063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUMNER_4_TIMBJCT4 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 138.0 KV 532984 TO TIMBJCT4 138.0 KV 532992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUMNER_4_TIMBJCT4 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 138.0 KV 532984 TO TIMBJCT4 138.0 KV 532992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUMNER_4_VIOLA_4 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 138.0 KV 532984 TO VIOLA 4 138.0 KV 533075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUMNER_4_VIOLA_4 | 3 Phase fault on SUMNER 4 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 138.0 KV 532984 TO VIOLA 4 138.0 KV 533075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4_515135 | a. Apply single-phase fault on: a.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1, b. with stuck breaker near SUNNYSD4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 c.2. LOAD 1 515137 c.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 c.4. LOAD 1 515372 c.5. ARDWEST4 138.0 KV 515372 TO CARTER 4 138.0 KV 515138 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4_515135 | a. Apply single-phase fault on: a.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1, b. with stuck breaker near SUNNYSD4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 c.2. LOAD 1 515137 c.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 c.4. LOAD 1 515372 c.5. ARDWEST4 138.0 KV 515372 TO CARTER 4 138.0 KV 515138 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4_515136_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4_515136_7 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4_CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4_CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4_CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4_CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4_CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4_CHEEKTP4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 b.2. LOAD 1 515144 b.3. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD4_ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD4_ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD7_515135 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD7_515135 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD7_G16_063 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD7_G16_063 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 trips on voltage protection settings | Disabling instantaneous voltage protection settings for GEN-2017-027 prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNNYSD7_GEN_2017_167_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNNYSD7_GEN_2017_167_6 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-167 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNSHIN4_521059 | a. Apply single-phase fault on: a.1. EL RENO4 138.0 KV 520893 TO MUSTANG4 138.0 KV 520412 CKT 1 a.2. LOAD 1 520412 a.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 a.4. LOAD 1 521005 a.5. SUNSHIN4 138.0 KV 521059 TO SARA RD4 138.0 KV 521005 CKT 1, b. with stuck breaker near SUNSHIN4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SUNSHIN4 138.0 KV 521059 TO BRIDGCR4 138.0 KV 520501 CKT 1 c.2. LOAD 1 520501 c.3. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNSHIN4_521059 | a. Apply single-phase fault on: a.1. EL RENO4 138.0 KV 520893 TO MUSTANG4 138.0 KV 520412 CKT 1 a.2. LOAD 1 520412 a.3. MUSTANG4 138.0 KV 520412 TO SARA RD4 138.0 KV 521005 CKT 1 a.4. LOAD 1 521005 a.5. SUNSHIN4 138.0 KV 521059 TO SARA RD4 138.0 KV 521005 CKT 1, b. with stuck breaker near SUNSHIN4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. SUNSHIN4 138.0 KV 521059 TO BRIDGCR4 138.0 KV 520501 CKT 1 c.2. LOAD 1 520501 c.3. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNSHIN4_FRNKLNS4 | 3 Phase fault on SUNSHIN4 (521059) 138 kV Bus a. Apply fault at the SUNSHIN4 (521059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.5. LOAD 1 521123 b.6. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNSHIN4_FRNKLNS4 | 3 Phase fault on SUNSHIN4 (521059) 138 kV Bus a. Apply fault at the SUNSHIN4 (521059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAILEY4 138.0 KV 520401 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. BAILEY4 138.0 KV 520401 TO WMOORE 4 138.0 KV 521123 CKT 1 b.5. LOAD 1 521123 b.6. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SUNSHIN4_TUTLETP4 | 3 Phase fault on SUNSHIN4 (521059) 138 kV Bus a. Apply fault at the SUNSHIN4 (521059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SUNSHIN4_TUTLETP4 | 3 Phase fault on SUNSHIN4 (521059) 138 kV Bus a. Apply fault at the SUNSHIN4 (521059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO SUNSHIN4 138.0 KV 521059 CKT 1 b.2. LOAD 1 521059 b.3. LOAD 2 521059 b.4. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SW4_ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SW4_ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN units trips on voltage protection settings | Disabling instantaneous voltage protection settings for BLUCAN units prevents trip. There are no stability constraints when this generator trips offline or when the protection settings are disabled to prevent it from tripping. It is recommended that generators are submitted with data that is in compliance with PRC standards and IEEE 2800.
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | SXMLCKT4_HOWE_4 | 3 Phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | SXMLCKT4_HOWE_4 | 3 Phase fault on SXMLCKT4 (515122) 138 kV Bus a. Apply fault at the SXMLCKT4 (515122) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SXMLCKT4 138.0 KV 515122 TO HOWE 4 138.0 KV 521122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TAHLQH_5_512647 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5( 512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TAHLQH_5_512647 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5( 512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TAHLQH_5_7CLANS_5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TAHLQH_5_7CLANS_5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TAHLQH_5_BRIGSKM_5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TAHLQH_5_BRIGSKM_5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TAHLQH_5_HWY59TP5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TAHLQH_5_HWY59TP5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TATONGA7_CRSRDSW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TATONGA7_CRSRDSW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TATONGA7_MAMTHPW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TATONGA7_MAMTHPW7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TATONGA7_MATHWSN7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TATONGA7_MATHWSN7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TATONGA7_SLNGWND7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TATONGA7_SLNGWND7_6 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TERRYRD7_G17_171 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TERRYRD7_G17_171 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TERRYRD7_RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TERRYRD7_RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TERRYRD7_RUSHSPR7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TERRYRD7_RUSHSPR7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TERRYRD7_SUNNYSD7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TERRYRD7_SUNNYSD7_6 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | THUNDER7_515890 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | THUNDER7_515890 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL11 515890 TO THNDRT11 515892 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | THUNDER7_515891 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | THUNDER7_515891 | 3 Phase fault on THUNDER7 (515894) 345 kV Bus a. Apply fault at the THUNDER7( 515894) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THUNDER7 515894 TO THNDRL21 515891 TO THNDRT21 515893 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TNO24_509852 | 3 Phase fault on T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4( 509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TNO24_509852 | 3 Phase fault on T.NO.2-4 (509895) 138 kV Bus a. Apply fault at the T.NO.2-4( 509895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.NO.2-4 509895 TO T.NO.--7 509852 TO TNO2-1 509894 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TNO7_CLEVLND7_6 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO CLEVLND7 345.0 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TNO7_CLEVLND7_6 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO CLEVLND7 345.0 KV 512694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TNO7_IGLOOV_7_6 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO IGLOOV 7 345.0 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TNO7_IGLOOV_7_6 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO IGLOOV 7 345.0 KV 513596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TNO7_NE7_6 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TNO7_NE7_6 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TONTITN5_506959 | 3 Phase fault on TONTITN5 (506957) 161 kV Bus a. Apply fault at the TONTITN5( 506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONTITN5 506957 TO TONTITN7 506959 TO TONTITN1 506958 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TONTITN5_506959 | 3 Phase fault on TONTITN5 (506957) 161 kV Bus a. Apply fault at the TONTITN5( 506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONTITN5 506957 TO TONTITN7 506959 TO TONTITN1 506958 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TONTITN5_BRUSHCRK_5 | 3 Phase fault on TONTITN5 (506957) 161 kV Bus a. Apply fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONTITN5 161.0 KV 506957 TO BRUSHCRK_5 161.0 KV 506991 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TONTITN5_BRUSHCRK_5 | 3 Phase fault on TONTITN5 (506957) 161 kV Bus a. Apply fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONTITN5 161.0 KV 506957 TO BRUSHCRK_5 161.0 KV 506991 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TONTITN5_MATTISN5 | 3 Phase fault on TONTITN5 (506957) 161 kV Bus a. Apply fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONTITN5 161.0 KV 506957 TO MATTISN5 161.0 KV 506978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TONTITN5_MATTISN5 | 3 Phase fault on TONTITN5 (506957) 161 kV Bus a. Apply fault at the TONTITN5 (506957) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TONTITN5 161.0 KV 506957 TO MATTISN5 161.0 KV 506978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TOTAL_4_CHIKSAW4 | 3 Phase fault on TOTAL 4 (515165) 138 kV Bus a. Apply fault at the TOTAL 4 (515165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOTAL 4 138.0 KV 515165 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TOTAL_4_CHIKSAW4 | 3 Phase fault on TOTAL 4 (515165) 138 kV Bus a. Apply fault at the TOTAL 4 (515165) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOTAL 4 138.0 KV 515165 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TRAVERSE3_587301 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3( 900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 900001 TO G16-045XFMR1 587301 TO TRAV3 TER1 900011 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TRAVERSE3_587301 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3( 900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 900001 TO G16-045XFMR1 587301 TO TRAV3 TER1 900011 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TRAVERSE3_TRW2 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 345.0 KV 900001 TO TRW2-TRW3 345.0 KV 900004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TRAVERSE3_TRW2 | 3 Phase fault on TRAVERSE3 (900001) 345 kV Bus a. Apply fault at the TRAVERSE3 (900001) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRAVERSE3 345.0 KV 900001 TO TRW2-TRW3 345.0 KV 900004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TRYON_4_515675 | a. Apply single-phase fault on: a.1. TRYON 4 138.0 KV 515675 TO KNIPE 4 138.0 KV 515514 CKT 1 a.2. LOAD 1 515514 a.3. KNIPE 4 138.0 KV 515514 TO SPGVLLY4 138.0 KV 515574 CKT 1, b. with stuck breaker near TRYON 4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. TRYON 4 138.0 KV 515675 TO LNWOODT4 138.0 KV 515453 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TRYON_4_515675 | a. Apply single-phase fault on: a.1. TRYON 4 138.0 KV 515675 TO KNIPE 4 138.0 KV 515514 CKT 1 a.2. LOAD 1 515514 a.3. KNIPE 4 138.0 KV 515514 TO SPGVLLY4 138.0 KV 515574 CKT 1, b. with stuck breaker near TRYON 4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. TRYON 4 138.0 KV 515675 TO LNWOODT4 138.0 KV 515453 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TRYON_4_GEN_2017_230 | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TRYON 4 138.0 KV 515675 TO GEN-2017-230 138.0 KV 762195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TRYON_4_GEN_2017_230 | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TRYON 4 138.0 KV 515675 TO GEN-2017-230 138.0 KV 762195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TRYON_4_SPGVLLY4 | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNIPE 4 138.0 KV 515514 TO TRYON 4 138.0 KV 515675 CKT 1 b.2. KNIPE 4 138.0 KV 515514 TO SPGVLLY4 138.0 KV 515574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TRYON_4_SPGVLLY4 | 3 Phase fault on TRYON 4 (515675) 138 kV Bus a. Apply fault at the TRYON 4 (515675) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNIPE 4 138.0 KV 515514 TO TRYON 4 138.0 KV 515675 CKT 1 b.2. KNIPE 4 138.0 KV 515514 TO SPGVLLY4 138.0 KV 515574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT_7_525832 | a. Apply single-phase fault on: a.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1, b. with stuck breaker near TUCO_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT_7_525832 | a. Apply single-phase fault on: a.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1, b. with stuck breaker near TUCO_INT 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUCO_INT_7_G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUCO_INT_7_G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUPELO_4_505600 | a. Apply single-phase fault on: a.1. TUPELO 4 138.0 KV 505600 TO STNWLSW4 138.0 KV 521071 CKT 1, b. with stuck breaker near TUPELO 4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. TUPELO 4 138.0 KV 505600 TO ALLENGT4 138.0 KV 510881 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUPELO_4_505600 | a. Apply single-phase fault on: a.1. TUPELO 4 138.0 KV 505600 TO STNWLSW4 138.0 KV 521071 CKT 1, b. with stuck breaker near TUPELO 4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. TUPELO 4 138.0 KV 505600 TO ALLENGT4 138.0 KV 510881 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUPELO_4_ALLENGT4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUPELO_4_ALLENGT4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO ALLENGT4 138.0 KV 510881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUPELO_4_BOGGY4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUPELO_4_BOGGY4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO BOGGY4 138.0 KV 521074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUPELO_4_CENTRATAP4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO CENTRATAP4 138.0 KV 505665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUPELO_4_CENTRATAP4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO CENTRATAP4 138.0 KV 505665 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUPELO_4_S_BROWN4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO S BROWN4 138.0 KV 505602 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUPELO_4_S_BROWN4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO S BROWN4 138.0 KV 505602 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUPELO_4_SALTTP_4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 520406 TO COLGATE4 138.0 KV 520862 CKT 1 b.2. LOAD 1P 520862 b.3. SALTTP 4 138.0 KV 520551 TO COLGATE4 138.0 KV 520862 CKT 1 b.4. LOAD 1P 520862 b.5. TUPELO 4 138.0 KV 505600 TO TUPELO 4 138.0 KV 520406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUPELO_4_SALTTP_4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 520406 TO COLGATE4 138.0 KV 520862 CKT 1 b.2. LOAD 1P 520862 b.3. SALTTP 4 138.0 KV 520551 TO COLGATE4 138.0 KV 520862 CKT 1 b.4. LOAD 1P 520862 b.5. TUPELO 4 138.0 KV 505600 TO TUPELO 4 138.0 KV 520406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUPELO_4_STNWLSW4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUPELO_4_STNWLSW4 | 3 Phase fault on TUPELO 4 (505600) 138 kV Bus a. Apply fault at the TUPELO 4 (505600) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUPELO 4 138.0 KV 505600 TO STNWLSW4 138.0 KV 521071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TURK_7_NWTXARK7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TURK_7_NWTXARK7_6 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUTCONT4_CEMRD_TP4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CEMRD_TP4 138.0 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUTCONT4_CEMRD_TP4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CEMRD_TP4 138.0 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUTCONT4_CIMARON4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUTCONT4_CIMARON4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUTCONT4_TUTTLE4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO TUTTLE4 138.0 KV 511501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUTCONT4_TUTTLE4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO TUTTLE4 138.0 KV 511501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUTLETP4_ANADARK4 | 3 Phase fault on TUTLETP4 (521072) 138 kV Bus a. Apply fault at the TUTLETP4 (521072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 b.2. LOAD 1 521031 b.3. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUTLETP4_ANADARK4 | 3 Phase fault on TUTLETP4 (521072) 138 kV Bus a. Apply fault at the TUTLETP4 (521072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 b.2. LOAD 1 521031 b.3. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | TUTTLE_4_TUTLETP4 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | TUTTLE_4_TUTLETP4 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VALIANT2_510918 | 3 Phase fault on VALIANT2 (510910) 69 kV Bus a. Apply fault at the VALIANT2( 510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT2 510910 TO VALIANT4 510918 TO VALN1-1 510937 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VALIANT2_510918 | 3 Phase fault on VALIANT2 (510910) 69 kV Bus a. Apply fault at the VALIANT2( 510910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT2 510910 TO VALIANT4 510918 TO VALN1-1 510937 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VALIANT4_510911 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VALIANT4_510911 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VALIANT4_HUGO_PP4 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 138.0 KV 510918 TO HUGO PP4 138.0 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VALIANT4_HUGO_PP4 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4 (510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 138.0 KV 510918 TO HUGO PP4 138.0 KV 520948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VALIANT7_510911 | a. Apply single-phase fault on: a.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1, b. with stuck breaker near VALIANT7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VALIANT7_510911 | a. Apply single-phase fault on: a.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1, b. with stuck breaker near VALIANT7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VALIANT7_HUGO_7_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VALIANT7_HUGO_7_6 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VAN_BUR5_505522 | a. Apply single-phase fault on: a.1. VAN BUR5 161.0 KV 505522 TO VBI5 161.1 KV 515339 CKT Z1, b. with stuck breaker near VAN BUR5 161 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. RS KERR5 161.0 KV 505582 TO VAN BUR5 161.0 KV 505522 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VAN_BUR5_505522 | a. Apply single-phase fault on: a.1. VAN BUR5 161.0 KV 505522 TO VBI5 161.1 KV 515339 CKT Z1, b. with stuck breaker near VAN BUR5 161 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. RS KERR5 161.0 KV 505582 TO VAN BUR5 161.0 KV 505522 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VAN_BUR5_LIBERTY5 | 3 Phase fault on VAN BUR5 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO LIBERTY5 161.0 KV 505524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VAN_BUR5_LIBERTY5 | 3 Phase fault on VAN BUR5 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO LIBERTY5 161.0 KV 505524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VAN_BUR5_RS_KERR5 | 3 Phase fault on VAN BUR5 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VAN_BUR5_RS_KERR5 | 3 Phase fault on VAN BUR5 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO RS KERR5 161.0 KV 505582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VAN_BUR5_VBI_5 | 3 Phase fault on VAN BUR5 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO VBI 5 161.0 KV 515339 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VAN_BUR5_VBI_5 | 3 Phase fault on VAN BUR5 (505522) 161 kV Bus a. Apply fault at the VAN BUR5 (505522) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VAN BUR5 161.0 KV 505522 TO VBI 5 161.0 KV 515339 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VANOSS_4_PARKLN_4 | 3 Phase fault on VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VANOSS_4_PARKLN_4 | 3 Phase fault on VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO PARKLN 4 138.0 KV 515178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VANOSS_4_VANOSTP4 | 3 Phase fault on VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VANOSS_4_VANOSTP4 | 3 Phase fault on VANOSS 4 (515174) 138 kV Bus a. Apply fault at the VANOSS 4 (515174) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VANOSS 4 138.0 KV 515174 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VBAVEC_2_VBI_2 | 3 Phase fault on VBAVEC 2 (515298) 69 kV Bus a. Apply fault at the VBAVEC 2 (515298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBAVEC 2 69.0 KV 515298 TO VBI 2 69.0 KV 515336 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VBAVEC_2_VBI_2 | 3 Phase fault on VBAVEC 2 (515298) 69 kV Bus a. Apply fault at the VBAVEC 2 (515298) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBAVEC 2 69.0 KV 515298 TO VBI 2 69.0 KV 515336 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VBI_2_515339 | 3 Phase fault on VBI 2 (515336) 69 kV Bus a. Apply fault at the VBI 2( 515336) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 515336 TO VBI 5 515339 TO VBI 1 515769 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VBI_2_515339 | 3 Phase fault on VBI 2 (515336) 69 kV Bus a. Apply fault at the VBI 2( 515336) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 2 515336 TO VBI 5 515339 TO VBI 1 515769 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VBI_5_ADABELL5 | 3 Phase fault on VBI 5 (515339) 161 kV Bus a. Apply fault at the VBI 5 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NALCOTP5 161.0 KV 515348 TO ADABELL5 161.0 KV 515406 CKT 1 b.2. LOAD 1 515406 b.3. VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VBI_5_ADABELL5 | 3 Phase fault on VBI 5 (515339) 161 kV Bus a. Apply fault at the VBI 5 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NALCOTP5 161.0 KV 515348 TO ADABELL5 161.0 KV 515406 CKT 1 b.2. LOAD 1 515406 b.3. VBI 5 161.0 KV 515339 TO ADABELL5 161.0 KV 515406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VBI_5_GRNDPRT5 | 3 Phase fault on VBI 5 (515339) 161 kV Bus a. Apply fault at the VBI 5 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VBI_5_GRNDPRT5 | 3 Phase fault on VBI 5 (515339) 161 kV Bus a. Apply fault at the VBI 5 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO GRNDPRT5 161.0 KV 515524 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VBI_5_HWY59TP5 | 3 Phase fault on VBI 5 (515339) 161 kV Bus a. Apply fault at the VBI 5 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VBI_5_HWY59TP5 | 3 Phase fault on VBI 5 (515339) 161 kV Bus a. Apply fault at the VBI 5 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI 5 161.0 KV 515339 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VBI_5_MASSARD5 | 3 Phase fault on VBI 5 (515339) 161 kV Bus a. Apply fault at the VBI 5 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKGROV5 161.0 KV 515340 TO WHITESD5 161.0 KV 515341 CKT 1 b.2. LOAD 1 515341 b.3. WHITESD5 161.0 KV 515341 TO MASSARD5 161.0 KV 515343 CKT 1 b.4. LOAD 1 515343 b.5. VBI 5 161.0 KV 515339 TO OAKGROV5 161.0 KV 515340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VBI_5_MASSARD5 | 3 Phase fault on VBI 5 (515339) 161 kV Bus a. Apply fault at the VBI 5 (515339) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKGROV5 161.0 KV 515340 TO WHITESD5 161.0 KV 515341 CKT 1 b.2. LOAD 1 515341 b.3. WHITESD5 161.0 KV 515341 TO MASSARD5 161.0 KV 515343 CKT 1 b.4. LOAD 1 515343 b.5. VBI 5 161.0 KV 515339 TO OAKGROV5 161.0 KV 515340 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VBI_N_2_VBI_2 | 3 Phase fault on VBI_N 2 (504032) 69 kV Bus a. Apply fault at the VBI_N 2 (504032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI_N 2 69.0 KV 504032 TO VBI 2 69.0 KV 515336 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VBI_N_2_VBI_2 | 3 Phase fault on VBI_N 2 (504032) 69 kV Bus a. Apply fault at the VBI_N 2 (504032) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VBI_N 2 69.0 KV 504032 TO VBI 2 69.0 KV 515336 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VBI5_515339 | a. Apply single-phase fault on: a.1. 515339 TO VAN BUR5 161.0 KV 505522 CKT Z1, b. with stuck breaker near VBI 5 161 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. 515339 TO HWY59TP5 161.0 KV 515527 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VBI5_515339 | a. Apply single-phase fault on: a.1. 515339 TO VAN BUR5 161.0 KV 505522 CKT Z1, b. with stuck breaker near VBI 5 161 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. 515339 TO HWY59TP5 161.0 KV 515527 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VIOLA_4_533075 | a. Apply single-phase fault on: a.1. CLEARWT4 138.0 KV 533036 TO VIOLA 4 138.0 KV 533075 CKT 1, b. with stuck breaker near VIOLA 4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. VIOLA 4 138.0 KV 533075 TO CONWAY 138.0 KV 539009 CKT 1 c.2. LOAD 1 539009 c.3. CONWAY 138.0 KV 539009 TO MILANTP4 138.0 KV 539675 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VIOLA_4_533075 | a. Apply single-phase fault on: a.1. CLEARWT4 138.0 KV 533036 TO VIOLA 4 138.0 KV 533075 CKT 1, b. with stuck breaker near VIOLA 4 138 kV for 7 cycles c. Clear Fault after 10 cycles and trip: c.1. VIOLA 4 138.0 KV 533075 TO CONWAY 138.0 KV 539009 CKT 1 c.2. LOAD 1 539009 c.3. CONWAY 138.0 KV 539009 TO MILANTP4 138.0 KV 539675 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VIOLA_4_CONWAY | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONWAY 138.0 KV 539009 TO MILANTP4 138.0 KV 539675 CKT 1 b.2. VIOLA 4 138.0 KV 533075 TO CONWAY 138.0 KV 539009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VIOLA_4_CONWAY | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CONWAY 138.0 KV 539009 TO MILANTP4 138.0 KV 539675 CKT 1 b.2. VIOLA 4 138.0 KV 533075 TO CONWAY 138.0 KV 539009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VIOLA_4_MILAN_GOAB | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 138.0 KV 533075 TO MILAN_GOAB 138.0 KV 539008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VIOLA_4_MILAN_GOAB | 3 Phase fault on VIOLA 4 (533075) 138 kV Bus a. Apply fault at the VIOLA 4 (533075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 138.0 KV 533075 TO MILAN_GOAB 138.0 KV 539008 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VIOLA_7_532798 | a. Apply single-phase fault on: a.1. VIOLA7 345.0 KV 532798 TO RENFROW7 345.0 KV 515543 CKT 1, b. with stuck breaker near VIOLA 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. VIOLA7 345.0 KV 532798 TO WICHITA7 345.0 KV 532796 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VIOLA_7_532798 | a. Apply single-phase fault on: a.1. VIOLA7 345.0 KV 532798 TO RENFROW7 345.0 KV 515543 CKT 1, b. with stuck breaker near VIOLA 7 345 kV for 6 cycles c. Clear Fault after 10 cycles and trip: c.1. VIOLA7 345.0 KV 532798 TO WICHITA7 345.0 KV 532796 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | VIOLA_7_533075 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7( 532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 532798 TO VIOLA 4 533075 TO VIOL2X1 532833 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | VIOLA_7_533075 | 3 Phase fault on VIOLA 7 (532798) 345 kV Bus a. Apply fault at the VIOLA 7( 532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 532798 TO VIOLA 4 533075 TO VIOL2X1 532833 CKT 2 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | V-WEYCO__VALIANT | 3 Phase fault on V-WEYCO4 (510866) 138 kV Bus a. Apply fault at the V-WEYCO4 (510866) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. V-WEYCO4 138.0 KV 510866 TO VALIANT4 138.0 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | V-WEYCO__VALIANT | 3 Phase fault on V-WEYCO4 (510866) 138 kV Bus a. Apply fault at the V-WEYCO4 (510866) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. V-WEYCO4 138.0 KV 510866 TO VALIANT4 138.0 KV 510918 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WAKTASW4_521085 | 3 Phase fault on WAKTASW4 (520434) 138 kV Bus a. Apply fault at the WAKTASW4( 520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 520434 TO WAKITA 2 521085 TO WAKITA_13.8 520435 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WAKTASW4_521085 | 3 Phase fault on WAKTASW4 (520434) 138 kV Bus a. Apply fault at the WAKTASW4( 520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 520434 TO WAKITA 2 521085 TO WAKITA_13.8 520435 CKT 1 Three winding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WAKTASW4_BYRONTP4 | 3 Phase fault on WAKTASW4 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 138.0 KV 520434 TO WAKTASB4 138.0 KV 520452 CKT 1 b.2. LOAD 1 520452 b.3. SANDYCR4 138.0 KV 520433 TO WAKTASB4 138.0 KV 520452 CKT 1 b.4. LOAD 1 520452 b.5. SANDYCR4 138.0 KV 520433 TO UNIONVL4 138.0 KV 520453 CKT 1 b.6. LOAD 1 520453 b.7. BYRONTP4 138.0 KV 520432 TO UNIONVL4 138.0 KV 520453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WAKTASW4_BYRONTP4 | 3 Phase fault on WAKTASW4 (520434) 138 kV Bus a. Apply fault at the WAKTASW4 (520434) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAKTASW4 138.0 KV 520434 TO WAKTASB4 138.0 KV 520452 CKT 1 b.2. LOAD 1 520452 b.3. SANDYCR4 138.0 KV 520433 TO WAKTASB4 138.0 KV 520452 CKT 1 b.4. LOAD 1 520452 b.5. SANDYCR4 138.0 KV 520433 TO UNIONVL4 138.0 KV 520453 CKT 1 b.6. LOAD 1 520453 b.7. BYRONTP4 138.0 KV 520432 TO UNIONVL4 138.0 KV 520453 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WARWICK4_BRISTOW4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYWEST4 138.0 KV 515048 TO BELLCOW4 138.0 KV 515369 CKT 1 b.2. LOAD 1 515369 b.3. WARWICK4 138.0 KV 515047 TO BELLCOW4 138.0 KV 515369 CKT 1 b.4. LOAD 1 515369 b.5. BRISTOW4 138.0 KV 515035 TO KEYWEST4 138.0 KV 515048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WARWICK4_BRISTOW4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYWEST4 138.0 KV 515048 TO BELLCOW4 138.0 KV 515369 CKT 1 b.2. LOAD 1 515369 b.3. WARWICK4 138.0 KV 515047 TO BELLCOW4 138.0 KV 515369 CKT 1 b.4. LOAD 1 515369 b.5. BRISTOW4 138.0 KV 515035 TO KEYWEST4 138.0 KV 515048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25S | Transfer | WARWICK4_TRYON_4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO TRYON 4 138.0 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 SOUTHEAST | DISIS-2017-002 CF | 25W | Transfer | WARWICK4_TRYON_4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO TRYON 4 138.0 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes