04 - Southeast | 25W | Transfer | FTSMTHE5__FTSMTHW5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSMTHE5__QUANXTP5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSMTHE5__QUANXTP5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO QUANXTP5 161.0 KV 515310 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSMTHW5__515302_0 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5( 515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSMTHW5__515302_0 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5( 515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH7 515302 TO FTSMTH51 515728 CKT 5 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSMTHW5__515305_0 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5( 515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSMTHW5__515305_0 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5( 515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 515301 TO FTSMITH8 515305 TO FTSMTH41 515791 CKT 4 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSMTHW5__ARKOMA_5 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161.0 KV 515301 TO ARKOMA 5 161.0 KV 515306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSMTHW5__ARKOMA_5 | 3 Phase fault on FTSMTHW5 (515301) 161 kV Bus a. Apply fault at the FTSMTHW5 (515301) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHW5 161.0 KV 515301 TO ARKOMA 5 161.0 KV 515306 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G07621119_20__GREAT_WESTRN | 3 Phase fault on G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345.0 KV 515599 TO GREAT_WESTRN 345.0 KV 585410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G07621119_20__GREAT_WESTRN | 3 Phase fault on G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345.0 KV 515599 TO GREAT_WESTRN 345.0 KV 585410 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G07621119_20__PRSIMN_CRK1 | 3 Phase fault on G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345.0 KV 515599 TO PRSIMN_CRK1 345.0 KV 585430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | G07621119_20__PRSIMN_CRK1 | 3 Phase fault on G07621119-20 (515599) 345 kV Bus a. Apply fault at the G07621119-20 (515599) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G07621119-20 345.0 KV 515599 TO PRSIMN_CRK1 345.0 KV 585430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | G16_003_TAP__GEN_2016_003 | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345.0 KV 560071 TO GEN-2016-003 345.0 KV 587020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | G16_003_TAP__GEN_2016_003 | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345.0 KV 560071 TO GEN-2016-003 345.0 KV 587020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | G16_003_TAP__GEN_2017_011 | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345.0 KV 560071 TO GEN-2017-011 345.0 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G16_003_TAP__GEN_2017_011 | 3 Phase fault on G16-003-TAP (560071) 345 kV Bus a. Apply fault at the G16-003-TAP (560071) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-003-TAP 345.0 KV 560071 TO GEN-2017-011 345.0 KV 588560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | G16_037_TAP__GEN_2018_021 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2018-021 345.0 KV 762570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | G16_037_TAP__GEN_2018_021 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2018-021 345.0 KV 762570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | G16_063_TAP__GEN_2016_063 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2016-063 345.0 KV 587430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G16_063_TAP__GEN_2016_063 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2016-063 345.0 KV 587430 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G16_063_TAP__GEN_2017_075 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | G16_063_TAP__GEN_2017_075 | 3 Phase fault on G16-063-TAP (560088) 345 kV Bus a. Apply fault at the G16-063-TAP (560088) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-063-TAP 345.0 KV 560088 TO GEN-2017-075 345.0 KV 589130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | G16_091_TAP__GEN_2016_095 | 3 Phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345.0 KV 587744 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G16_091_TAP__GEN_2016_095 | 3 Phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345.0 KV 587744 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G16133G16146__G16133_345GS | 3 Phase fault on G16133G16146 (588039) 345 kV Bus a. Apply fault at the G16133G16146 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 345.0 KV 588039 TO G16133_345GS 345.0 KV 588040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | G16133G16146__G16133_345GS | 3 Phase fault on G16133G16146 (588039) 345 kV Bus a. Apply fault at the G16133G16146 (588039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16133G16146 345.0 KV 588039 TO G16133_345GS 345.0 KV 588040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G17_092_SWYD__FIREWHL_TAP | 3 Phase fault on G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | G17_092_SWYD__FIREWHL_TAP | 3 Phase fault on G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | G17_092_SWYD__GEN_2017_092 | 3 Phase fault on G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2017-092 345.0 KV 589300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | G17_092_SWYD__GEN_2017_092 | 3 Phase fault on G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2017-092 345.0 KV 589300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | G17_092_SWYD__GEN_2018_024 | 3 Phase fault on G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2018-024 345.0 KV 762592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G17_092_SWYD__GEN_2018_024 | 3 Phase fault on G17-092-SWYD (588838) 345 kV Bus a. Apply fault at the G17-092-SWYD (588838) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-092-SWYD 345.0 KV 588838 TO GEN-2018-024 345.0 KV 762592 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2016_091__G16_091_TAP | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | GEN_2016_091__G16_091_TAP | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | GEN_2016_167__G16_167_TAP | 3 Phase fault on GEN-2016-167 (588400) 138 kV Bus a. Apply fault at the GEN-2016-167 (588400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2016-167 138.0 KV 588400 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2016_167__G16_167_TAP | 3 Phase fault on GEN-2016-167 (588400) 138 kV Bus a. Apply fault at the GEN-2016-167 (588400) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2016-167 138.0 KV 588400 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. | Lower acceleration to 0.2.
04 - Southeast | 25S | Transfer | GEN_2017_040__G17_092_SWYD | 3 Phase fault on GEN-2017-040 (588810) 345 kV Bus a. Apply fault at the GEN-2017-040 (588810) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-040 345.0 KV 588810 TO G17-092-SWYD 345.0 KV 588838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | GEN_2017_040__G17_092_SWYD | 3 Phase fault on GEN-2017-040 (588810) 345 kV Bus a. Apply fault at the GEN-2017-040 (588810) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-040 345.0 KV 588810 TO G17-092-SWYD 345.0 KV 588838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25S | Transfer | GEN_2017_140__G17_140_BUS | 3 Phase fault on GEN-2017-140 (760389) 345 kV Bus a. Apply fault at the GEN-2017-140 (760389) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-140 345.0 KV 760389 TO G17-140-345.0 KV 760393 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2017_140__G17_140_BUS | 3 Phase fault on GEN-2017-140 (760389) 345 kV Bus a. Apply fault at the GEN-2017-140 (760389) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-140 345.0 KV 760389 TO G17-140-345.0 KV 760393 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. | Lower acceleration to 0.2.
04 - Southeast | 25S | Transfer | GEN_2017_149__GEN_2017_154 | 3 Phase fault on GEN-2017-149 (760830) 345 kV Bus a. Apply fault at the GEN-2017-149 (760830) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-149 345.0 KV 760830 TO GEN-2017-154 345.0 KV 760851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2017_149__GEN_2017_154 | 3 Phase fault on GEN-2017-149 (760830) 345 kV Bus a. Apply fault at the GEN-2017-149 (760830) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-149 345.0 KV 760830 TO GEN-2017-154 345.0 KV 760851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2017_150__GEN_2017_233 | 3 Phase fault on GEN-2017-150 (761229) 345 kV Bus a. Apply fault at the GEN-2017-150 (761229) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-150 345.0 KV 761229 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | GEN_2017_150__GEN_2017_233 | 3 Phase fault on GEN-2017-150 (761229) 345 kV Bus a. Apply fault at the GEN-2017-150 (761229) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2017-150 345.0 KV 761229 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | GEN_2018_003__G18_003_TAP | 3 Phase fault on GEN-2018-003 (762427) 138 kV Bus a. Apply fault at the GEN-2018-003 (762427) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2018_003__G18_003_TAP | 3 Phase fault on GEN-2018-003 (762427) 138 kV Bus a. Apply fault at the GEN-2018-003 (762427) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-003 138.0 KV 762427 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GEN_2018_027__G18_027_TAP | 3 Phase fault on GEN-2018-027 (762625) 138 kV Bus a. Apply fault at the GEN-2018-027 (762625) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-027 138.0 KV 762625 TO G18-027-TAP 138.0 KV 762629 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | GEN_2018_027__G18_027_TAP | 3 Phase fault on GEN-2018-027 (762625) 138 kV Bus a. Apply fault at the GEN-2018-027 (762625) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-027 138.0 KV 762625 TO G18-027-TAP 138.0 KV 762629 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | GLASMTN4__MOORLND4 | 3 Phase fault on GLASMTN4 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASMTN4 138.0 KV 514788 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GLASMTN4__MOORLND4 | 3 Phase fault on GLASMTN4 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLASMTN4 138.0 KV 514788 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GORDON_TAP_4__CRAIGJT4 | 3 Phase fault on GORDON TAP 4 (507461) 138 kV Bus a. Apply fault at the GORDON TAP 4 (507461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORDON TAP 4 138.0 KV 507461 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GORDON_TAP_4__CRAIGJT4 | 3 Phase fault on GORDON TAP 4 (507461) 138 kV Bus a. Apply fault at the GORDON TAP 4 (507461) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORDON TAP 4 138.0 KV 507461 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GORE___5__MUSKTAP5 | 3 Phase fault on GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO MUSKTAP5 161.0 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GORE___5__MUSKTAP5 | 3 Phase fault on GORE 5 (505552) 161 kV Bus a. Apply fault at the GORE 5 (505552) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORE 5 161.0 KV 505552 TO MUSKTAP5 161.0 KV 505558 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.1
04 - Southeast | 25S | Transfer | GRACMNT7_345kV_515800 | Apply single-phase fault on: GRACMNT7 345KV 515800 TO G16091TAP 345KV 587744 CKT 1, near GRACMNT7 345kV for 6 cycles with stuck breaker at GRACMNT7 345kV. Clear Fault after 16 cycles and trip: GRACMNT7 345KV 515800 TO G16037TAP 345.0 KV 560078 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRACMNT7_345kV_515800 | Apply single-phase fault on: GRACMNT7 345KV 515800 TO G16091TAP 345KV 587744 CKT 1, near GRACMNT7 345kV for 6 cycles with stuck breaker at GRACMNT7 345kV. Clear Fault after 16 cycles and trip: GRACMNT7 345KV 515800 TO G16037TAP 345.0 KV 560078 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRDGVTP4__MEEKRSW4 | 3 Phase fault on GRDGVTP4 (520526) 138 kV Bus a. Apply fault at the GRDGVTP4 (520526) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDGVTP4 138.0 KV 520526 TO MEEKRSW4 138.0 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRDGVTP4__MEEKRSW4 | 3 Phase fault on GRDGVTP4 (520526) 138 kV Bus a. Apply fault at the GRDGVTP4 (520526) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDGVTP4 138.0 KV 520526 TO MEEKRSW4 138.0 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRNWOOD4_138kV_515417 | Apply single-phase fault on: CUSHING4 138KV 515033 TO GRNWOOD4 138KV 515417 CKT 1, near GRNWOOD4 138kV for 7 cycles with stuck breaker at GRNWOOD4 138kV. Clear Fault after 16 cycles and trip: GRTPLNS4 138KV 515043 TO GRNWOOD4 138KV 515417 CKT 1 and GRTPLNS4 138KV 515043 TO LNWOODT4 138KV 515453 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRNWOOD4_138kV_515417 | Apply single-phase fault on: CUSHING4 138KV 515033 TO GRNWOOD4 138KV 515417 CKT 1, near GRNWOOD4 138kV for 7 cycles with stuck breaker at GRNWOOD4 138kV. Clear Fault after 16 cycles and trip: GRTPLNS4 138KV 515043 TO GRNWOOD4 138KV 515417 CKT 1 and GRTPLNS4 138KV 515043 TO LNWOODT4 138KV 515453 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | GRTWSRN7__GUTHRIE7 | 3 Phase fault on GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 345.0 KV 515825 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | GRTWSRN7__GUTHRIE7 | 3 Phase fault on GRTWSRN7 (515825) 345 kV Bus a. Apply fault at the GRTWSRN7 (515825) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRTWSRN7 345.0 KV 515825 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HAMMTAP4__HAMMETT4 | 3 Phase fault on HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO HAMMETT4 138.0 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HAMMTAP4__HAMMETT4 | 3 Phase fault on HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO HAMMETT4 138.0 KV 520951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HAMMTAP4__LINCOLN4 | 3 Phase fault on HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HAMMTAP4__LINCOLN4 | 3 Phase fault on HAMMTAP4 (515046) 138 kV Bus a. Apply fault at the HAMMTAP4 (515046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAMMTAP4 138.0 KV 515046 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HARPER2__ANADARK2 | 3 Phase fault on HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HARPER2__ANADARK2 | 3 Phase fault on HARPER2 (520440) 69 kV Bus a. Apply fault at the HARPER2 (520440) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER2 69.0 KV 520440 TO ANADARK2 69.0 KV 520810 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HARTSIS4__S_SHV__4 | 3 Phase fault on HARTSIS4 (507735) 138 kV Bus a. Apply fault at the HARTSIS4 (507735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138.0 KV 507735 TO S SHV 4 138.0 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HARTSIS4__S_SHV__4 | 3 Phase fault on HARTSIS4 (507735) 138 kV Bus a. Apply fault at the HARTSIS4 (507735) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARTSIS4 138.0 KV 507735 TO S SHV 4 138.0 KV 507755 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HAYMAKR4__CIMARON4 | 3 Phase fault on HAYMAKR4 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 138.0 KV 514863 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HAYMAKR4__CIMARON4 | 3 Phase fault on HAYMAKR4 (514863) 138 kV Bus a. Apply fault at the HAYMAKR4 (514863) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAYMAKR4 138.0 KV 514863 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HEFNER_4__DVISION4 | 3 Phase fault on HEFNER 4 (514848) 138 kV Bus a. Apply fault at the HEFNER 4 (514848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 138.0 KV 514848 TO LAKESID4 138.0 KV 514849 CKT 1 b.2. LOAD 1 514849 b.3. LAKESID4 138.0 KV 514849 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HEFNER_4__DVISION4 | 3 Phase fault on HEFNER 4 (514848) 138 kV Bus a. Apply fault at the HEFNER 4 (514848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEFNER 4 138.0 KV 514848 TO LAKESID4 138.0 KV 514849 CKT 1 b.2. LOAD 1 514849 b.3. LAKESID4 138.0 KV 514849 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HEFNER_4__TENESTP4 | 3 Phase fault on HEFNER 4 (514848) 138 kV Bus a. Apply fault at the HEFNER 4 (514848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILSHIR4 138.0 KV 514836 TO HEFNER 4 138.0 KV 514848 CKT 1 b.2. WILSHIR4 138.0 KV 514836 TO TENNESE4 138.0 KV 514838 CKT 1 b.3. LOAD 1 514838 b.4. TENESTP4 138.0 KV 514837 TO TENNESE4 138.0 KV 514838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HEFNER_4__TENESTP4 | 3 Phase fault on HEFNER 4 (514848) 138 kV Bus a. Apply fault at the HEFNER 4 (514848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILSHIR4 138.0 KV 514836 TO HEFNER 4 138.0 KV 514848 CKT 1 b.2. WILSHIR4 138.0 KV 514836 TO TENNESE4 138.0 KV 514838 CKT 1 b.3. LOAD 1 514838 b.4. TENESTP4 138.0 KV 514837 TO TENNESE4 138.0 KV 514838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HEFNER4_138kV_514848 | Apply single-phase fault on: HEFNER4 138KV 514848 TO LAKESID4 138KV 514849 CKT 1, near HEFNER 4 138 kV for 7 cycles with stuck breaker at HEFNER 4 138 kV. Clear Fault after 16 cycles and trip: HEFNER4 138KV 514848 TO WILSHIR4 138KV 514836 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HEFNER4_138kV_514848 | Apply single-phase fault on: HEFNER4 138KV 514848 TO LAKESID4 138KV 514849 CKT 1, near HEFNER 4 138 kV for 7 cycles with stuck breaker at HEFNER 4 138 kV. Clear Fault after 16 cycles and trip: HEFNER4 138KV 514848 TO WILSHIR4 138KV 514836 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HENESEY4__BULFTTP4 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HENESEY4__BULFTTP4 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HENESEY4__DOVERSW4 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HENESEY4__DOVERSW4 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HENESEY4 138.0 KV 514774 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HENESEY4__WAUKOTP4 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 b.2. LOAD 1 514774 b.3. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HENESEY4__WAUKOTP4 | 3 Phase fault on HENESEY4 (514774) 138 kV Bus a. Apply fault at the HENESEY4 (514774) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOMI4 138.0 KV 514710 TO HENESEY4 138.0 KV 514774 CKT 1 b.2. LOAD 1 514774 b.3. WAUKOMI4 138.0 KV 514710 TO WAUKOTP4 138.0 KV 514711 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HITCHLAND__7__523095_0 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7( 523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 523097 TO HITCHLAND 6 523095 TO HITCHLD_TR21 523094 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HITCHLAND__7__523095_0 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7( 523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 523097 TO HITCHLAND 6 523095 TO HITCHLD_TR21 523094 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HITCHLAND__7__CARPENTER__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO CARPENTER 7 345.0 KV 523823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HITCHLAND__7__G10014G11022 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO G10014G11022 345.0 KV 576397 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HITCHLAND__7__NOBLE_WND__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOBLE_WND 7 345.0 KV 523101 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HITCHLAND__7__NOVUS1_____7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO NOVUS1 7 345.0 KV 523112 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HITCHLAND__7__POTTER_CO__7 | 3 Phase fault on HITCHLAND 7 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 345.0 KV 523097 TO POTTER_CO 7 345.0 KV 523961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HOBBYLO4__CHEMTRN4 | 3 Phase fault on HOBBYLO4 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBYLO4 138.0 KV 515338 TO CHEMTRN4 138.0 KV 515367 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HOBBYLO4__CHEMTRN4 | 3 Phase fault on HOBBYLO4 (515338) 138 kV Bus a. Apply fault at the HOBBYLO4 (515338) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBYLO4 138.0 KV 515338 TO CHEMTRN4 138.0 KV 515367 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HOLLYWD4__INDNHIL4 | 3 Phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLLYWD4 138.0 KV 514953 TO INDNHIL4 138.0 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | HOLLYWD4__INDNHIL4 | 3 Phase fault on HOLLYWD4 (514953) 138 kV Bus a. Apply fault at the HOLLYWD4 (514953) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLLYWD4 138.0 KV 514953 TO INDNHIL4 138.0 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HOOKS__2__LSORDTP2 | 3 Phase fault on HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69.0 KV 508057 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HOOKS__2__LSORDTP2 | 3 Phase fault on HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69.0 KV 508057 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HOOKS__2__REDRVR_2 | 3 Phase fault on HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69.0 KV 508057 TO REDRVR-2 69.0 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HOOKS__2__REDRVR_2 | 3 Phase fault on HOOKS 2 (508057) 69 kV Bus a. Apply fault at the HOOKS 2 (508057) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOKS 2 69.0 KV 508057 TO REDRVR-2 69.0 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HSL____4__GEN_2018_029 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2018-029 138.0 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265). | Lower acceleration to 0.2. Remove Reclose. Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | HSL____4__GEN_2018_029 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO GEN-2018-029 138.0 KV 762647 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | HSL____4__HAMMTAP4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265). | Lower acceleration to 0.2. Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | HSL____4__HAMMTAP4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | HSL____4__JONESSB4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265). | Lower acceleration to 0.2. Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | HSL____4__JONESSB4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | HSL____4__RENO___4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138.0 KV 514964 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265). | Lower acceleration to 0.2. Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | HSL____4__RENO___4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.2. LOAD 1 514966 b.3. NE10TH 4 138.0 KV 514964 TO MIDWAY 4 138.0 KV 514966 CKT 1 b.4. LOAD 1 514966 b.5. NE10TH 4 138.0 KV 514964 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | HSL____4__SE15TH_4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Lower acceleration to 0.2. Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | HSL____4__SE15TH_4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO SE15TH 4 138.0 KV 514993 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | HSL____4__SQUIRCK4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO DALE 4 138.0 KV 514987 CKT 1 b.2. LOAD 1 514987 b.3. DALE 4 138.0 KV 514987 TO SQUIRCK4 138.0 KV 515059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Lower acceleration to 0.2. Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | HSL____4__SQUIRCK4 | 3 Phase fault on HSL 4 (514941) 138 kV Bus a. Apply fault at the HSL 4 (514941) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSL 4 138.0 KV 514941 TO DALE 4 138.0 KV 514987 CKT 1 b.2. LOAD 1 514987 b.3. DALE 4 138.0 KV 514987 TO SQUIRCK4 138.0 KV 515059 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | HSL4_138kV_514941 | Apply single-phase fault on:HSL4 138KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 ,near HSL 4 138 kV for 7 cycles with stuck breaker at HSL 4 138 kV. Clear Fault after 16 cycles and trip: HSL4 138KV 514941 TO MIDWAY4 138.0 KV 514966 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HSL4_138kV_514941 | Apply single-phase fault on:HSL4 138KV 514941 TO HAMMTAP4 138.0 KV 515046 CKT 1 ,near HSL 4 138 kV for 7 cycles with stuck breaker at HSL 4 138 kV. Clear Fault after 16 cycles and trip: HSL4 138KV 514941 TO MIDWAY4 138.0 KV 514966 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HSLEAST2__DEEPFKT2 | 3 Phase fault on HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO GRNPAST2 69.0 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69.0 KV 514970 TO GRNPAST2 69.0 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HSLEAST2__DEEPFKT2 | 3 Phase fault on HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO GRNPAST2 69.0 KV 514971 CKT 1 b.2. LOAD 1 514971 b.3. DEEPFKT2 69.0 KV 514970 TO GRNPAST2 69.0 KV 514971 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HSLEAST2__HSLWEST2 | 3 Phase fault on HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO HSLWEST2 69.0 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HSLEAST2__HSLWEST2 | 3 Phase fault on HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO HSLWEST2 69.0 KV 514937 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HSLEAST2__MCLOUDT2 | 3 Phase fault on HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HSLEAST2__MCLOUDT2 | 3 Phase fault on HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HSLEAST2__TXSTELA2 | 3 Phase fault on HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO TXSTELA2 69.0 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HSLEAST2__TXSTELA2 | 3 Phase fault on HSLEAST2 (514927) 69 kV Bus a. Apply fault at the HSLEAST2 (514927) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLEAST2 69.0 KV 514927 TO TXSTELA2 69.0 KV 514985 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HSLEAST2_138kV_514927 | Apply single-phase fault on:HSLEAST2 138KV 514927 TO HSLWEST2 138KV 514937 CKT 1 ,near HSLEAST2 69 kV for 7 cycles with stuck breaker at HSLEAST2 69 kV. Clear Fault after 16 cycles and trip: HSLEAST2 138KV 514927 TO TXSTELA2 138KV 514985 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HSLEAST2_138kV_514927 | Apply single-phase fault on:HSLEAST2 138KV 514927 TO HSLWEST2 138KV 514937 CKT 1 ,near HSLEAST2 69 kV for 7 cycles with stuck breaker at HSLEAST2 69 kV. Clear Fault after 16 cycles and trip: HSLEAST2 138KV 514927 TO TXSTELA2 138KV 514985 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HSLWEST2__514941_0 | 3 Phase fault on HSLWEST2 (514937) 69 kV Bus a. Apply fault at the HSLWEST2( 514937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HSLWEST2__514941_0 | 3 Phase fault on HSLWEST2 (514937) 69 kV Bus a. Apply fault at the HSLWEST2( 514937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HSLWEST2 514937 TO HSL 4 514941 TO HSL 1 515731 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HUGO___7__520560_0 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HUGO___7__520560_0 | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7( 521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 521157 TO HUGOITC4 520560 TO HUGO TERTA 521189 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | HUGO___7__G16_063_TAP | 3 Phase fault on HUGO 7 (521157) 345 kV Bus a. Apply fault at the HUGO 7 (521157) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUGO 7 345.0 KV 521157 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HUNTERS7_345kV_515476 | Apply single-phase fault on: WOODRNG7 345KV 514715 TO HUNTERS7 345KV 515476 CKT 1, near HUNTERS7 345kV for 6 cycles with stuck breaker at HUNTERS7 345kV. Clear Fault after 16 cycles and trip: HUNTERS7 345KV 515476 TO RENFROW7 345KV 515543 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HUNTERS7_345kV_515476 | Apply single-phase fault on: WOODRNG7 345KV 514715 TO HUNTERS7 345KV 515476 CKT 1, near HUNTERS7 345kV for 6 cycles with stuck breaker at HUNTERS7 345kV. Clear Fault after 16 cycles and trip: HUNTERS7 345KV 515476 TO RENFROW7 345KV 515543 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | HWY20_T4__WLDCT_HIL4 | 3 Phase fault on HWY20-T4 (509821) 138 kV Bus a. Apply fault at the HWY20-T4 (509821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138.0 KV 509821 TO WLDCT_HIL4 138.0 KV 509897 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | HWY20_T4__WLDCT_HIL4 | 3 Phase fault on HWY20-T4 (509821) 138 kV Bus a. Apply fault at the HWY20-T4 (509821) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HWY20-T4 138.0 KV 509821 TO WLDCT_HIL4 138.0 KV 509897 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IODINE_4__MOORLND4 | 3 Phase fault on IODINE 4 (520957) 138 kV Bus a. Apply fault at the IODINE 4 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IODINE_4__MOORLND4 | 3 Phase fault on IODINE 4 (520957) 138 kV Bus a. Apply fault at the IODINE 4 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE 4 138.0 KV 520957 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IODINE_4__WWRDEHV4 | 3 Phase fault on IODINE-4 (514796) 138 kV Bus a. Apply fault at the IODINE-4 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | IODINE_4__WWRDEHV4 | 3 Phase fault on IODINE-4 (514796) 138 kV Bus a. Apply fault at the IODINE-4 (514796) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IODINE-4 138.0 KV 514796 TO WWRDEHV4 138.0 KV 515376 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | IPC_T__4__CASSTP4 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | IPC_T__4__CASSTP4 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | IPC_T__4__IPC____4 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC 4 138.0 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | IPC_T__4__IPC____4 | 3 Phase fault on IPC T 4 (508059) 138 kV Bus a. Apply fault at the IPC T 4 (508059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC T 4 138.0 KV 508059 TO IPC 4 138.0 KV 508095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | JEFFRSN4__LAKEPIN4 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JEFFRSN4__LAKEPIN4 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO LAKEPIN4 138.0 KV 509624 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JEFFRSN4__WILKES_4 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JEFFRSN4__WILKES_4 | 3 Phase fault on JEFFRSN4 (508835) 138 kV Bus a. Apply fault at the JEFFRSN4 (508835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JEFFRSN4 138.0 KV 508835 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JENKS__4__SAPLPRD4 | 3 Phase fault on JENKS--4 (509759) 138 kV Bus a. Apply fault at the JENKS--4 (509759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138.0 KV 509759 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JENKS__4__SAPLPRD4 | 3 Phase fault on JENKS--4 (509759) 138 kV Bus a. Apply fault at the JENKS--4 (509759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENKS--4 138.0 KV 509759 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JENSEN4_138kV_514821 | Apply single-phase fault on: JENSENT4 138KV 514820 TO JENSEN4 138KV 514821 CKT 1, near JENSEN4 138kV for 7 cycles with stuck breaker at JENSEN4 138kV. Clear Fault after 16 cycles and trip: CANGAS4 138KV 511540 TO JENSEN4 138KV 514821 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JENSEN4_138kV_514821 | Apply single-phase fault on: JENSENT4 138KV 514820 TO JENSEN4 138KV 514821 CKT 1, near JENSEN4 138kV for 7 cycles with stuck breaker at JENSEN4 138kV. Clear Fault after 16 cycles and trip: CANGAS4 138KV 511540 TO JENSEN4 138KV 514821 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JENSENT4__CIMARON4 | 3 Phase fault on JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JENSENT4__CIMARON4 | 3 Phase fault on JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JENSENT4__JENSEN_4 | 3 Phase fault on JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JENSENT4__JENSEN_4 | 3 Phase fault on JENSENT4 (514820) 138 kV Bus a. Apply fault at the JENSENT4 (514820) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JENSENT4 138.0 KV 514820 TO JENSEN 4 138.0 KV 514821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JNSKAMO4__ARCADIA4 | 3 Phase fault on JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JNSKAMO4__ARCADIA4 | 3 Phase fault on JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JNSKAMO4__HSL____4 | 3 Phase fault on JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JNSKAMO4__HSL____4 | 3 Phase fault on JNSKAMO4 (514906) 138 kV Bus a. Apply fault at the JNSKAMO4 (514906) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JNSKAMO4 138.0 KV 514906 TO HSL 4 138.0 KV 514941 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JNSKAMO4_138kV_514906 | Apply single-phase fault on: JNSKAMO4 138KV 514906 TO 4MEMORALT 138KV 300136 CKT 1, near JNSKAMO4 138 kV for 7 cycles with stuck breaker at JNSKAMO4 138 kV. Clear Fault after 16 cycles and trip: JNSKAMO4 138KV 514906 TO ARCADIA4 138KV 514907 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JNSKAMO4_138kV_514906 | Apply single-phase fault on: JNSKAMO4 138KV 514906 TO 4MEMORALT 138KV 300136 CKT 1, near JNSKAMO4 138 kV for 7 cycles with stuck breaker at JNSKAMO4 138 kV. Clear Fault after 16 cycles and trip: JNSKAMO4 138KV 514906 TO ARCADIA4 138KV 514907 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO_4__514809_0 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4( 514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 514808 TO JOHNCO 7 514809 TO JOHNCO11 514810 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_4__CANEYCK4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO_4__CANEYCK4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_4__RUSSET_4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO_4__RUSSET_4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO RUSSET-4 138.0 KV 515120 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_4__SXMLCKT4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | JOHNCO_4__SXMLCKT4 | 3 Phase fault on JOHNCO 4 (514808) 138 kV Bus a. Apply fault at the JOHNCO 4 (514808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNCO 4 138.0 KV 514808 TO SXMLCKT4 138.0 KV 515122 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | JOHNCO_7__DMNDSPG7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25S | Transfer | JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | JOHNCO_7__GEN_2017_149 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO GEN-2017-149 345.0 KV 760830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25S | Transfer | JOHNCO4_138kV_514808 | Apply single-phase fault on: JOHNCO4 138KV 514808 TO RUSSET4 138.0 KV 515120 CKT 1, near JOHNCO4 138kV for 7 cycles with stuck breaker at JOHNCO4 138kV. Clear Fault after 16 cycles and trip: JOHNCO4 138KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO4_138kV_514808 | Apply single-phase fault on: JOHNCO4 138KV 514808 TO RUSSET4 138.0 KV 515120 CKT 1, near JOHNCO4 138kV for 7 cycles with stuck breaker at JOHNCO4 138kV. Clear Fault after 16 cycles and trip: JOHNCO4 138KV 514808 TO CANEYCK4 138.0 KV 515150 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | JOHNCO7_345kV_514809 | Apply single-phase fault on: JOHNCO7 345KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1, near JOHNCO7 345kV for 6 cycles with stuck breaker at JOHNCO7 345kV. Clear Fault after 16 cycles and trip: PITTSB7 345KV 510907 TO JOHNCO7 345KV 514809 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JOHNCO7_345kV_514809 | Apply single-phase fault on: JOHNCO7 345KV 514809 TO DMNDSPG7 345.0 KV 516006 CKT 1, near JOHNCO7 345kV for 6 cycles with stuck breaker at JOHNCO7 345kV. Clear Fault after 16 cycles and trip: PITTSB7 345KV 510907 TO JOHNCO7 345KV 514809 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JONESSB4__ARCADIA4 | 3 Phase fault on JONESSB4 (515480) 138 kV Bus a. Apply fault at the JONESSB4 (515480) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JONESSB4__ARCADIA4 | 3 Phase fault on JONESSB4 (515480) 138 kV Bus a. Apply fault at the JONESSB4 (515480) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. CHTWOOD4 138.0 KV 514842 TO LGARBER4 138.0 KV 515465 CKT 1 b.3. LOAD 1 515465 b.4. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | JONESSB4__MEMRIAL4 | 3 Phase fault on JONESSB4 (515480) 138 kV Bus a. Apply fault at the JONESSB4 (515480) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 b.3. LOAD 1 515459 b.4. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | JONESSB4__MEMRIAL4 | 3 Phase fault on JONESSB4 (515480) 138 kV Bus a. Apply fault at the JONESSB4 (515480) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 b.2. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 b.3. LOAD 1 515459 b.4. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KELLYVL4__BLUEBEL4 | 3 Phase fault on KELLYVL4 (515200) 138 kV Bus a. Apply fault at the KELLYVL4 (515200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYVL4 138.0 KV 515200 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KELLYVL4__BLUEBEL4 | 3 Phase fault on KELLYVL4 (515200) 138 kV Bus a. Apply fault at the KELLYVL4 (515200) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYVL4 138.0 KV 515200 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KENTUKT2__SAGE___2 | 3 Phase fault on KENTUKT2 (514977) 69 kV Bus a. Apply fault at the KENTUKT2 (514977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENTUKT2 69.0 KV 514977 TO SAGE 2 69.0 KV 514978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KENTUKT2__SAGE___2 | 3 Phase fault on KENTUKT2 (514977) 69 kV Bus a. Apply fault at the KENTUKT2 (514977) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENTUKT2 69.0 KV 514977 TO SAGE 2 69.0 KV 514978 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KETCHTP4__KETCH__4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KETCHTP4__KETCH__4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KETCHTP4__MITCHSB4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO MITCHSB4 138.0 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KETCHTP4__MITCHSB4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO MITCHSB4 138.0 KV 515466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KETCHTP4__NORTWST4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KETCHTP4__NORTWST4 | 3 Phase fault on KETCHTP4 (514828) 138 kV Bus a. Apply fault at the KETCHTP4 (514828) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KETCHTP4 138.0 KV 514828 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KEYSTON4__WEKIWA_4 | 3 Phase fault on KEYSTON4 (505610) 138 kV Bus a. Apply fault at the KEYSTON4 (505610) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138.0 KV 505610 TO WEKIWA-4 138.0 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KEYSTON4__WEKIWA_4 | 3 Phase fault on KEYSTON4 (505610) 138 kV Bus a. Apply fault at the KEYSTON4 (505610) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEYSTON4 138.0 KV 505610 TO WEKIWA-4 138.0 KV 509757 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KGFSHSW4__CONCHO_4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KGFSHSW4__CONCHO_4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KGFSHSW4__EKFSHTP4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KGFSHSW4__EKFSHTP4 | 3 Phase fault on KGFSHSW4 (520533) 138 kV Bus a. Apply fault at the KGFSHSW4 (520533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSHSW4 138.0 KV 520533 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KGFSJCT4__EKFSHTP4 | 3 Phase fault on KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KGFSJCT4__EKFSHTP4 | 3 Phase fault on KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KGFSJCT4__NKNGFSH4 | 3 Phase fault on KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO NKNGFSH4 138.0 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KGFSJCT4__NKNGFSH4 | 3 Phase fault on KGFSJCT4 (520405) 138 kV Bus a. Apply fault at the KGFSJCT4 (520405) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KGFSJCT4 138.0 KV 520405 TO NKNGFSH4 138.0 KV 520603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KNGFSHR7__515855_0 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7( 515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 515600 TO KNGFSR11 515855 TO KNGFRT11 515857 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KNGFSHR7__515855_0 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7( 515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 515600 TO KNGFSR11 515855 TO KNGFRT11 515857 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KNGFSHR7__515856_0 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7( 515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 515600 TO KNGFSR21 515856 TO KNGFRT21 515858 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KNGFSHR7__515856_0 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7( 515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 515600 TO KNGFSR21 515856 TO KNGFRT21 515858 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KNGFSHR7__FSHRTAP7 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7 (515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 345.0 KV 515600 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KNGFSHR7__FSHRTAP7 | 3 Phase fault on KNGFSHR7 (515600) 345 kV Bus a. Apply fault at the KNGFSHR7 (515600) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KNGFSHR7 345.0 KV 515600 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KNOBHIL4__DGRASSE4 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KNOBHIL4__DGRASSE4 | 3 Phase fault on KNOBHIL4 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 138.0 KV 514795 TO DGRASSE4 138.0 KV 515853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | KNOXLEE4__BRANDYBR | 3 Phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | KNOXLEE4__BRANDYBR | 3 Phase fault on KNOXLEE4 (508548) 138 kV Bus a. Apply fault at the KNOXLEE4 (508548) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOXLEE4 138.0 KV 508548 TO BRANDYBR 138.0 KV 508596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | L_E_S__2__LGORE_N2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | L_E_S__2__LGORE_N2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | L_E_S__2__LGORE_S2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | L_E_S__2__LGORE_S2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | L_E_S__4__SHERID4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | L_E_S__4__SHERID4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2016-095 (587773). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-095 (587773)
04 - Southeast | 25S | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2016-095 (587773). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | LEASIDE_2__507793_0 | 3 Phase fault on LEASIDE 2 (507794) 69 kV Bus a. Apply fault at the LEASIDE 2( 507794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LEASIDE_2__507793_0 | 3 Phase fault on LEASIDE 2 (507794) 69 kV Bus a. Apply fault at the LEASIDE 2( 507794) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 2 507794 TO LEASIDE 4 507793 TO LEASIDE 1-1 507795 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LEASIDE_4__STONWAL4 | 3 Phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138.0 KV 507793 TO STONWAL4 138.0 KV 509052 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LEASIDE_4__STONWAL4 | 3 Phase fault on LEASIDE 4 (507793) 138 kV Bus a. Apply fault at the LEASIDE 4 (507793) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEASIDE 4 138.0 KV 507793 TO STONWAL4 138.0 KV 509052 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LEBROCK7__TENRUSK7 | 3 Phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LEBROCK7__TENRUSK7 | 3 Phase fault on LEBROCK7 (508572) 345 kV Bus a. Apply fault at the LEBROCK7 (508572) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEBROCK7 345.0 KV 508572 TO TENRUSK7 345.0 KV 508585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_138kV_511467 | Apply single-phase fault on: LWSTAP4 138KV 511439 TO LES4 138KV 511467 CKT 1, near LES 138kV for 7 cycles with stuck breaker at LES 138kV. Clear Fault after 16 cycles and trip: LES4 138KV 511467 TO SHERID4 138KV 511474 CKT 1 and SHERID4 138KV 511474 TO ARTVLTP4 138KV 511537 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_138kV_511467 | Apply single-phase fault on: LWSTAP4 138KV 511439 TO LES4 138KV 511467 CKT 1, near LES 138kV for 7 cycles with stuck breaker at LES 138kV. Clear Fault after 16 cycles and trip: LES4 138KV 511467 TO SHERID4 138KV 511474 CKT 1 and SHERID4 138KV 511474 TO ARTVLTP4 138KV 511537 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LES_345kV_511468 | Apply single-phase fault on: LES7 345KV 511468 TO G17171TAP 345.0 KV 760938 CKT 1, near LES 345kV for 6 cycles with stuck breaker at LES 345kV. Clear Fault after 16 cycles and trip: OKU7 345KV 511456 TO LES7 345KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LES_345kV_511468 | Apply single-phase fault on: LES7 345KV 511468 TO G17171TAP 345.0 KV 760938 CKT 1, near LES 345kV for 6 cycles with stuck breaker at LES 345kV. Clear Fault after 16 cycles and trip: OKU7 345KV 511456 TO LES7 345KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LIEBERM2__508806_0 | 3 Phase fault on LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2( 508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LIEBERM2__508806_0 | 3 Phase fault on LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2( 508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 508805 TO LIEBERM4 508806 TO LBMN3-1 508822 CKT 3 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LIEBERM2__OILCITY2 | 3 Phase fault on LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69.0 KV 508805 TO OILCITY2 69.0 KV 508812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LIEBERM2__OILCITY2 | 3 Phase fault on LIEBERM2 (508805) 69 kV Bus a. Apply fault at the LIEBERM2 (508805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM2 69.0 KV 508805 TO OILCITY2 69.0 KV 508812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LIEBERM4__G16_167_TAP | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LIEBERM4__G16_167_TAP | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LIEBERM4__JEFFRSN4 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO IPCJEFF4 138.0 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LIEBERM4__JEFFRSN4 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO IPCJEFF4 138.0 KV 508833 CKT 1 b.2. LOAD 1 508833 b.3. IPCJEFF4 138.0 KV 508833 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LIEBERM4__LONGWD_4 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LIEBERM4__LONGWD_4 | 3 Phase fault on LIEBERM4 (508806) 138 kV Bus a. Apply fault at the LIEBERM4 (508806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIEBERM4 138.0 KV 508806 TO LONGWD 4 138.0 KV 508808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LINCOLN4__MEEKRSW4 | 3 Phase fault on LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138.0 KV 515442 TO MEEKER 4 138.0 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138.0 KV 520464 TO MEEKRSW4 138.0 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LINCOLN4__MEEKRSW4 | 3 Phase fault on LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINCOLN4 138.0 KV 515442 TO MEEKER 4 138.0 KV 520464 CKT 1 b.2. LOAD 1 520464 b.3. MEEKER 4 138.0 KV 520464 TO MEEKRSW4 138.0 KV 520994 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LINCOLN4__WOLVRNT4 | 3 Phase fault on LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138.0 KV 515051 TO LINCOLN4 138.0 KV 515442 CKT 1 b.2. JACKTWN4 138.0 KV 515051 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LINCOLN4__WOLVRNT4 | 3 Phase fault on LINCOLN4 (515442) 138 kV Bus a. Apply fault at the LINCOLN4 (515442) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JACKTWN4 138.0 KV 515051 TO LINCOLN4 138.0 KV 515442 CKT 1 b.2. JACKTWN4 138.0 KV 515051 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LINTNRD4__NBENTON4 | 3 Phase fault on LINTNRD4 (508807) 138 kV Bus a. Apply fault at the LINTNRD4 (508807) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138.0 KV 508807 TO NBENTON4 138.0 KV 508811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LINTNRD4__NBENTON4 | 3 Phase fault on LINTNRD4 (508807) 138 kV Bus a. Apply fault at the LINTNRD4 (508807) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINTNRD4 138.0 KV 508807 TO NBENTON4 138.0 KV 508811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LINWOOD4__POWELL_4 | 3 Phase fault on LINWOOD4 (507738) 138 kV Bus a. Apply fault at the LINWOOD4 (507738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO POWELL 4 138.0 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LINWOOD4__POWELL_4 | 3 Phase fault on LINWOOD4 (507738) 138 kV Bus a. Apply fault at the LINWOOD4 (507738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LINWOOD4 138.0 KV 507738 TO POWELL 4 138.0 KV 507748 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LITTLAX2__LITLAXT2 | 3 Phase fault on LITTLAX2 (514951) 69 kV Bus a. Apply fault at the LITTLAX2 (514951) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTLAX2 69.0 KV 514951 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LITTLAX2__LITLAXT2 | 3 Phase fault on LITTLAX2 (514951) 69 kV Bus a. Apply fault at the LITTLAX2 (514951) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LITTLAX2 69.0 KV 514951 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONEGRV4__CHEEKTP4 | 3 Phase fault on LONEGRV4 (515144) 138 kV Bus a. Apply fault at the LONEGRV4 (515144) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25W | Transfer | LONEGRV4__CHEEKTP4 | 3 Phase fault on LONEGRV4 (515144) 138 kV Bus a. Apply fault at the LONEGRV4 (515144) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONEGRV4 138.0 KV 515144 TO CHEEKTP4 138.0 KV 515415 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25S | Transfer | LONGVHT4__WHITNEY4 | 3 Phase fault on LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGVHT4__WHITNEY4 | 3 Phase fault on LONGVHT4 (508554) 138 kV Bus a. Apply fault at the LONGVHT4 (508554) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGVHT4 138.0 KV 508554 TO WHITNEY4 138.0 KV 508575 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_4__508809_0 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4( 508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_4__508809_0 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4( 508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 508808 TO LONGWD 7 508809 TO LONGW1-1 508819 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_4__FLOURNY4 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138.0 KV 507727 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_4__FLOURNY4 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LONGWD 4 138.0 KV 508808 TO OAKPH 4 138.0 KV 508816 CKT 1 b.2. LOAD 1 508816 b.3. FLOURNY4 138.0 KV 507727 TO OAKPH 4 138.0 KV 508816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_4__RAINES_4 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 b.2. RAINES 4 138.0 KV 507749 TO NORAM 4 138.0 KV 507774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_4__RAINES_4 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORAM 4 138.0 KV 507774 TO LONGWD 4 138.0 KV 508808 CKT 1 b.2. RAINES 4 138.0 KV 507749 TO NORAM 4 138.0 KV 507774 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_4__SABMINT4 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO LONGWD 4 138.0 KV 508808 CKT 1 b.2. SCOTTSV4 138.0 KV 508567 TO SEMRSHL4 138.0 KV 508569 CKT 1 b.3. LOAD 1 508569 b.4. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_4__SABMINT4 | 3 Phase fault on LONGWD 4 (508808) 138 kV Bus a. Apply fault at the LONGWD 4 (508808) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTTSV4 138.0 KV 508567 TO LONGWD 4 138.0 KV 508808 CKT 1 b.2. SCOTTSV4 138.0 KV 508567 TO SEMRSHL4 138.0 KV 508569 CKT 1 b.3. LOAD 1 508569 b.4. SABMINT4 138.0 KV 508566 TO SEMRSHL4 138.0 KV 508569 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_7__GEN_2018_050 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_7__GEN_2018_050 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO GEN-2018-050 345.0 KV 762845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD_7__WILKES_7 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD_7__WILKES_7 | 3 Phase fault on LONGWD 7 (508809) 345 kV Bus a. Apply fault at the LONGWD 7 (508809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LONGWD 7 345.0 KV 508809 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD4_138kV_508808 | Apply single-phase fault on: LONGWD4 138KV 508808 TO NORAM4 138KV 507774 CKT 1, near LONGWD 4 138 kV for 7 cycles with stuck breaker at LONGWD 4 138 kV. Clear Fault after 16 cycles and trip: LONGWD4 138KV 508808 TO LIEBERM4 138KV 508806 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD4_138kV_508808 | Apply single-phase fault on: LONGWD4 138KV 508808 TO NORAM4 138KV 507774 CKT 1, near LONGWD 4 138 kV for 7 cycles with stuck breaker at LONGWD 4 138 kV. Clear Fault after 16 cycles and trip: LONGWD4 138KV 508808 TO LIEBERM4 138KV 508806 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LONGWD7_345kV_508809 | Apply single-phase fault on: LONGWD7 345KV 508809 TO SWSHV7 345.0 KV 507760 CKT 1, near LONGWD 7 345 kV for 6 cycles with stuck breaker at LONGWD 7 345 kV. Clear Fault after 16 cycles and trip: LONGWD7 345KV 508809 TO WILKES7 345KV 508841 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LONGWD7_345kV_508809 | Apply single-phase fault on: LONGWD7 345KV 508809 TO SWSHV7 345.0 KV 507760 CKT 1, near LONGWD 7 345 kV for 6 cycles with stuck breaker at LONGWD 7 345 kV. Clear Fault after 16 cycles and trip: LONGWD7 345KV 508809 TO WILKES7 345KV 508841 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSORDTP2__LSORD__2 | 3 Phase fault on LSORDTP2 (508063) 69 kV Bus a. Apply fault at the LSORDTP2 (508063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSORDTP2 69.0 KV 508063 TO LSORD 2 69.0 KV 508093 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSORDTP2__LSORD__2 | 3 Phase fault on LSORDTP2 (508063) 69 kV Bus a. Apply fault at the LSORDTP2 (508063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSORDTP2 69.0 KV 508063 TO LSORD 2 69.0 KV 508093 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSSOUTH2__508297_0 | 3 Phase fault on LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2( 508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSSOUTH2__508297_0 | 3 Phase fault on LSSOUTH2 (508296) 69 kV Bus a. Apply fault at the LSSOUTH2( 508296) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH2 508296 TO LSSOUTH4 508297 TO LSS-1 508325 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSSOUTH4__DIANA__4 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSSOUTH4__DIANA__4 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSSOUTH4__PITTSB_4 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSSOUTH4__PITTSB_4 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO PITTSB_4 138.0 KV 508313 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LSSOUTH4__WILKES_4 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LSSOUTH4__WILKES_4 | 3 Phase fault on LSSOUTH4 (508297) 138 kV Bus a. Apply fault at the LSSOUTH4 (508297) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LSSOUTH4 138.0 KV 508297 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_10_P4_SWShreveport | Apply single-phase fault on SW SHV7 345.0 KV 507760 TO DIANA7 345.0 KV 508832 CKT 1, near SW SHV 7 for 5 cycles with stuck breaker at SW SHV 7 (507760) 345 kV Bus. Clear Fault after 10 cycles and trip SW SHV7 345.0 KV 507760 TO LONGWD7 345.0 KV 508809 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_3_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO NWTXARK7 345.0 KV 508072 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO WILKES7 345.0 KV 508841 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_4_P4_Welsh | Apply single-phase fault on WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 1, near WELSH 7 for 5 cycles with stuck breaker at WELSH 7 (508359) 345 kV Bus. Clear Fault after 10 cycles and trip WELSH 345.0 KV 508359 TO DIANA7 345.0 KV 508832 CKT 2 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_5_P4_Wilkes | Apply single-phase fault on LINE 508841 TO 508809 CKT 1, near WILKES 7 for 5 cycles with stuck breaker at WILKES 7 (508841) 345 kV Bus. Clear Fault after 10 cycles and trip LINE 508841 TO 508359 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_6_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO PIRKEY7 345.0 KV 508563 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_7_P4_Diana | Apply single-phase fault on DIANA7 345.0 KV 508832 TO WELSH7 345.0 KV 508359 CKT 1, near DIANA 7 for 5 cycles with stuck breaker at DIANA 7 (508832) 345 kV Bus. Clear Fault after 10 cycles and trip DIANA7 345.0 KV 508832 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_8_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO WILKES7 345.0 KV 508841 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_82_P4_Oneta | Apply single-phase fault on ONETA7 345.0 KV 509807 TO RSS7 345.0 KV 509782 CKT 1, near ONETA--7 for 5 cycles with stuck breaker at ONETA--7 (509807) 345 kV Bus. Clear Fault after 10 cycles and trip ONETA7 345.0 KV 509807 TO CLARKSV7 345.0 KV 509745 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_83_P4_Riverside | Apply single-phase fault on RSS7 345.0 KV 509782 TO REDBUD7 345.0 KV 514909 CKT 1, near R.S.S.-7 for 5 cycles with stuck breaker at R.S.S.-7 (509782) 345 kV Bus. Clear Fault after 10 cycles and trip RSS7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_84_P4_SantaFe | Apply single-phase fault on SANTAFE4 345.0 KV 511492 TO CORNVIL4 345.0 KV 511449 CKT 1, near SANTAFE4 for 5 cycles with stuck breaker at SANTAFE4 (511492) 138 kV Bus. Clear Fault after 10 cycles and trip SANTAFE4 345.0 KV 511492 TO RUSHSPT4 345.0 KV 511491 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__AEPW_2022_9_P4_Longwood | Apply single-phase fault on LONGWD7 345.0 KV 508809 TO 7SAREPTA% 345.0 KV 337376 CKT 1, near LONGWD 7 for 5 cycles with stuck breaker at LONGWD 7 (508809) 345 kV Bus. Clear Fault after 10 cycles and trip LONGWD7 345.0 KV 508809 TO SW SHV7 345.0 KV 507760 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_46_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_47_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_48_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_49_P4_GRDA17 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 7 for 15 cycles with stuck breaker at GRDA1 7 (512650) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_50_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_51_P4_GRECTAP7 | Apply single-phase fault on and DISCONNECT 527964, near GREC TAP5 for 15 cycles with stuck breaker at GREC TAP5 (512865) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_52_P4_IGLOOV7 | Apply single-phase fault on and DISCONNECT 527964, near IGLOOV 7 for 15 cycles with stuck breaker at IGLOOV 7 (513596) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_53_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_54_P4_GRDA15 | Apply single-phase fault on and DISCONNECT 527964, near GRDA1 5 for 15 cycles with stuck breaker at GRDA1 5 (512656) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_55_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_56_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_57_P4_CLEVLND7 | Apply single-phase fault on and DISCONNECT 527964, near CLEVLND7 for 15 cycles with stuck breaker at CLEVLND7 (512694) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_58_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_59_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_60_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_61_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_62_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_63_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_64_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_65_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_66_P4_MAID5 | Apply single-phase fault on and DISCONNECT 527964, near MAID 5 for 15 cycles with stuck breaker at MAID 5 (512648) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_67_P4_KERRGR3 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR3 for 15 cycles with stuck breaker at KERR GR3 (512634) 115 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_68_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_69_P4_KERRGR5 | Apply single-phase fault on and DISCONNECT 527964, near KERR GR5 for 15 cycles with stuck breaker at KERR GR5 (512635) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_70_P4_KETCHUM5 | Apply single-phase fault on and DISCONNECT 527964, near KETCHUM5 for 15 cycles with stuck breaker at KETCHUM5 (512669) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_71_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_72_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_73_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_74_P4_PENSA5 | Apply single-phase fault on and DISCONNECT 527964, near PENSA 5 for 15 cycles with stuck breaker at PENSA 5 (512654) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_75_P4_SALNCRK5 | Apply single-phase fault on and DISCONNECT 527964, near SALNCRK5 for 15 cycles with stuck breaker at SALNCRK5 (512805) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_76_P4_TONECE5 | Apply single-phase fault on and DISCONNECT 527964, near TONECE5 for 15 cycles with stuck breaker at TONECE5 (512751) 161 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_77_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__GRDA_All_78_P4_TONECE7 | Apply single-phase fault on and DISCONNECT 527964, near TONECE7 for 15 cycles with stuck breaker at TONECE7 (512750) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_16_P4_2_BVRCNTY7 | Apply single-phase fault on and DISCONNECT 527964, near BVRCNTY7 for 16 cycles with stuck breaker at BVRCNTY7 (515554) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_17_P4_2_WINDFRM4 | Apply single-phase fault on and DISCONNECT 527964, near WINDFRM4 for 16 cycles with stuck breaker at WINDFRM4 (515785) 138 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | LT__OKGE_All_18_P4_2_SUNNYSD7 | Apply single-phase fault on and DISCONNECT 527964, near SUNNYSD7 for 16 cycles with stuck breaker at SUNNYSD7 (515136) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | LT__OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_19_P4_2_DRAPER4 | Apply single-phase fault on and DISCONNECT 527964, near DRAPER 4 for 16 cycles with stuck breaker at DRAPER 4 (514933) 138 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_20_P4_2_WAUKOTP4 | Apply single-phase fault on LINE 514711 TO 514731 CKT 1 and LINE 514710 TO 514711 CKT 1, near WAUKOTP4 for 6 cycles with stuck breaker at WAUKOTP4 (514711) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514711 TO 514714 CKT 1 and LINE 514709 TO 514712 CKT 1 and LINE 514709 TO 514714 CKT 1 and LINE 514709 TO 514731 CKT 1 and DISCONNECT 514711 and DISCONNECT 514709 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_21_P4_2_JOHNCO7 | Apply single-phase fault on and DISCONNECT 527964, near JOHNCO 7 for 16 cycles with stuck breaker at JOHNCO 7 (514809) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | LT__OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_22_P4_2_GRACMNT7 | Apply single-phase fault on and DISCONNECT 527964, near GRACMNT7 for 16 cycles with stuck breaker at GRACMNT7 (515800) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_23_P4_2_OPENSKY7 | Apply single-phase fault on and DISCONNECT 527964, near OPENSKY7 for 16 cycles with stuck breaker at OPENSKY7 (515621) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_24_P4_2_PECANCK7 | Apply single-phase fault on and DISCONNECT 527964, near PECANCK7 for 16 cycles with stuck breaker at PECANCK7 (515235) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_25_P4_2_RANCHRD7 | Apply single-phase fault on and DISCONNECT 527964, near RANCHRD7 for 16 cycles with stuck breaker at RANCHRD7 (515576) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_26_P4_2_REDBUD7 | Apply single-phase fault on and DISCONNECT 527964, near REDBUD 7 for 16 cycles with stuck breaker at REDBUD 7 (514909) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_27_P4_2_FTSMITH8 | Apply single-phase fault on and DISCONNECT 527964, near FTSMITH8 for 16 cycles with stuck breaker at FTSMITH8 (515305) 500 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | LT__OKGE_All_28_P4_3_SEMINOL7 | Apply single-phase fault on and DISCONNECT 527964, near SEMINOL7 for 16 cycles with stuck breaker at SEMINOL7 (515045) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | LT__OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_29_P4_3_SOONER7 | Apply single-phase fault on and DISCONNECT 527964, near SOONER 7 for 16 cycles with stuck breaker at SOONER 7 (514803) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_30_P4_2_NORTWST7 | Apply single-phase fault on and DISCONNECT 527964, near NORTWST7 for 16 cycles with stuck breaker at NORTWST7 (514880) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_31_P4_2_BORDER7 | Apply single-phase fault on and DISCONNECT 527964, near BORDER 7 for 16 cycles with stuck breaker at BORDER 7 (515458) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and drop LOAD 1 514731 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__OKGE_All_35_P4_6_SO4TH4 | Apply single-phase fault on LINE 514731 TO 514790 CKT 1 and LINE 514711 TO 514731 CKT 1, near SO4TH 4 for 6 cycles with stuck breaker at SO4TH 4 (514731) 138 kV Bus. Clear Fault after 10 cycles and trip LINE 514709 TO 514731 CKT 1 and LINE 514731 TO 514815 CKT 1 and DISCONNECT 515758 and LOAD 1 514731 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_10_P4_2_BullShoals | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_11_P4_2_BullShoals | Apply single-phase fault on LINE 338104 TO 338121 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and drop LOAD 1 338121 and drop LOAD 1 338122 and drop LOAD 1 338124 and DISCONNECT 338121 and DISCONNECT 338122 and DISCONNECT 338123 and DISCONNECT 338124 and DISCONNECT 505462 and DISCONNECT 505464 and DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_12_P4_2_BullShoals | Apply single-phase fault on LINE 300095 TO 301057 CKT 1, near BULL SH5 for 5 cycles with stuck breaker at BULL SH5 (505460) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505460 and trip GENERATOR 1 505462 and trip GENERATOR 2 505464 and trip GENERATOR 3 505466 and trip GENERATOR 4 505466 and trip DISCONNECT 505462 and trip DISCONNECT 505464 and trip DISCONNECT 505466 and drop LOAD A1 338813 and DISCONNECT 338813 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_13_P4_2_TableRock | Apply single-phase fault on LINE 505461 TO 338110 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_14_P4_2_TableRock | Apply single-phase fault on LINE 300130 TO 300727 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_15_P4_2_TableRock | Apply single-phase fault on LINE 338099 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_16_P4_2_TableRock | Apply single-phase fault on LINE 505496 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_17_P4_2_TableRock | Apply single-phase fault on LINE 547497 TO 505472 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505472 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_18_P4_2_TableRock | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near TABLE R5 for 5 cycles with stuck breaker at TABLE R5 (505472) 161 kV Bus. Clear Fault after 12 cycles and trip LINE 505474 TO 300735 CKT 1 and DISCONNECT 505473 and trip GENERATOR 1 505476 and trip GENERATOR 2 505476 and trip GENERATOR 3 505478 and trip GENERATOR 4 505478 and DISCONNECT 505473 and DISCONNECT 505475 and DISCONNECT 505476 and DISCONNECT 505478 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_19_P4_2_Norfork | Apply single-phase fault on LINE 505460 TO 300081 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338125 and drop LOAD A1 338813 and drop LOAD A1 338814 and DISCONNECT 338125 and DISCONNECT 338606 and DISCONNECT 338607 and DISCONNECT 338608 and DISCONNECT 338609 and DISCONNECT 338813 and DISCONNECT 338814 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_20_P4_2_Norfork | Apply single-phase fault on LINE 505461 TO 504440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_21_P4_2_Norfork | Apply single-phase fault on LINE 301549 TO 505448 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_22_P4_2_Norfork | Apply single-phase fault on LINE 338132 TO 338129 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338130 and drop LOAD 1 338131 and DISCONNECT 338130 and DISCONNECT 338131 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_23_P4_2_Norfork | Apply single-phase fault on LINE 505442 TO 505440 CKT 1, near NORFORK5 for 5 cycles with stuck breaker at NORFORK5 (505448) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505448 and trip GENERATOR 1 505452 and trip GENERATOR 2 505454 and drop LOAD 1 338220 and drop LOAD A1 504080 and DISCONNECT 338220 and DISCONNECT 504080 and DISCONNECT 504081 and DISCONNECT 504082 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505452 and DISCONNECT 505454 and drop LOAD A1 338813 and DISCONNECT 338813 and drop LOAD A1 338814 and DISCONNECT 338814 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_24_P4_2_Norfork | Apply single-phase fault on LINE 301121 TO 505458 CKT 1, near NORFORK2 for 5 cycles with stuck breaker at NORFORK2 (505450) 69 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505450 and drop LOAD A1 504448 and drop LOAD 1 505458 and DISCONNECT 504448 and DISCONNECT 505449 and DISCONNECT 505451 and DISCONNECT 505458 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_7_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505472 TO 505496 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD 1 300718 and drop LOAD 1 338120 and DISCONNECT 300718 and DISCONNECT 338120 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_8_P4_2_BullShoalsWest | Apply single-phase fault on LINE 505448 TO 504440 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and drop LOAD A1 504440 and DISCONNECT 504440 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__SPA_All_9_P4_2_BullShoalsWest | Apply single-phase fault on LINE 338110 TO 505461 CKT 1, near BULL SH W5 for 5 cycles with stuck breaker at BULL SH W5 (505461) 161 kV Bus. Clear Fault after 12 cycles and DISCONNECT 505461 and trip GENERATOR 5 505468 and trip GENERATOR 6 505468 and trip GENERATOR 7 505470 and trip GENERATOR 8 505470 and DISCONNECT 505468 and DISCONNECT 505470 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_50_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520422 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_51_P4_2_ANADARK4 | Apply single-phase fault on LINE 521059 TO 520501 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 520814 CKT 1 and LINE 520812 TO 520814 CKT 1 and LINE 520814 TO 520923 CKT 1 and trip GENERATOR 1 520812 and drop LOAD F1 520812 and drop LOAD V1 520812 and DISCONNECT 520812 and drop LOAD 1 520496 and drop LOAD 1 520501 and drop LOAD 1 521031 and DISCONNECT 520496 and DISCONNECT 520501 and DISCONNECT 521031 and DISCONNECT 521072 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_52_P4_2_ANADARK4 | Apply single-phase fault on LINE 521129 TO 521024 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 511477 TO 520814 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_53_P4_2_CANADNS4 | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near CANADNS4 for 6 cycles with stuck breaker at CANADNS4 (520842) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 514947 TO 520842 CKT 1 and LINE 520842 TO 514947 CKT 1 and drop LOAD 1 520924 and DISCONNECT 520924 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_54_P4_2_FRNKLNS4 | Apply single-phase fault on LINE 520842 TO 514947 CKT 1, near FRNKLNS4 for 6 cycles with stuck breaker at FRNKLNS4 (520917) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 514946 and LINE 520917 TO 514946 CKT 1 and drop LOAD 1 520400 and drop LOAD 1 520975 and DISCONNECT 520400 and DISCONNECT 520975 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_55_P4_2_FTSUPLY4 | Apply single-phase fault on LINE 520922 TO 520920 CKT 1 and trip GENERATOR 1 521145 and DISCONNECT 520922 and DISCONNECT 521141 and DISCONNECT 521144 and DISCONNECT 521145 and DISCONNECT 521151, near FTSUPLY4 for 6 cycles with stuck breaker at FTSUPLY4 (520920) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and LINE 520920 TO 520957 CKT 1 and drop LOAD 1 520957 and DISCONNECT 520957 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_56_P4_2_HUGOPP4 | Apply single-phase fault on LINE 510887 TO 520448 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 505602 TO 521044 CKT 1 and drop LOAD 1 515370 and drop LOAD 1 515568 and drop LOAD 1 520463 and drop LOAD 1 520483 and drop LOAD 1 520497 and drop LOAD 1 520918 and drop LOAD 1 521077 and drop LOAD 1 521115 and DISCONNECT 515370 and DISCONNECT 515568 and DISCONNECT 520463 and DISCONNECT 520483 and DISCONNECT 520497 and DISCONNECT 520826 and DISCONNECT 520884 and DISCONNECT 520918 and DISCONNECT 521049 and DISCONNECT 521077 and DISCONNECT 521098 and DISCONNECT 521115 and drop LOAD 1 520411 and drop LOAD 1 520874 and drop LOAD 1 520968 and drop LOAD 1 521036 and DISCONNECT 520411 and DISCONNECT 520874 and DISCONNECT 520968 and DISCONNECT 521036 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | LT__WFEC_All_57_P4_2_HUGOPP4 | Apply single-phase fault on LINE 521194 TO 521195 CKT 1, near HUGO PP4 for 6 cycles with stuck breaker at HUGO PP4 (520948) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520948 TO 510918 CKT 1 and LINE 520948 TO 521079 CKT 1 and trip GENERATOR 1 520947 and drop LOAD F1 520947 and drop LOAD V1 520947 and DISCONNECT 520947 and drop LOAD 1 520419 and drop LOAD 1 520466 and drop LOAD 1 520834 and drop LOAD 1 520946 and drop LOAD 1 521079 and DISCONNECT 520419 and DISCONNECT 520466 and DISCONNECT 520834 and DISCONNECT 520946 and DISCONNECT 520953 and DISCONNECT 521079 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | LT__WFEC_All_58_P4_2_MARIETTAS4 | Apply single-phase fault on LINE 515150 TO 514808 CKT 1, near MARIETA4 for 6 cycles with stuck breaker at MARIETA4 (520988) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520988 TO 515160 CKT 1 and LINE 520981 TO 520864 CKT 1 and drop LOAD 1 520455 and drop LOAD 1 520487 and drop LOAD 1 520488 and drop LOAD 1 520511 and drop LOAD 1 520901 and drop LOAD 1 521038 and drop LOAD 1 521061 and drop LOAD 1 521066 and DISCONNECT 520455 and DISCONNECT 520467 and DISCONNECT 520487 and DISCONNECT 520488 and DISCONNECT 520511 and DISCONNECT 520901 and DISCONNECT 520939 and DISCONNECT 520972 and DISCONNECT 521038 and DISCONNECT 521061 and DISCONNECT 521066 and DISCONNECT 521067 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_59_P4_2_NOELSW4 | Apply single-phase fault on LINE 521200 TO 520431 CKT 1, near NOELSW 4 for 6 cycles with stuck breaker at NOELSW 4 (520430) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520436 TO 515853 CKT 1 and LINE 520430 TO 520437 CKT 1 and drop LOAD 1 520431 and drop LOAD 1 520437 and drop LOAD 2 520437 and DISCONNECT 520431 and DISCONNECT 520437 and drop LOAD 1 520436 and drop LOAD 1 520601 and DISCONNECT 520436 and DISCONNECT 520601 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_60_P4_2_OKEENE4 | Apply single-phase fault on LINE 520882 TO 521016 CKT 1, near OKEENE 4 for 6 cycles with stuck breaker at OKEENE 4 (521016) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520999 TO 515853 CKT 1 and drop LOAD 1 520425 and drop LOAD 1 520507 and DISCONNECT 520425 and DISCONNECT 520848 and DISCONNECT 520507 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_61_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 520510 CKT 1 and LINE 511449 TO 511483 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and drop LOAD 1 520472 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and DISCONNECT 520473 and DISCONNECT 520472 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_62_P4_2_PHAROAH4 | Apply single-phase fault on LINE 300686 TO 300137 CKT 1, near PHAROAH4 for 6 cycles with stuck breaker at PHAROAH4 (521026) 138 kV Bus. Clear Fault after 9 cycles and trip DISCONNECT 301553 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_63_P4_2_TWNLKSW4 | Apply single-phase fault on LINE 520882 TO 520535 CKT 1, near TWNLKSW4 for 6 cycles with stuck breaker at TWNLKSW4 (521073) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520533 TO 520865 CKT 1 and LINE 521073 TO 520540 CKT Z1 and drop LOAD 1 520879 and drop LOAD 1 520540 and DISCONNECT 520879 and DISCONNECT 520540 and drop LOAD 1 521037 and drop LOAD 1 515930 and drop LOAD 1 520546 and drop LOAD 1 520479 and DISCONNECT 521037 and DISCONNECT 520474 and DISCONNECT 515930 and DISCONNECT 520545 and DISCONNECT 520546 and DISCONNECT 520847 and DISCONNECT 520479 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_64_P4_2_WAKTASW4 | Apply single-phase fault on LINE 515544 TO 515546 CKT 1, near WAKTASW4 for 6 cycles with stuck breaker at WAKTASW4 (520434) 138 kV Bus. Clear Fault after 9 cycles and DISCONNECT 520434 and drop LOAD 1 520409 and drop LOAD 1A 520409 and DISCONNECT 520409 and DISCONNECT 520435 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_65_P4_2_WASHITA4 | Apply single-phase fault on LINE 511485 TO 520856 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 1 and LINE 521089 TO 521017 CKT 1 and drop LOAD 1 520468 and drop LOAD 1 520503 and drop LOAD 1 520856 and drop LOAD 1 520950 and drop LOAD 1 521010 and drop LOAD 2 521010 and drop LOAD 1 521017 and drop LOAD 1 521050 and drop LOAD 1 521092 and DISCONNECT 520468 and DISCONNECT 520503 and DISCONNECT 520827 and DISCONNECT 520856 and DISCONNECT 520950 and DISCONNECT 521010 and DISCONNECT 521017 and DISCONNECT 521050 and DISCONNECT 521092 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_66_P4_2_WASHITA4 | Apply single-phase fault on LINE 515802 TO 521089 CKT 1, near WASHITA4 for 6 cycles with stuck breaker at WASHITA4 (521089) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 515802 TO 521089 CKT 2 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_75_P4_2_ANADARK4 | Apply single-phase fault on LINE 520864 TO 520900 CKT 1 and LINE 520912 TO 520923 CKT 1, near ANADARK4 for 6 cycles with stuck breaker at ANADARK4 (520814) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520814 TO 520923 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 520867 TO 520510 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520900 and drop LOAD 1 520923 and DISCONNECT 520900 and DISCONNECT 520923 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LT__WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LT__WFEC_All_76_P4_2_PAYNE | Apply single-phase fault on LINE 521104 TO 520861 CKT 1, near PAYNESW4 for 6 cycles with stuck breaker at PAYNESW4 (520888) 138 kV Bus. Clear Fault after 9 cycles and trip LINE 520888 TO 521023 CKT 1 and LINE 520888 TO 521023 CKT 1 and LINE 511449 TO 511502 CKT 1 and LINE 520814 TO 520923 CKT 1 and drop LOAD 1 520547 and drop LOAD 2 520547 and drop LOAD 1A 520604 and DISCONNECT 520422 and DISCONNECT 520510 and DISCONNECT 520604 and DISCONNECT 520867 and DISCONNECT 520547 and drop LOAD 1 520861 and drop LOAD 1 520868 and DISCONNECT 520861 and DISCONNECT 520868 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LTLRLKT2__TXPLSTP2 | 3 Phase fault on LTLRLKT2 (514983) 69 kV Bus a. Apply fault at the LTLRLKT2 (514983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLRLKT2 69.0 KV 514983 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LTLRLKT2__TXPLSTP2 | 3 Phase fault on LTLRLKT2 (514983) 69 kV Bus a. Apply fault at the LTLRLKT2 (514983) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LTLRLKT2 69.0 KV 514983 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LYDIA__7__VALIANT7 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | LYDIA__7__VALIANT7 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | LYDIA__7__WELSH__7 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | LYDIA__7__WELSH__7 | 3 Phase fault on LYDIA 7 (508298) 345 kV Bus a. Apply fault at the LYDIA 7 (508298) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LYDIA 7 345.0 KV 508298 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MACOCTP2__LITLAXT2 | 3 Phase fault on MACOCTP2 (514956) 69 kV Bus a. Apply fault at the MACOCTP2 (514956) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACOCTP2 69.0 KV 514956 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MACOCTP2__LITLAXT2 | 3 Phase fault on MACOCTP2 (514956) 69 kV Bus a. Apply fault at the MACOCTP2 (514956) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACOCTP2 69.0 KV 514956 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MAMTHPW7__515586_0 | 3 Phase fault on MAMTHPW7 (515585) 345 kV Bus a. Apply fault at the MAMTHPW7( 515585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MAMTHPW7 515585 TO MMTHPW11 515586 TO MMTHPWT1 515588 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MAMTHPW7__515586_0 | 3 Phase fault on MAMTHPW7 (515585) 345 kV Bus a. Apply fault at the MAMTHPW7( 515585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MAMTHPW7 515585 TO MMTHPW11 515586 TO MMTHPWT1 515588 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MANDEVILTP4__504363_0 | 3 Phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4( 508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MANDEVILTP4__504363_0 | 3 Phase fault on MANDEVILTP4 (508105) 138 kV Bus a. Apply fault at the MANDEVILTP4( 508105) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANDEVILTP4 508105 TO NE-TEXARK2 504363 TO NE-TEXARK1 504364 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARAUTO2__508557_0 | 3 Phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2( 508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARAUTO2__508557_0 | 3 Phase fault on MARAUTO2 (508576) 69 kV Bus a. Apply fault at the MARAUTO2( 508576) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARAUTO2 508576 TO MARSHL-4 508557 TO MRSH4#21 508592 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARSHL_4__CTNWOOD4 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARSHL_4__CTNWOOD4 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO CTNWOOD4 138.0 KV 514827 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARSHL_4__JEFFRSN4 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARSHL_4__JEFFRSN4 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO JEFFRSN4 138.0 KV 508835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARSHL_4__MARSHAL4 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARSHL_4__MARSHAL4 | 3 Phase fault on MARSHL 4 (514733) 138 kV Bus a. Apply fault at the MARSHL 4 (514733) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL 4 138.0 KV 514733 TO MARSHAL4 138.0 KV 521006 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MARSHL_4__PIRKEY_4 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MARSHL_4__PIRKEY_4 | 3 Phase fault on MARSHL-4 (508557) 138 kV Bus a. Apply fault at the MARSHL-4 (508557) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARSHL-4 138.0 KV 508557 TO PIRKEY 4 138.0 KV 508562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MATHSWSN7_345kV_515497 | Apply single-phase fault on: NORTWST7 345KV 514880 TO MATHSWSN7 345.0 KV 515497 CKT 1, near MATHSWSN7 345kV for 6 cycles with stuck breaker at MATHSWSN7 345kV. Clear Fault after 16 cycles and trip: CIMARON7 345.0 KV 514901 TO MATHSWSN7 345.0 KV 515497 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MATHSWSN7_345kV_515497 | Apply single-phase fault on: NORTWST7 345KV 514880 TO MATHSWSN7 345.0 KV 515497 CKT 1, near MATHSWSN7 345kV for 6 cycles with stuck breaker at MATHSWSN7 345kV. Clear Fault after 16 cycles and trip: CIMARON7 345.0 KV 514901 TO MATHSWSN7 345.0 KV 515497 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MATHWSN7__REDNGTN7 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2016-119 (587953, 587958). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MATHWSN7__REDNGTN7 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25S | Transfer | MATHWSN7__TRAVERSE3 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6.GEN-2016-119 (587953, 587958) and GEN-2017-150 (761232) trip on Voltage Protection | Lower acceleration to 0.2. Disable Voltage Protection for GEN-2016-119 (587953, 587958) and GEN-2017-150 (761232)
04 - Southeast | 25W | Transfer | MATHWSN7__TRAVERSE3 | 3 Phase fault on MATHWSN7 (515497) 345 kV Bus a. Apply fault at the MATHWSN7 (515497) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MATHWSN7 345.0 KV 515497 TO TRAVERSE3 345.0 KV 900001 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | MAUD___4__515054_0 | 3 Phase fault on MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4( 515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MAUD___4__515054_0 | 3 Phase fault on MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4( 515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 515055 TO MAUD 2 515054 TO MAUD 1 515736 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MAUD___4__FRSTHIL4 | 3 Phase fault on MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MAUD___4__FRSTHIL4 | 3 Phase fault on MAUD 4 (515055) 138 kV Bus a. Apply fault at the MAUD 4 (515055) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 4 138.0 KV 515055 TO FRSTHIL4 138.0 KV 515075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MAUDT__2__REDWATR2 | 3 Phase fault on MAUDT 2 (509653) 69 kV Bus a. Apply fault at the MAUDT 2 (509653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69.0 KV 509653 TO REDWATR2 69.0 KV 509667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MAUDT__2__REDWATR2 | 3 Phase fault on MAUDT 2 (509653) 69 kV Bus a. Apply fault at the MAUDT 2 (509653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUDT 2 69.0 KV 509653 TO REDWATR2 69.0 KV 509667 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MAY_AVE2__38TH_ST2 | 3 Phase fault on MAY AVE2 (514913) 69 kV Bus a. Apply fault at the MAY AVE2 (514913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAY AVE2 69.0 KV 514913 TO SW 5TH 2 69.0 KV 514919 CKT 1 b.2. 38TH ST2 69.0 KV 514845 TO MAY AVE2 69.0 KV 514913 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MAY_AVE2__38TH_ST2 | 3 Phase fault on MAY AVE2 (514913) 69 kV Bus a. Apply fault at the MAY AVE2 (514913) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAY AVE2 69.0 KV 514913 TO SW 5TH 2 69.0 KV 514919 CKT 1 b.2. 38TH ST2 69.0 KV 514845 TO MAY AVE2 69.0 KV 514913 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MCALEST4__TALAWANDA__4 | 3 Phase fault on MCALEST4 (510908) 138 kV Bus a. Apply fault at the MCALEST4 (510908) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MCALEST4__TALAWANDA__4 | 3 Phase fault on MCALEST4 (510908) 138 kV Bus a. Apply fault at the MCALEST4 (510908) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALEST4 138.0 KV 510908 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MCALESTIND_4__TALAWANDA__4 | 3 Phase fault on MCALESTIND 4 (510909) 138 kV Bus a. Apply fault at the MCALESTIND 4 (510909) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALESTIND 4 138.0 KV 510909 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MCALESTIND_4__TALAWANDA__4 | 3 Phase fault on MCALESTIND 4 (510909) 138 kV Bus a. Apply fault at the MCALESTIND 4 (510909) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCALESTIND 4 138.0 KV 510909 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MCCLAIN4_138kV_514902 | Apply single-phase fault on: MCCLAIN4 138KV 514902 TO PLVALLY4 138.0 KV 514929 CKT 1, near MCCLAIN4 138kV for 7 cycles with stuck breaker at MCCLAIN4 138kV. Clear Fault after 16 cycles and trip: G17-152-TAP 138KV 914902 TO MCCLAIN4 138KV 514902 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MCCLAIN4_138kV_514902 | Apply single-phase fault on: MCCLAIN4 138KV 514902 TO PLVALLY4 138.0 KV 514929 CKT 1, near MCCLAIN4 138kV for 7 cycles with stuck breaker at MCCLAIN4 138kV. Clear Fault after 16 cycles and trip: SW134TP4 138KV 514876 TO MCCLAIN4 138KV 514902 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MCDWL_CREEK6__POTTER_CO__6 | 3 Phase fault on MCDWL_CREEK6 (523323) 230 kV Bus a. Apply fault at the MCDWL_CREEK6 (523323) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCDWL_CREEK6 230.0 KV 523323 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MCLOUD_2__MCLOUDT2 | 3 Phase fault on MCLOUD 2 (515065) 69 kV Bus a. Apply fault at the MCLOUD 2 (515065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69.0 KV 515065 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MCLOUD_2__MCLOUDT2 | 3 Phase fault on MCLOUD 2 (515065) 69 kV Bus a. Apply fault at the MCLOUD 2 (515065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUD 2 69.0 KV 515065 TO MCLOUDT2 69.0 KV 515504 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MCLOUDT2__SINCPNT2 | 3 Phase fault on MCLOUDT2 (515504) 69 kV Bus a. Apply fault at the MCLOUDT2 (515504) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69.0 KV 515504 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MCLOUDT2__SINCPNT2 | 3 Phase fault on MCLOUDT2 (515504) 69 kV Bus a. Apply fault at the MCLOUDT2 (515504) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCLOUDT2 69.0 KV 515504 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MEEKRSW4__WREDHIL4 | 3 Phase fault on MEEKRSW4 (520994) 138 kV Bus a. Apply fault at the MEEKRSW4 (520994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEEKRSW4 138.0 KV 520994 TO WREDHIL4 138.0 KV 521097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MEEKRSW4__WREDHIL4 | 3 Phase fault on MEEKRSW4 (520994) 138 kV Bus a. Apply fault at the MEEKRSW4 (520994) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEEKRSW4 138.0 KV 520994 TO WREDHIL4 138.0 KV 521097 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MEMRIAL4__DANFRTH4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MEMRIAL4__DANFRTH4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MEMRIAL4__JONESSB4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 b.2. LOAD 1 514839 b.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 b.4. LOAD 1 515459 b.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MEMRIAL4__JONESSB4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO BRYANT 4 138.0 KV 514839 CKT 1 b.2. LOAD 1 514839 b.3. BRYANT 4 138.0 KV 514839 TO ACORN 4 138.0 KV 515459 CKT 1 b.4. LOAD 1 515459 b.5. ACORN 4 138.0 KV 515459 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MEMRIAL4__REMPKTP4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138.0 KV 514501 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138.0 KV 514501 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MEMRIAL4__REMPKTP4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLYAV4 138.0 KV 514501 TO MEMRIAL4 138.0 KV 514835 CKT 1 b.2. LOAD 1 514835 b.3. KELLYAV4 138.0 KV 514501 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MEMRIAL4__SKYLINE4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO SKYLINE4 138.0 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MEMRIAL4__SKYLINE4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO SKYLINE4 138.0 KV 514850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MEMRIAL4__TENESTP4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MEMRIAL4__TENESTP4 | 3 Phase fault on MEMRIAL4 (514835) 138 kV Bus a. Apply fault at the MEMRIAL4 (514835) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEMRIAL4 138.0 KV 514835 TO TENESTP4 138.0 KV 514837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MIDWEST4__FRNKLNS4 | 3 Phase fault on MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MIDWEST4__FRNKLNS4 | 3 Phase fault on MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MIDWEST4__HOLLYWD4 | 3 Phase fault on MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MIDWEST4__HOLLYWD4 | 3 Phase fault on MIDWEST4 (514946) 138 kV Bus a. Apply fault at the MIDWEST4 (514946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDWEST4 138.0 KV 514946 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-095 (587773)
04 - Southeast | 25W | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-095 (587773)
04 - Southeast | 25S | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) and GEN-2017-150 (761232) trip on Voltage Protection | Disable Voltage Protection for GEN-2016-095 (587773) and GEN-2017-150 (761232)
04 - Southeast | 25S | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-095 (587773)
04 - Southeast | 25S | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-095 (587773)
04 - Southeast | 25S | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. GEN-2016-095 (587773) trips on Voltage Protection | Remove Reclose. Disable Voltage Protection for GEN-2016-095 (587773)
04 - Southeast | 25S | Transfer | MINCO__7__NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-095 (587773)
04 - Southeast | 25W | Transfer | MINCO__7__NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-095 (587773) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-095 (587773)
04 - Southeast | 25S | Transfer | MINCO_345kV_514801 | Apply single-phase fault on: MINCO7 345KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1, near MINCO 345kV for 6 cycles with stuck breaker at MINCO 345kV. Clear Fault after 16 cycles and trip: MINCO7 345KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINCO_345kV_514801 | Apply single-phase fault on: MINCO7 345KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1, near MINCO 345kV for 6 cycles with stuck breaker at MINCO 345kV. Clear Fault after 16 cycles and trip: MINCO7 345KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MINGO_S4__T_S_E__4 | 3 Phase fault on MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138.0 KV 509761 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MINGO_S4__T_S_E__4 | 3 Phase fault on MINGO-S4 (509761) 138 kV Bus a. Apply fault at the MINGO-S4 (509761) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MINGO-S4 138.0 KV 509761 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MNCWND37__MNCWND47 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | MNCWND37__MNCWND47 | 3 Phase fault on MNCWND37 (515549) 345 kV Bus a. Apply fault at the MNCWND37 (515549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND37 345.0 KV 515549 TO MNCWND47 345.0 KV 515939 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25S | Transfer | MNCWND47__515940_0 | 3 Phase fault on MNCWND47 (515939) 345 kV Bus a. Apply fault at the MNCWND47( 515939) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND47 515939 TO MNCO4L11 515940 TO MNCO4T11 515941 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MNCWND47__515940_0 | 3 Phase fault on MNCWND47 (515939) 345 kV Bus a. Apply fault at the MNCWND47( 515939) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND47 515939 TO MNCO4L11 515940 TO MNCO4T11 515941 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MNCWND47__MNCWND57 | 3 Phase fault on MNCWND47 (515939) 345 kV Bus a. Apply fault at the MNCWND47 (515939) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND47 345.0 KV 515939 TO MNCWND57 345.0 KV 515980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | MNCWND47__MNCWND57 | 3 Phase fault on MNCWND47 (515939) 345 kV Bus a. Apply fault at the MNCWND47 (515939) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MNCWND47 345.0 KV 515939 TO MNCWND57 345.0 KV 515980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | MOORE__4__OAKCRK_4 | 3 Phase fault on MOORE 4 (514955) 138 kV Bus a. Apply fault at the MOORE 4 (514955) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 4 138.0 KV 514955 TO OAKCRK 4 138.0 KV 514960 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MOORE__4__OAKCRK_4 | 3 Phase fault on MOORE 4 (514955) 138 kV Bus a. Apply fault at the MOORE 4 (514955) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 4 138.0 KV 514955 TO OAKCRK 4 138.0 KV 514960 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | MOORLND4__520995_0 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4( 520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MOORLND4__520995_0 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4( 520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 520999 TO MOORLND2 520995 TO MLNDTERT 521180 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MOORLND4__GEN_2016_020 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MOORLND4__GEN_2016_020 | 3 Phase fault on MOORLND4 (520999) 138 kV Bus a. Apply fault at the MOORLND4 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 138.0 KV 520999 TO GEN-2016-020 138.0 KV 587140 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MRIETA_2__ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MRIETA_2__ROCKYPT4 | 3 Phase fault on MRIETA 2 (515160) 138 kV Bus a. Apply fault at the MRIETA 2 (515160) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MRIETA 2 138.0 KV 515160 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MSKPORT5__MSKPTAP5 | 3 Phase fault on MSKPORT5 (515184) 161 kV Bus a. Apply fault at the MSKPORT5 (515184) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPORT5 161.0 KV 515184 TO MSKPTAP5 161.0 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MSKPORT5__MSKPTAP5 | 3 Phase fault on MSKPORT5 (515184) 161 kV Bus a. Apply fault at the MSKPORT5 (515184) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSKPORT5 161.0 KV 515184 TO MSKPTAP5 161.0 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MSTANG_2__38TH_ST2 | 3 Phase fault on MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 69.0 KV 514860 TO WODLAWN2 69.0 KV 514915 CKT 1 b.2. LOAD 1 514915 b.3. BETHANY2 69.0 KV 514914 TO WODLAWN2 69.0 KV 514915 CKT 1 b.4. LOAD 1 514915 b.5. 38TH ST2 69.0 KV 514845 TO BETHANY2 69.0 KV 514914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG (515668, 515669) trips on Voltage Protection | Disable Voltage Protection for MSTNG (515668, 515669)
04 - Southeast | 25W | Transfer | MSTANG_2__38TH_ST2 | 3 Phase fault on MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 69.0 KV 514860 TO WODLAWN2 69.0 KV 514915 CKT 1 b.2. LOAD 1 514915 b.3. BETHANY2 69.0 KV 514914 TO WODLAWN2 69.0 KV 514915 CKT 1 b.4. LOAD 1 514915 b.5. 38TH ST2 69.0 KV 514845 TO BETHANY2 69.0 KV 514914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | MSTANG_2__514861_0 | 3 Phase fault on MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2( 514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 514860 TO MUSTANG4 514861 TO MUSTANG1 515740 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MSTANG_2__514861_0 | 3 Phase fault on MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2( 514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 514860 TO MUSTANG4 514861 TO MUSTANG1 515740 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | MSTANG_2__PENN___2 | 3 Phase fault on MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 69.0 KV 514860 TO MCARTHR2 69.0 KV 514917 CKT 1 b.2. LOAD 1 514917 b.3. MCARTHR2 69.0 KV 514917 TO SW 64TH2 69.0 KV 514918 CKT 1 b.4. LOAD 1 514918 b.5. SW 64TH2 69.0 KV 514918 TO PENN 2 69.0 KV 514924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG (515668, 515669) trips on Voltage Protection | Disable Voltage Protection for MSTNG (515668, 515669)
04 - Southeast | 25W | Transfer | MSTANG_2__PENN___2 | 3 Phase fault on MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 69.0 KV 514860 TO MCARTHR2 69.0 KV 514917 CKT 1 b.2. LOAD 1 514917 b.3. MCARTHR2 69.0 KV 514917 TO SW 64TH2 69.0 KV 514918 CKT 1 b.4. LOAD 1 514918 b.5. SW 64TH2 69.0 KV 514918 TO PENN 2 69.0 KV 514924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | MSTANG_2__WILROGR2 | 3 Phase fault on MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 69.0 KV 514860 TO WILROGR2 69.0 KV 514916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG (515668, 515669) trips on Voltage Protection | Disable Voltage Protection for MSTNG (515668, 515669)
04 - Southeast | 25W | Transfer | MSTANG_2__WILROGR2 | 3 Phase fault on MSTANG 2 (514860) 69 kV Bus a. Apply fault at the MSTANG 2 (514860) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTANG 2 69.0 KV 514860 TO WILROGR2 69.0 KV 514916 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | MSTNG_8G__514861_0 | 3 Phase fault on MSTNG 8G (515670) 13.8 kV Bus a. Apply fault at the MSTNG 8G( 515670) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG 8G 515670 TO MUSTANG4 514861 TO MSTNG 9G 515671 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MSTNG_8G__514861_0 | 3 Phase fault on MSTNG 8G (515670) 13.8 kV Bus a. Apply fault at the MSTNG 8G( 515670) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG 8G 515670 TO MUSTANG4 514861 TO MSTNG 9G 515671 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), and MSTNG 11G (515673) trips on Voltage Protection | Disable Voltage Protection forMSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), and MSTNG 11G (515673)
04 - Southeast | 25S | Transfer | MSTNG10G__514861_0 | 3 Phase fault on MSTNG10G (515672) 13.8 kV Bus a. Apply fault at the MSTNG10G( 515672) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG10G 515672 TO MUSTANG4 514861 TO MSTNG11G 515673 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MSTNG10G__514861_0 | 3 Phase fault on MSTNG10G (515672) 13.8 kV Bus a. Apply fault at the MSTNG10G( 515672) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MSTNG10G 515672 TO MUSTANG4 514861 TO MSTNG11G 515673 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUNZCTY4__DUGLASV4 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUNZCTY4__DUGLASV4 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO DUGLASV4 138.0 KV 509666 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUNZCTY4__WILKES_4 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUNZCTY4__WILKES_4 | 3 Phase fault on MUNZCTY4 (508064) 138 kV Bus a. Apply fault at the MUNZCTY4 (508064) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNZCTY4 138.0 KV 508064 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKOGE2__515222_0 | 3 Phase fault on MUSKOGE2 (515221) 69 kV Bus a. Apply fault at the MUSKOGE2( 515221) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE2 515221 TO MUSKOGE5 515222 TO MUSKOG41 515797 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUSKOGE2__515222_0 | 3 Phase fault on MUSKOGE2 (515221) 69 kV Bus a. Apply fault at the MUSKOGE2( 515221) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE2 515221 TO MUSKOGE5 515222 TO MUSKOG41 515797 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKOGE5__MSKPTAP5 | 3 Phase fault on MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161.0 KV 515222 TO MSKPTAP5 161.0 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUSKOGE5__MSKPTAP5 | 3 Phase fault on MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161.0 KV 515222 TO MSKPTAP5 161.0 KV 515232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKOGE5__TAHLQH_5 | 3 Phase fault on MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161.0 KV 515222 TO KETOWAH5 161.0 KV 516027 CKT 1 b.2. LOAD 1 516027 b.3. 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUSKOGE5__TAHLQH_5 | 3 Phase fault on MUSKOGE5 (515222) 161 kV Bus a. Apply fault at the MUSKOGE5 (515222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKOGE5 161.0 KV 515222 TO KETOWAH5 161.0 KV 516027 CKT 1 b.2. LOAD 1 516027 b.3. 7CLANS 5 161.0 KV 515956 TO KETOWAH5 161.0 KV 516027 CKT 1 b.4. LOAD 1 516027 b.5. TAHLQH 5 161.0 KV 512655 TO 7CLANS 5 161.0 KV 515956 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKOGE7__FIREWHL_TAP | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSKOGE7__FIREWHL_TAP | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKOGE7__FTSMITH7 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSKOGE7__FTSMITH7 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345.0 KV 515302 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKOGE7__GEN_2017_155 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO GEN-2017-155 345.0 KV 761334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSKOGE7__GEN_2017_155 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO GEN-2017-155 345.0 KV 761334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKOGE7__PECANCK7 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSKOGE7__PECANCK7 | 3 Phase fault on MUSKOGE7 (515224) 345 kV Bus a. Apply fault at the MUSKOGE7 (515224) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKOGEE_345kV_515224 | Apply single-phase fault on: CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1, near MUSKOGEE 345kV for 6 cycles with stuck breaker at MUSKOGEE 345kV. Clear Fault after 16 cycles and trip: MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345KV 515302 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUSKOGEE_345kV_515224 | Apply single-phase fault on: CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1, near MUSKOGEE 345kV for 6 cycles with stuck breaker at MUSKOGEE 345kV. Clear Fault after 16 cycles and trip: MUSKOGE7 345.0 KV 515224 TO FTSMITH7 345KV 515302 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKTAP5__FT_GIB_5 | 3 Phase fault on MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161.0 KV 505558 TO FT GIB 5 161.0 KV 505560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUSKTAP5__FT_GIB_5 | 3 Phase fault on MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161.0 KV 505558 TO FT GIB 5 161.0 KV 505560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSKTAP5__MUSKOGE5 | 3 Phase fault on MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161.0 KV 505558 TO MUSKOGE5 161.0 KV 515222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUSKTAP5__MUSKOGE5 | 3 Phase fault on MUSKTAP5 (505558) 161 kV Bus a. Apply fault at the MUSKTAP5 (505558) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSKTAP5 161.0 KV 505558 TO MUSKOGE5 161.0 KV 515222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUSTANG2_69kV_514860 | Apply single-phase fault on: MUSTANG2 69KV 514860 TO WODLAWN2 69KV 514915 CKT 1, near MSTANG 2 69 kV for 7 cycles with stuck breaker at MSTANG 2 69 kV. Clear Fault after 16 cycles and trip: MUSTANG2 69KV 514860 TO MCARTHR2 69.0 KV 514917 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSTANG2_69kV_514860 | Apply single-phase fault on: MUSTANG2 69KV 514860 TO WODLAWN2 69KV 514915 CKT 1, near MSTANG 2 69 kV for 7 cycles with stuck breaker at MSTANG 2 69 kV. Clear Fault after 16 cycles and trip: MUSTANG2 69KV 514860 TO MCARTHR2 69.0 KV 514917 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | MUSTANG4__CIMARON4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO MORGAN 4 138.0 KV 514896 CKT 1 b.2. LOAD 1 514896 b.3. XEROX 4 138.0 KV 514893 TO MORGAN 4 138.0 KV 514896 CKT 1 b.4. LOAD 1 514896 b.5. XEROX 4 138.0 KV 514893 TO CZECHAL4 138.0 KV 514894 CKT 1 b.6. LOAD 1 514894 b.7. CZECHAL4 138.0 KV 514894 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Lower acceleration to 0.2. Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSTANG4__CIMARON4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO MORGAN 4 138.0 KV 514896 CKT 1 b.2. LOAD 1 514896 b.3. XEROX 4 138.0 KV 514893 TO MORGAN 4 138.0 KV 514896 CKT 1 b.4. LOAD 1 514896 b.5. XEROX 4 138.0 KV 514893 TO CZECHAL4 138.0 KV 514894 CKT 1 b.6. LOAD 1 514894 b.7. CZECHAL4 138.0 KV 514894 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6.. MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Lower acceleration to 0.2. Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | MUSTANG4__DAYTON_4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO DAYTON 4 138.0 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-201 | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) . Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSTANG4__DAYTON_4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO DAYTON 4 138.0 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Lower acceleration to 0.2. Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | MUSTANG4__DOUGLTP4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 b.2. LOAD 1 514865 b.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 b.4. LOAD 1 514866 b.5. WESTOAK4 138.0 KV 514866 TO MERIDAN4 138.0 KV 514867 CKT 1 b.6. LOAD 1 514867 b.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-201 | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) . Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSTANG4__DOUGLTP4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 b.2. LOAD 1 514865 b.3. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 b.4. LOAD 1 514866 b.5. WESTOAK4 138.0 KV 514866 TO MERIDAN4 138.0 KV 514867 CKT 1 b.6. LOAD 1 514867 b.7. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | MUSTANG4__GEN_2018_026 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO GEN-2018-026 138.0 KV 762614 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-201 | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) . Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSTANG4__GEN_2018_026 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO GEN-2018-026 138.0 KV 762614 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | MUSTANG4__MORGAN_4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO MORGAN 4 138.0 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-201 | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) . Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSTANG4__MORGAN_4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO MORGAN 4 138.0 KV 514896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | MUSTANG4__SW_5TH_4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO SW 5TH 4 138.0 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-201 | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) . Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | MUSTANG4__SW_5TH_4 | 3 Phase fault on MUSTANG4 (514861) 138 kV Bus a. Apply fault at the MUSTANG4 (514861) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUSTANG4 138.0 KV 514861 TO SW 5TH 4 138.0 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 10G (515672), MSTNG 11G (515673), MSTNG 12G (515674), MSTNG 7G (515669), and MSTNG 6G (515668) . Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | MUSTANG4_138kV_514861 | Apply single-phase fault on: MUSTANG4 138KV 514861 TO SW5TH4 138KV 514920 CKT 1 and 36MER4 138KV 514888 TO SW5TH4 138KV 514920 CKT 1, near MUSTANG4 138kV for 7 cycles with stuck breaker at MUSTANG4 138kV. Clear Fault after 16 cycles and trip: MUSTANG4 138KV 514861 TO COUNCIL4 138KV 514865 CKT 1 and COUNCIL4 138KV 514865 TO WESTOAK4 138KV 514866 CKT 1 and WESTOAK4 138KV 514866 TO MERIDAN4 138KV 514867 CKT 1 and MERIDAN4 138KV 514867 TO DOUGLTP4 138KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | MUSTANG4_138kV_514861 | Apply single-phase fault on: MUSTANG4 138KV 514861 TO SW5TH4 138KV 514920 CKT 1 and 36MER4 138KV 514888 TO SW5TH4 138KV 514920 CKT 1, near MUSTANG4 138kV for 7 cycles with stuck breaker at MUSTANG4 138kV. Clear Fault after 16 cycles and trip: MUSTANG4 138KV 514861 TO COUNCIL4 138KV 514865 CKT 1 and COUNCIL4 138KV 514865 TO WESTOAK4 138KV 514866 CKT 1 and WESTOAK4 138KV 514866 TO MERIDAN4 138KV 514867 CKT 1 and MERIDAN4 138KV 514867 TO DOUGLTP4 138KV 514868 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NASH___4__ALUMAX_4 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NASH___4__ALUMAX_4 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO ALUMAX 4 138.0 KV 508091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | NASH___4__BANN___4 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NASH___4__BANN___4 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO BANN 4 138.0 KV 508054 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | NASH___4__NWTXARK4 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NASH___4__NWTXARK4 | 3 Phase fault on NASH 4 (508049) 138 kV Bus a. Apply fault at the NASH 4 (508049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASH 4 138.0 KV 508049 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | NBENTON2__508811_0 | 3 Phase fault on NBENTON2 (508810) 69 kV Bus a. Apply fault at the NBENTON2( 508810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NBENTON2__508811_0 | 3 Phase fault on NBENTON2 (508810) 69 kV Bus a. Apply fault at the NBENTON2( 508810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON2 508810 TO NBENTON4 508811 TO NBENTON1 508823 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NBENTON4__G16_167_TAP | 3 Phase fault on NBENTON4 (508811) 138 kV Bus a. Apply fault at the NBENTON4 (508811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138.0 KV 508811 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NBENTON4__G16_167_TAP | 3 Phase fault on NBENTON4 (508811) 138 kV Bus a. Apply fault at the NBENTON4 (508811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NBENTON4 138.0 KV 508811 TO G16-167-TAP 138.0 KV 588404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NE10TH_4__RENO___4 | 3 Phase fault on NE10TH 4 (514964) 138 kV Bus a. Apply fault at the NE10TH 4 (514964) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138.0 KV 514964 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NE10TH_4__RENO___4 | 3 Phase fault on NE10TH 4 (514964) 138 kV Bus a. Apply fault at the NE10TH 4 (514964) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE10TH 4 138.0 KV 514964 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NE30TH_2__DEEPFKT2 | 3 Phase fault on NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO DEEPFKT2 69.0 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NE30TH_2__DEEPFKT2 | 3 Phase fault on NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO DEEPFKT2 69.0 KV 514970 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NE30TH_2__RENO___2 | 3 Phase fault on NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO RENO 2 69.0 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NE30TH_2__RENO___2 | 3 Phase fault on NE30TH 2 (514969) 69 kV Bus a. Apply fault at the NE30TH 2 (514969) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE30TH 2 69.0 KV 514969 TO RENO 2 69.0 KV 514972 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NE45TAP4__RUSHING4 | 3 Phase fault on NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE45TAP4 138.0 KV 515062 TO RUSHING4 138.0 KV 515064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NE45TAP4__RUSHING4 | 3 Phase fault on NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NE45TAP4 138.0 KV 515062 TO RUSHING4 138.0 KV 515064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NE45TAP4__WOLVRNT4 | 3 Phase fault on NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCK CK4 138.0 KV 515058 TO NE45TAP4 138.0 KV 515062 CKT 1 b.2. MOBIL 4 138.0 KV 515057 TO ROCK CK4 138.0 KV 515058 CKT 1 b.3. LOAD 1 515058 b.4. MOBIL 4 138.0 KV 515057 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NE45TAP4__WOLVRNT4 | 3 Phase fault on NE45TAP4 (515062) 138 kV Bus a. Apply fault at the NE45TAP4 (515062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCK CK4 138.0 KV 515058 TO NE45TAP4 138.0 KV 515062 CKT 1 b.2. MOBIL 4 138.0 KV 515057 TO ROCK CK4 138.0 KV 515058 CKT 1 b.3. LOAD 1 515058 b.4. MOBIL 4 138.0 KV 515057 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NEWBOST2__DEKALB_2 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO DEKALB 2 69.0 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NEWBOST2__DEKALB_2 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO DEKALB 2 69.0 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NEWBOST2__NNBOSTN2 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO NNBOSTN2 69.0 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NEWBOST2__NNBOSTN2 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO NNBOSTN2 69.0 KV 508068 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NEWBOST2__REDRVR_2 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO REDRVR-2 69.0 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NEWBOST2__REDRVR_2 | 3 Phase fault on NEWBOST2 (508067) 69 kV Bus a. Apply fault at the NEWBOST2 (508067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEWBOST2 69.0 KV 508067 TO REDRVR-2 69.0 KV 508074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NKNGFSH4__DOVERSW4 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NKNGFSH4__DOVERSW4 | 3 Phase fault on NKNGFSH4 (520603) 138 kV Bus a. Apply fault at the NKNGFSH4 (520603) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKNGFSH4 138.0 KV 520603 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NMAGZIN5_161kV_507190 | Apply single-phase fault on: NMAGZIN5 161KV 507190 TO 5 161KV 515316 CKT 1, near NMAGZIN5 161kV for 7 cycles with stuck breaker at NMAGZIN5 161kV. Clear Fault after 16 cycles and trip: NMAGZIN5 161KV 507190 TO MAGZREC5 161.0 KV 507195 CKT 1 and 5DANVLEAR 161KV 337902 TO MAGZREC5 161.0 KV 507195 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NMAGZIN5_161kV_507190 | Apply single-phase fault on: NMAGZIN5 161KV 507190 TO 5 161KV 515316 CKT 1, near NMAGZIN5 161kV for 7 cycles with stuck breaker at NMAGZIN5 161kV. Clear Fault after 16 cycles and trip: NMAGZIN5 161KV 507190 TO MAGZREC5 161.0 KV 507195 CKT 1 and 5DANVLEAR 161KV 337902 TO MAGZREC5 161.0 KV 507195 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NNBOSTN2__508069_0 | 3 Phase fault on NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2( 508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NNBOSTN2__508069_0 | 3 Phase fault on NNBOSTN2 (508068) 69 kV Bus a. Apply fault at the NNBOSTN2( 508068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN2 508068 TO NNBOSTN4 508069 TO NNBT2-1 508099 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NNBOSTN4__ANDRSNC4 | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO RIFFIN REC4 138.0 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. ANDRSNC4 138.0 KV 508050 TO RIFFIN REC4 138.0 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NNBOSTN4__ANDRSNC4 | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO RIFFIN REC4 138.0 KV 508104 CKT 1 b.2. LOAD 1 508104 b.3. ANDRSNC4 138.0 KV 508050 TO RIFFIN REC4 138.0 KV 508104 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NNBOSTN4__G18_003_TAP | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NNBOSTN4__G18_003_TAP | 3 Phase fault on NNBOSTN4 (508069) 138 kV Bus a. Apply fault at the NNBOSTN4 (508069) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NNBOSTN4 138.0 KV 508069 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | NNBOSTN4_138kV_508069 | Apply single-phase fault on: NNBOSTN4 138KV 508069 TO RIFFINREC4 138KV 508104 CKT 1, near NNBOSTN4 138 kV for 7 cycles with stuck breaker at NNBOSTN4 138 kV. Clear Fault after 16 cycles and trip: NNBOSTN4 138KV 508069 TO G18003TAP 138KV 762431 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NNBOSTN4_138kV_508069 | Apply single-phase fault on: NNBOSTN4 138KV 508069 TO RIFFINREC4 138KV 508104 CKT 1, near NNBOSTN4 138 kV for 7 cycles with stuck breaker at NNBOSTN4 138 kV. Clear Fault after 16 cycles and trip: NNBOSTN4 138KV 508069 TO G18003TAP 138KV 762431 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NORTWST4__514880_0 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NORTWST4__514880_0 | 3 Phase fault on NORTWST4 (514879) 138 kV Bus a. Apply fault at the NORTWST4( 514879) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTWST4 514879 TO NORTWST7 514880 TO NORTWS31 515743 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NORTWST7__ARCADIA7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25W | Transfer | NORTWST7__ARCADIA7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO ARCADIA7 345.0 KV 514908 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25S | Transfer | NORTWST7__CIMARON7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25W | Transfer | NORTWST7__CIMARON7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25S | Transfer | NORTWST7__MATHWSN7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25W | Transfer | NORTWST7__MATHWSN7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO MATHWSN7 345.0 KV 515497 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25S | Transfer | NORTWST7__SPRNGCK7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25W | Transfer | NORTWST7__SPRNGCK7 | 3 Phase fault on NORTWST7 (514880) 345 kV Bus a. Apply fault at the NORTWST7 (514880) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NORTWST7 345.0 KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25S | Transfer | NORTWST7_345kV_514880 | Apply single-phase fault on: NORTWST7 345KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1, near NORTWST7 345kV for 6 cycles with stuck breaker at NORTWST7 345kV. Clear Fault after 16 cycles and trip: NORTWST7 345.0 KV 514880 TO ARCADIA 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NORTWST7_345kV_514880 | Apply single-phase fault on: NORTWST7 345KV 514880 TO SPRNGCK7 345.0 KV 514881 CKT 1, near NORTWST7 345kV for 6 cycles with stuck breaker at NORTWST7 345kV. Clear Fault after 16 cycles and trip: NORTWST7 345.0 KV 514880 TO ARCADIA 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWT_BNT4__G18_003_TAP | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NWT_BNT4__G18_003_TAP | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO G18-003-TAP 138.0 KV 762431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | NWT_BNT4__NWTXARK4 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NWT_BNT4__NWTXARK4 | 3 Phase fault on NWT-BNT4 (508070) 138 kV Bus a. Apply fault at the NWT-BNT4 (508070) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWT-BNT4 138.0 KV 508070 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NWTBNT4_138kV_508070 | Apply single-phase fault on: NWTBNT4 138KV 508070 TO BANN4 138KV 508054 CKT 1, near NWT-BNT4 138 kV for 7 cycles with stuck breaker at NWT-BNT4 138 kV. Clear Fault after 16 cycles and trip: NWTBNT4 138KV 508070 TO NWTXARK4 138KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTBNT4_138kV_508070 | Apply single-phase fault on: NWTBNT4 138KV 508070 TO BANN4 138KV 508054 CKT 1, near NWT-BNT4 138 kV for 7 cycles with stuck breaker at NWT-BNT4 138 kV. Clear Fault after 16 cycles and trip: NWTBNT4 138KV 508070 TO NWTXARK4 138KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK4__508072_0 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NWTXARK4__508072_0 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4( 508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 508071 TO NWTXARK7 508072 TO NWTEX2-1 508101 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | NWTXARK4__SUGARHL4 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NWTXARK4__SUGARHL4 | 3 Phase fault on NWTXARK4 (508071) 138 kV Bus a. Apply fault at the NWTXARK4 (508071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWTXARK4 138.0 KV 508071 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NWTXARK4_138kV_508071 | Apply single-phase fault on: NWTXARK4 138KV 508071 TO NASH4 138KV 508049 CKT 1, near NWTXARK4 138 kV for 7 cycles with stuck breaker at NWTXARK4 138 kV. Clear Fault after 16 cycles and trip: NWTBNT4 138KV 508070 TO NWTXARK4 138KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK4_138kV_508071 | Apply single-phase fault on: NWTXARK4 138KV 508071 TO NASH4 138KV 508049 CKT 1, near NWTXARK4 138 kV for 7 cycles with stuck breaker at NWTXARK4 138 kV. Clear Fault after 16 cycles and trip: NWTBNT4 138KV 508070 TO NWTXARK4 138KV 508071 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK7__LYDIA__7 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NWTXARK7__LYDIA__7 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO LYDIA 7 345.0 KV 508298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK7__VALIANT7 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NWTXARK7__VALIANT7 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | NWTXARK7__WELSH__7 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | NWTXARK7__WELSH__7 | 3 Phase fault on NWTXARK7 (508072) 345 kV Bus a. Apply fault at the NWTXARK7 (508072) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NWTXARK7 345.0 KV 508072 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OAKCRK_4__DRAPER_4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 b.2. LOAD 1 514984 b.3. WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | OAKCRK_4__DRAPER_4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 b.2. LOAD 1 514984 b.3. WILDMRY4 138.0 KV 514984 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.4. LOAD 1 515457 b.5. GM 4 138.0 KV 514961 TO AIRDEPT4 138.0 KV 515457 CKT 1 b.6. LOAD 1 515457 b.7. DRAPER 4 138.0 KV 514933 TO GM 4 138.0 KV 514961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OAKCRK_4__INDNHIL4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 4 138.0 KV 514955 TO OAKCRK 4 138.0 KV 514960 CKT 1 b.2. MOORE 4 138.0 KV 514955 TO INDIANH4 138.0 KV 515380 CKT 1 b.3. LOAD 1 515380 b.4. INDNHIL4 138.0 KV 514954 TO INDIANH4 138.0 KV 515380 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | OAKCRK_4__INDNHIL4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORE 4 138.0 KV 514955 TO OAKCRK 4 138.0 KV 514960 CKT 1 b.2. MOORE 4 138.0 KV 514955 TO INDIANH4 138.0 KV 515380 CKT 1 b.3. LOAD 1 515380 b.4. INDNHIL4 138.0 KV 514954 TO INDIANH4 138.0 KV 515380 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OAKCRK_4__PENN___4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANTAFE4 138.0 KV 514926 TO OAKCRK 4 138.0 KV 514960 CKT 1 b.2. PENN 4 138.0 KV 514925 TO SANTAFE4 138.0 KV 514926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | OAKCRK_4__PENN___4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANTAFE4 138.0 KV 514926 TO OAKCRK 4 138.0 KV 514960 CKT 1 b.2. PENN 4 138.0 KV 514925 TO SANTAFE4 138.0 KV 514926 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OAKCRK_4__SELNDTP4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138.0 KV 514960 TO SELNDTP4 138.0 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | OAKCRK_4__SELNDTP4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138.0 KV 514960 TO SELNDTP4 138.0 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OAKCRK_4__WILDMRY4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | OAKCRK_4__WILDMRY4 | 3 Phase fault on OAKCRK 4 (514960) 138 kV Bus a. Apply fault at the OAKCRK 4 (514960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKCRK 4 138.0 KV 514960 TO WILDMRY4 138.0 KV 514984 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OAKS__E4__OAKSETP4 | 3 Phase fault on OAKS--E4 (509846) 138 kV Bus a. Apply fault at the OAKS--E4 (509846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS--E4 138.0 KV 509846 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OAKS__E4__OAKSETP4 | 3 Phase fault on OAKS--E4 (509846) 138 kV Bus a. Apply fault at the OAKS--E4 (509846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS--E4 138.0 KV 509846 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OAKS__W4__OAKSWTP4 | 3 Phase fault on OAKS W4 (509727) 138 kV Bus a. Apply fault at the OAKS W4 (509727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS W4 138.0 KV 509727 TO OAKSWTP4 138.0 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OAKS__W4__OAKSWTP4 | 3 Phase fault on OAKS W4 (509727) 138 kV Bus a. Apply fault at the OAKS W4 (509727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKS W4 138.0 KV 509727 TO OAKSWTP4 138.0 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OAKSETP4__G18_027_TAP | 3 Phase fault on OAKSETP4 (509850) 138 kV Bus a. Apply fault at the OAKSETP4 (509850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSETP4 138.0 KV 509850 TO G18-027-TAP 138.0 KV 762629 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OAKSETP4__G18_027_TAP | 3 Phase fault on OAKSETP4 (509850) 138 kV Bus a. Apply fault at the OAKSETP4 (509850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSETP4 138.0 KV 509850 TO G18-027-TAP 138.0 KV 762629 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OAKSWTP4__SAPLPRD4 | 3 Phase fault on OAKSWTP4 (509848) 138 kV Bus a. Apply fault at the OAKSWTP4 (509848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138.0 KV 509848 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | OAKSWTP4__SAPLPRD4 | 3 Phase fault on OAKSWTP4 (509848) 138 kV Bus a. Apply fault at the OAKSWTP4 (509848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKSWTP4 138.0 KV 509848 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | OAKTRET4__SOONRTP4 | 3 Phase fault on OAKTRET4 (514930) 138 kV Bus a. Apply fault at the OAKTRET4 (514930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138.0 KV 514930 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | OAKTRET4__SOONRTP4 | 3 Phase fault on OAKTRET4 (514930) 138 kV Bus a. Apply fault at the OAKTRET4 (514930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAKTRET4 138.0 KV 514930 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OGMARTN2__DX____E2 | 3 Phase fault on OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGMARTN2 69.0 KV 509751 TO DX----E2 69.0 KV 509795 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OGMARTN2__DX____E2 | 3 Phase fault on OGMARTN2 (509751) 69 kV Bus a. Apply fault at the OGMARTN2 (509751) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OGMARTN2 69.0 KV 509751 TO DX----E2 69.0 KV 509795 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKAY___2__507428_0 | 3 Phase fault on OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2( 507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKAY___2__507428_0 | 3 Phase fault on OKAY 2 (507427) 69 kV Bus a. Apply fault at the OKAY 2( 507427) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 2 507427 TO OKAY 4 507428 TO OKAY1-1 507442 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKAY___4__TURK___4 | 3 Phase fault on OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138.0 KV 507428 TO TURK 4 138.0 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKAY___4__TURK___4 | 3 Phase fault on OKAY 4 (507428) 138 kV Bus a. Apply fault at the OKAY 4 (507428) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAY 4 138.0 KV 507428 TO TURK 4 138.0 KV 507454 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKEENE_2__TALOGA_2 | 3 Phase fault on OKEENE 2 (521015) 69 kV Bus a. Apply fault at the OKEENE 2 (521015) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 b.2. LOAD 1 521015 b.3. CANTON-2 69.0 KV 520843 TO TALOGA 2 69.0 KV 521064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKEENE_2__TALOGA_2 | 3 Phase fault on OKEENE 2 (521015) 69 kV Bus a. Apply fault at the OKEENE 2 (521015) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANTON-2 69.0 KV 520843 TO OKEENE 2 69.0 KV 521015 CKT 1 b.2. LOAD 1 521015 b.3. CANTON-2 69.0 KV 520843 TO TALOGA 2 69.0 KV 521064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKEENE_4__521015_0 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKEENE_4__521015_0 | 3 Phase fault on OKEENE 4 (521016) 138 kV Bus a. Apply fault at the OKEENE 4( 521016) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKEENE 4 521016 TO OKEENE 2 521015 TO OKENTERT 521173 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKEENE4_138kV_521016 | Apply single-phase fault on: OKEENE4 138KV 521016 TO WATNGSW4 138KV 520536 CKT 1, near OKEENE 4 138 kV for 7 cycles with stuck breaker at OKEENE 4 138 kV. Clear Fault after 16 cycles and trip: OKEENE4 138KV 521016 TO DOVERSW4 138KV 520882 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKEENE4_138kV_521016 | Apply single-phase fault on: OKEENE4 138KV 521016 TO WATNGSW4 138KV 520536 CKT 1, near OKEENE 4 138 kV for 7 cycles with stuck breaker at OKEENE 4 138 kV. Clear Fault after 16 cycles and trip: OKEENE4 138KV 521016 TO DOVERSW4 138KV 520882 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKMULGE4__EC_HEN_4 | 3 Phase fault on OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO EC.HEN-4 138.0 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKMULGE4__EC_HEN_4 | 3 Phase fault on OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO EC.HEN-4 138.0 KV 510923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKMULGE4__KELCO_4 | 3 Phase fault on OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKMULGE4__KELCO_4 | 3 Phase fault on OKMULGE4 (510898) 138 kV Bus a. Apply fault at the OKMULGE4 (510898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKMULGE4 138.0 KV 510898 TO KELCO 4 138.0 KV 510931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OKU7_345kV_511456 | Apply single-phase fault on: OKU7 345KV 511456 TO LES7 345.0 KV 511468 CKT 1, near OKU7 345kV for 6 cycles with stuck breaker at OKU7 345kV. Clear Fault after 16 cycles and trip: OKU7 345KV 511456 TO G18015TAP 345KV 762467 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OKU7_345kV_511456 | Apply single-phase fault on: OKU7 345KV 511456 TO LES7 345.0 KV 511468 CKT 1, near OKU7 345kV for 6 cycles with stuck breaker at OKU7 345kV. Clear Fault after 16 cycles and trip: OKU7 345KV 511456 TO G18015TAP 345KV 762467 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ONETA__4__121LYNN4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO 121LYNN4 138.0 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ONETA__4__121LYNN4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO 121LYNN4 138.0 KV 509869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ONETA__4__509807_0 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4( 509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ONETA__4__509807_0 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4( 509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 509806 TO ONETA--7 509807 TO ONETA1-1 509881 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ONETA__4__BA_71ST4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO BA_71ST4 138.0 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ONETA__4__BA_71ST4 | 3 Phase fault on ONETA--4 (509806) 138 kV Bus a. Apply fault at the ONETA--4 (509806) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONETA--4 138.0 KV 509806 TO BA_71ST4 138.0 KV 509891 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ONETA__7__N_E_S__7 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ONETA__7__N_E_S__7 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ONETA__7__OEC____7 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ONETA__7__OEC____7 | 3 Phase fault on ONETA--7 (509807) 345 kV Bus a. Apply fault at the ONETA--7 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 345.0 KV 509807 TO OEC 7 345.0 KV 509836 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ONETA7_345kV_509782 | Apply single-phase fault on: ONETA7 345.0 KV 509807 TO OEC7 345.0 KV 509836 CKT 1, near ONETA7 345kV for 6 cycles with stuck breaker at ONETA7 345kV. Clear Fault after 16 cycles and trip: RSS7 345.0 KV 509782 TO ONETA7 345.0 KV 509807 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ONETA7_345kV_509782 | Apply single-phase fault on: ONETA7 345.0 KV 509807 TO OEC7 345.0 KV 509836 CKT 1, near ONETA7 345kV for 6 cycles with stuck breaker at ONETA7 345kV. Clear Fault after 16 cycles and trip: RSS7 345.0 KV 509782 TO ONETA7 345.0 KV 509807 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ORU___E4__ORU_ETP4 | 3 Phase fault on ORU E4 (509738) 138 kV Bus a. Apply fault at the ORU E4 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138.0 KV 509738 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ORU___E4__ORU_ETP4 | 3 Phase fault on ORU E4 (509738) 138 kV Bus a. Apply fault at the ORU E4 (509738) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU E4 138.0 KV 509738 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ORU___W4__ORU_WTP4 | 3 Phase fault on ORU W4 (509732) 138 kV Bus a. Apply fault at the ORU W4 (509732) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138.0 KV 509732 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ORU___W4__ORU_WTP4 | 3 Phase fault on ORU W4 (509732) 138 kV Bus a. Apply fault at the ORU W4 (509732) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU W4 138.0 KV 509732 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ORU_ETP4__WARNTAP4 | 3 Phase fault on ORU ETP4 (509849) 138 kV Bus a. Apply fault at the ORU ETP4 (509849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138.0 KV 509849 TO WARNTAP4 138.0 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ORU_ETP4__WARNTAP4 | 3 Phase fault on ORU ETP4 (509849) 138 kV Bus a. Apply fault at the ORU ETP4 (509849) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORU ETP4 138.0 KV 509849 TO WARNTAP4 138.0 KV 509858 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OTTER__4__ARMFTWD4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OTTER__4__ARMFTWD4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO ARMFTWD4 138.0 KV 515694 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OTTER__4__WOODRNG4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OTTER__4__WOODRNG4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | OTTER__4__WRVALLY4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | OTTER__4__WRVALLY4 | 3 Phase fault on OTTER 4 (514708) 138 kV Bus a. Apply fault at the OTTER 4 (514708) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OTTER 4 138.0 KV 514708 TO WRVALLY4 138.0 KV 514713 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PARADSE4__CHERRYRD_4 | 3 Phase fault on PARADSE4 (521024) 138 kV Bus a. Apply fault at the PARADSE4 (521024) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PARADSE4__CHERRYRD_4 | 3 Phase fault on PARADSE4 (521024) 138 kV Bus a. Apply fault at the PARADSE4 (521024) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARADSE4 138.0 KV 521024 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS2__507431_0 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2( 507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS2__507431_0 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2( 507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 507429 TO PATTERS4 507431 TO PATTN2-1 507444 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS2__ASHDOWN2 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69.0 KV 507429 TO ASHDOWN2 69.0 KV 508051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS2__ASHDOWN2 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69.0 KV 507429 TO ASHDOWN2 69.0 KV 508051 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS2__NEKOOSA2 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69.0 KV 507429 TO NEKOOSA2 69.0 KV 508065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS2__NEKOOSA2 | 3 Phase fault on PATTERS2 (507429) 69 kV Bus a. Apply fault at the PATTERS2 (507429) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS2 69.0 KV 507429 TO NEKOOSA2 69.0 KV 508065 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS4__BARITERDTP_4 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138.0 KV 504123 TO PATTERS4 138.0 KV 507431 CKT 1 b.2. LOCKSBRG 4 138.0 KV 504123 TO BARITERDTP 4 138.0 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS4__BARITERDTP_4 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOCKSBRG 4 138.0 KV 504123 TO PATTERS4 138.0 KV 507431 CKT 1 b.2. LOCKSBRG 4 138.0 KV 504123 TO BARITERDTP 4 138.0 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS4__NWTXARK4 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS4__NWTXARK4 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO NWTXARK4 138.0 KV 508071 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS4__OKAY___4 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO PATTERS4 138.0 KV 507431 CKT 1 b.2. ASHDWNR4 138.0 KV 507402 TO OKAY 4 138.0 KV 507428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS4__OKAY___4 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWNR4 138.0 KV 507402 TO PATTERS4 138.0 KV 507431 CKT 1 b.2. ASHDWNR4 138.0 KV 507402 TO OKAY 4 138.0 KV 507428 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PATTERS4__SNASHVL4 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PATTERS4__SNASHVL4 | 3 Phase fault on PATTERS4 (507431) 138 kV Bus a. Apply fault at the PATTERS4 (507431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATTERS4 138.0 KV 507431 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | PECANCK4__515234_0 | 3 Phase fault on PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4( 515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 515233 TO PECANCK5 515234 TO PECANC31 515750 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PECANCK4__515234_0 | 3 Phase fault on PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4( 515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 515233 TO PECANCK5 515234 TO PECANC31 515750 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | PECANCK4__BRISTOW4 | 3 Phase fault on PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 138.0 KV 515233 TO BEGGS 4 138.0 KV 515249 CKT 1 b.2. LOAD 1 515249 b.3. BRISTOW4 138.0 KV 515035 TO BEGGS 4 138.0 KV 515249 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PECANCK4__BRISTOW4 | 3 Phase fault on PECANCK4 (515233) 138 kV Bus a. Apply fault at the PECANCK4 (515233) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK4 138.0 KV 515233 TO BEGGS 4 138.0 KV 515249 CKT 1 b.2. LOAD 1 515249 b.3. BRISTOW4 138.0 KV 515035 TO BEGGS 4 138.0 KV 515249 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PECANCK5__515235_0 | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5( 515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PECANCK5__515235_0 | 3 Phase fault on PECANCK5 (515234) 161 kV Bus a. Apply fault at the PECANCK5( 515234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECANCK5 515234 TO PECANCK7 515235 TO PECANC21 515759 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PECANCK5_161kV_515234 | Apply single-phase fault on: PECANCK4 161KV 515234 TO 5STRIBES5 161KV 515228 CKT 1, near PECANCK5 161 kV for 7 cycles with stuck breaker at PECANCK5 161 kV. Clear Fault after 16 cycles and trip: PECANCK4 161KV 515234 TO AGENCY5 161KV 515230 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PECANCK5_161kV_515234 | Apply single-phase fault on: PECANCK4 161KV 515234 TO 5STRIBES5 161KV 515228 CKT 1, near PECANCK5 161 kV for 7 cycles with stuck breaker at PECANCK5 161 kV. Clear Fault after 16 cycles and trip: PECANCK4 161KV 515234 TO AGENCY5 161KV 515230 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PECANCK7__GEN_2018_048 | 3 Phase fault on PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345.0 KV 515235 TO GEN-2018-048 345.0 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Lower acceleration to 0.2. Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PECANCK7__GEN_2018_048 | 3 Phase fault on PECANCK7 (515235) 345 kV Bus a. Apply fault at the PECANCK7 (515235) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECANCK7 345.0 KV 515235 TO GEN-2018-048 345.0 KV 762823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | PECANCK7_345kV_515235 | Apply single-phase fault on: MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2, near PECANCK7 345kV for 6 cycles with stuck breaker at PECANCK7 345kV. Clear Fault after 16 cycles and trip: RSS7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PECANCK7_345kV_515235 | Apply single-phase fault on: MUSKOGE7 345.0 KV 515224 TO PECANCK7 345.0 KV 515235 CKT 2, near PECANCK7 345kV for 6 cycles with stuck breaker at PECANCK7 345kV. Clear Fault after 16 cycles and trip: RSS7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PENN___2__514925_0 | 3 Phase fault on PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2( 514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 514924 TO PENN 4 514925 TO PENN 1 515751 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PENN___2__514925_0 | 3 Phase fault on PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2( 514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 514924 TO PENN 4 514925 TO PENN 1 515751 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PENN___2__KENTUKT2 | 3 Phase fault on PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 69.0 KV 514924 TO KENTUKT2 69.0 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PENN___2__KENTUKT2 | 3 Phase fault on PENN 2 (514924) 69 kV Bus a. Apply fault at the PENN 2 (514924) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 2 69.0 KV 514924 TO KENTUKT2 69.0 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PENN___4__36&MER_4 | 3 Phase fault on PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRAIRPT4 138.0 KV 514889 TO PENN 4 138.0 KV 514925 CKT 1 b.2. LOAD 1 514925 b.3. 36&MER 4 138.0 KV 514888 TO WRAIRPT4 138.0 KV 514889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PENN___4__36&MER_4 | 3 Phase fault on PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRAIRPT4 138.0 KV 514889 TO PENN 4 138.0 KV 514925 CKT 1 b.2. LOAD 1 514925 b.3. 36&MER 4 138.0 KV 514888 TO WRAIRPT4 138.0 KV 514889 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PENN___4__OAKCRK_4 | 3 Phase fault on PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 138.0 KV 514925 TO SANTAFE4 138.0 KV 514926 CKT 1 b.2. LOAD 1 514926 b.3. SANTAFE4 138.0 KV 514926 TO OAKCRK 4 138.0 KV 514960 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PENN___4__OAKCRK_4 | 3 Phase fault on PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PENN 4 138.0 KV 514925 TO SANTAFE4 138.0 KV 514926 CKT 1 b.2. LOAD 1 514926 b.3. SANTAFE4 138.0 KV 514926 TO OAKCRK 4 138.0 KV 514960 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PENN___4__SW134TP4 | 3 Phase fault on PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTMOR4 138.0 KV 514887 TO PENN 4 138.0 KV 514925 CKT 1 b.2. LOAD 1 514925 b.3. SW134TP4 138.0 KV 514876 TO WESTMOR4 138.0 KV 514887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PENN___4__SW134TP4 | 3 Phase fault on PENN 4 (514925) 138 kV Bus a. Apply fault at the PENN 4 (514925) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTMOR4 138.0 KV 514887 TO PENN 4 138.0 KV 514925 CKT 1 b.2. LOAD 1 514925 b.3. SW134TP4 138.0 KV 514876 TO WESTMOR4 138.0 KV 514887 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PENN4_138kV_514925 | Apply single-phase fault on: PENN4 138.0 KV 514925 TO SANTAFE4 138.0 KV 514926 CKT 1 and SANTAFE4 138.0 KV 514926 TO OAKCRK4 138.0 KV 514960 CKT 1, near PENN4 138kV for 7 cycles with stuck breaker at PENN4 138kV. Clear Fault after 16 cycles and trip: SW134TP4 138KV 514876 TO WESTMOR4 138.0 KV 514887 CKT 1 and WESTMOR4 138.0 KV 514887 TO PENN4 138.0 KV 514925 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PENN4_138kV_514925 | Apply single-phase fault on: PENN4 138.0 KV 514925 TO SANTAFE4 138.0 KV 514926 CKT 1 and SANTAFE4 138.0 KV 514926 TO OAKCRK4 138.0 KV 514960 CKT 1, near PENN4 138kV for 7 cycles with stuck breaker at PENN4 138kV. Clear Fault after 16 cycles and trip: SW134TP4 138KV 514876 TO WESTMOR4 138.0 KV 514887 CKT 1 and WESTMOR4 138.0 KV 514887 TO PENN4 138.0 KV 514925 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PERDUE_4__DIANA__4 | 3 Phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138.0 KV 508351 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PERDUE_4__DIANA__4 | 3 Phase fault on PERDUE 4 (508351) 138 kV Bus a. Apply fault at the PERDUE 4 (508351) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PERDUE 4 138.0 KV 508351 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PERSIMN7__GUTHRIE7 | 3 Phase fault on PERSIMN7 (515951) 345 kV Bus a. Apply fault at the PERSIMN7 (515951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PERSIMN7 345.0 KV 515951 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PERSIMN7__GUTHRIE7 | 3 Phase fault on PERSIMN7 (515951) 345 kV Bus a. Apply fault at the PERSIMN7 (515951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PERSIMN7 345.0 KV 515951 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PETTY__4__CHAPELH4 | 3 Phase fault on PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PETTY__4__CHAPELH4 | 3 Phase fault on PETTY 4 (508310) 138 kV Bus a. Apply fault at the PETTY 4 (508310) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PETTY 4 138.0 KV 508310 TO CHAPELH4 138.0 KV 508337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PINERTP2__WASHITA2 | 3 Phase fault on PINERTP2 (521027) 69 kV Bus a. Apply fault at the PINERTP2 (521027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69.0 KV 521027 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PINERTP2__WASHITA2 | 3 Phase fault on PINERTP2 (521027) 69 kV Bus a. Apply fault at the PINERTP2 (521027) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PINERTP2 69.0 KV 521027 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PINTAIL7_345kV_516010 | Apply single-phase fault on: SOONER7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1, near PINTAIL7 345kV for 6 cycles with stuck breaker at PINTAIL7 345kV. Clear Fault after 16 cycles and trip: WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PINTAIL7_345kV_516010 | Apply single-phase fault on: SOONER7 345.0 KV 514803 TO PINTAIL7 345.0 KV 516010 CKT 1, near PINTAIL7 345kV for 6 cycles with stuck breaker at PINTAIL7 345kV. Clear Fault after 16 cycles and trip: WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_4__508563_0 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_4__508563_0 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4( 508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 508562 TO PIRKEY 7 508563 TO PIRKY2-1 508588 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_4__BRANDYBR | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_4__BRANDYBR | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO EASTON 4 138.0 KV 509092 CKT 1 b.2. LOAD 1 509092 b.3. BRANDYBR 138.0 KV 508596 TO EASTON 4 138.0 KV 509092 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_4__SABMINT4 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_4__SABMINT4 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO SABMINT4 138.0 KV 508566 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_4__WHITNEY4 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_4__WHITNEY4 | 3 Phase fault on PIRKEY 4 (508562) 138 kV Bus a. Apply fault at the PIRKEY 4 (508562) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIRKEY 4 138.0 KV 508562 TO HALLSVLS4 138.0 KV 508595 CKT 1 b.2. LOAD 1 508595 b.3. WHITNEY4 138.0 KV 508575 TO HALLSVLS4 138.0 KV 508595 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_7__DIANA__7 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_7__DIANA__7 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PIRKEY_7__LEBROCK7 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PIRKEY_7__LEBROCK7 | 3 Phase fault on PIRKEY 7 (508563) 345 kV Bus a. Apply fault at the PIRKEY 7 (508563) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PIRKEY 7 345.0 KV 508563 TO LEBROCK7 345.0 KV 508572 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PITTSB_7__C_RIVER7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB_7__C_RIVER7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO C-RIVER7 345.0 KV 515422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB_7__JOHNCO_7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO JOHNCO 7 345.0 KV 514809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PITTSB_7__KIOWA__7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB_7__KIOWA__7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO KIOWA 7 345.0 KV 510925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PITTSB_7__SEMINOL7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB_7__SEMINOL7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | PITTSB_7__VALIANT7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PITTSB_7__VALIANT7 | 3 Phase fault on PITTSB-7 (510907) 345 kV Bus a. Apply fault at the PITTSB-7 (510907) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PITTSB-7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | PITTSB7_345kV_510907 | Apply single-phase fault on: PITTSB7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1, near PITTSB7 345kV for 6 cycles with stuck breaker at PITTSB7 345kV. Clear Fault after 16 cycles and trip: PITTSB7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | PITTSB7_345kV_510907 | Apply single-phase fault on: PITTSB7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1, near PITTSB7 345kV for 6 cycles with stuck breaker at PITTSB7 345kV. Clear Fault after 16 cycles and trip: PITTSB7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PLAVALLY4_138kV_514929 | Apply single-phase fault on: PLVALLY4 138.0 KV 514929 TO HOLLYWD4 138.0 KV 514953 CKT 1, near PLAVALLY4 138kV for 7 cycles with stuck breaker at PLAVALLY4 138kV. Clear Fault after 16 cycles and trip: PLVALLY4 138.0 KV 514929 TO CHERYCK4 138.0 KV 514957 CKT 1 and CHERYCK4 138.0 KV 514957 TO BOYD4 138.0 KV 514958 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PLAVALLY4_138kV_514929 | Apply single-phase fault on: PLVALLY4 138.0 KV 514929 TO HOLLYWD4 138.0 KV 514953 CKT 1, near PLAVALLY4 138kV for 7 cycles with stuck breaker at PLAVALLY4 138kV. Clear Fault after 16 cycles and trip: PLVALLY4 138.0 KV 514929 TO CHERYCK4 138.0 KV 514957 CKT 1 and CHERYCK4 138.0 KV 514957 TO BOYD4 138.0 KV 514958 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PLVALLY4__555234_0 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4( 514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 514929 TO NSUB345 555234 TO NEWBUS13.8 750001 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PLVALLY4__555234_0 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4( 514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 514929 TO NSUB345 555234 TO NEWBUS13.8 750001 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PLVALLY4__CHERYCK4 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 138.0 KV 514929 TO CHERYCK4 138.0 KV 514957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PLVALLY4__CHERYCK4 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 138.0 KV 514929 TO CHERYCK4 138.0 KV 514957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PLVALLY4__HOLLYWD4 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 138.0 KV 514929 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PLVALLY4__HOLLYWD4 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 138.0 KV 514929 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | PLVALLY4__TURNER_4 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 138.0 KV 514929 TO TURNER 4 138.0 KV 514992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | PLVALLY4__TURNER_4 | 3 Phase fault on PLVALLY4 (514929) 138 kV Bus a. Apply fault at the PLVALLY4 (514929) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLVALLY4 138.0 KV 514929 TO TURNER 4 138.0 KV 514992 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POOLVIL4__CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | POOLVIL4__CARTRCO4 | 3 Phase fault on POOLVIL4 (515130) 138 kV Bus a. Apply fault at the POOLVIL4 (515130) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POOLVIL4 138.0 KV 515130 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POTTER_CO__6__BUSHLAND___6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO BUSHLAND 6 230.0 KV 524267 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POTTER_CO__6__HARRNG_EST_6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO HARRNG_EST 6 230.0 KV 523979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POTTER_CO__6__NEWHART____6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POTTER_CO__6__ROLLHILLS__6 | 3 Phase fault on POTTER_CO 6 (523959) 230 kV Bus a. Apply fault at the POTTER_CO 6 (523959) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTTER_CO 6 230.0 KV 523959 TO ROLLHILLS 6 230.0 KV 524010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7( 523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POTTER_CO__7__523959_0 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7( 523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 523961 TO POTTER_CO 6 523959 TO POTTER_TR 1 523957 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POTTER_CO__7__SPNSPUR_WND7 | 3 Phase fault on POTTER_CO 7 (523961) 345 kV Bus a. Apply fault at the POTTER_CO 7 (523961) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POTTER_CO 7 345.0 KV 523961 TO SPNSPUR_WND7 345.0 KV 524296 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | POWELL_4__SW_SHV_4 | 3 Phase fault on POWELL 4 (507748) 138 kV Bus a. Apply fault at the POWELL 4 (507748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138.0 KV 507748 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | POWELL_4__SW_SHV_4 | 3 Phase fault on POWELL 4 (507748) 138 kV Bus a. Apply fault at the POWELL 4 (507748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POWELL 4 138.0 KV 507748 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | QUAILCK4__NORTWST4 | 3 Phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO LNEOAK 4 138.0 KV 514873 CKT 1 b.2. LOAD 1 514873 b.3. LNEOAK 4 138.0 KV 514873 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | QUAILCK4__NORTWST4 | 3 Phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO LNEOAK 4 138.0 KV 514873 CKT 1 b.2. LOAD 1 514873 b.3. LNEOAK 4 138.0 KV 514873 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | QUAILCK4__SLVRLAK4 | 3 Phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO SLVRLAK4 138.0 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | QUAILCK4__SLVRLAK4 | 3 Phase fault on QUAILCK4 (514851) 138 kV Bus a. Apply fault at the QUAILCK4 (514851) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAILCK4 138.0 KV 514851 TO SLVRLAK4 138.0 KV 514852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__511844_0 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4( 509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__511844_0 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4( 509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 509783 TO RSS NG3 511844 TO RSS NG4 511845 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__52DELWT4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__52DELWT4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__B111___4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138.0 KV 509775 TO R.S.S.-4 138.0 KV 509783 CKT 1 b.2. 136YALE4 138.0 KV 509775 TO KIMCLRK4 138.0 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138.0 KV 509767 TO KIMCLRK4 138.0 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__B111___4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138.0 KV 509775 TO R.S.S.-4 138.0 KV 509783 CKT 1 b.2. 136YALE4 138.0 KV 509775 TO KIMCLRK4 138.0 KV 509845 CKT 1 b.3. LOAD 1 509845 b.4. B111---4 138.0 KV 509767 TO KIMCLRK4 138.0 KV 509845 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__EXP_OKM4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__EXP_OKM4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__EXPGLNT4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__EXPGLNT4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__OAKSETP4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__OAKSETP4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO OAKSETP4 138.0 KV 509850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__OKMULGE4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__OKMULGE4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO EXP_OKM4 138.0 KV 510904 CKT 1 b.2. LOAD 1 510904 b.3. OKMULGE4 138.0 KV 510898 TO EXP_OKM4 138.0 KV 510904 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__ORU_ETP4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__ORU_ETP4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU ETP4 138.0 KV 509849 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__ORU_WTP4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__ORU_WTP4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__RSS_T2_4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS T2 4 138.0 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__RSS_T2_4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. R.S.S.-4 138.0 KV 509783 TO RSS T2 4 138.0 KV 509875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__4__SAPLPRD4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 116JENK4 138.0 KV 509753 TO R.S.S.-4 138.0 KV 509783 CKT 1 b.2. 116JENK4 138.0 KV 509753 TO JENKS--4 138.0 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. JENKS--4 138.0 KV 509759 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__4__SAPLPRD4 | 3 Phase fault on R.S.S.-4 (509783) 138 kV Bus a. Apply fault at the R.S.S.-4 (509783) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 116JENK4 138.0 KV 509753 TO R.S.S.-4 138.0 KV 509783 CKT 1 b.2. 116JENK4 138.0 KV 509753 TO JENKS--4 138.0 KV 509759 CKT 1 b.3. LOAD 1 509759 b.4. JENKS--4 138.0 KV 509759 TO SAPLPRD4 138.0 KV 509871 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__7__COGENT_7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO COGENT 7 345.0 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__7__COGENT_7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO COGENT 7 345.0 KV 509834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__7__G16133G16146 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO G16133G16146 345.0 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__7__G16133G16146 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO G16133G16146 345.0 KV 588039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | R_S_S__7__ONETA__7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__7__ONETA__7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__7__PECANCK7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__7__PECANCK7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO PECANCK7 345.0 KV 515235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__7__REDBUD_7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__7__REDBUD_7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO REDBUD 7 345.0 KV 514909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | R_S_S__7__SAPLPRD7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | R_S_S__7__SAPLPRD7 | 3 Phase fault on R.S.S.-7 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 345.0 KV 509782 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RATLIFF4__CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | RATLIFF4__CARTRCO4 | 3 Phase fault on RATLIFF4 (515129) 138 kV Bus a. Apply fault at the RATLIFF4 (515129) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RATLIFF4 138.0 KV 515129 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25S | Transfer | REDBAYOU_6__DOLHILL6 | 3 Phase fault on REDBAYOU_6 (500255) 230 kV Bus a. Apply fault at the REDBAYOU_6 (500255) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBAYOU_6 230.0 KV 500255 TO DOLHILL6 230.0 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDBAYOU_6__DOLHILL6 | 3 Phase fault on REDBAYOU_6 (500255) 230 kV Bus a. Apply fault at the REDBAYOU_6 (500255) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBAYOU_6 230.0 KV 500255 TO DOLHILL6 230.0 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDBUD1S__514909_0 | 3 Phase fault on REDBUD1S (514899) 18 kV Bus a. Apply fault at the REDBUD1S( 514899) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDBUD1S__514909_0 | 3 Phase fault on REDBUD1S (514899) 18 kV Bus a. Apply fault at the REDBUD1S( 514899) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD1S 514899 TO REDBUD 7 514909 TO REDBUD1G 514910 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDBUD2S__514909_0 | 3 Phase fault on REDBUD2S (514900) 18 kV Bus a. Apply fault at the REDBUD2S( 514900) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD2S 514900 TO REDBUD 7 514909 TO REDBUD2G 514911 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDBUD2S__514909_0 | 3 Phase fault on REDBUD2S (514900) 18 kV Bus a. Apply fault at the REDBUD2S( 514900) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD2S 514900 TO REDBUD 7 514909 TO REDBUD2G 514911 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDBUD3S__514909_0 | 3 Phase fault on REDBUD3S (514905) 18 kV Bus a. Apply fault at the REDBUD3S( 514905) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDBUD3S__514909_0 | 3 Phase fault on REDBUD3S (514905) 18 kV Bus a. Apply fault at the REDBUD3S( 514905) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD3S 514905 TO REDBUD 7 514909 TO REDBUD3G 514912 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDBUD4S__514909_0 | 3 Phase fault on REDBUD4S (514940) 18 kV Bus a. Apply fault at the REDBUD4S( 514940) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDBUD4S__514909_0 | 3 Phase fault on REDBUD4S (514940) 18 kV Bus a. Apply fault at the REDBUD4S( 514940) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDBUD4S 514940 TO REDBUD 7 514909 TO REDBUD4G 514942 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDNGTN7_345kV_515875 | Apply single-phase fault on: MATHWSN7 345KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1, near REDNGTN7 345kV for 6 cycles with stuck breaker at REDNGTN7 345kV. Clear Fault after 16 cycles and trip: WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDNGTN7_345kV_515875 | Apply single-phase fault on: MATHWSN7 345KV 515497 TO REDNGTN7 345.0 KV 515875 CKT 1, near REDNGTN7 345kV for 6 cycles with stuck breaker at REDNGTN7 345kV. Clear Fault after 16 cycles and trip: WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDROCKRD4_138kV_511548 | Apply single-phase fault on: CANGAS4 138KV 511540 TO REDROCKRD4 138KV 511548 CKT 1, near REDROCKRD4 138kV for 7 cycles with stuck breaker at REDROCKRD4 138kV. Clear Fault after 16 cycles and trip: REDROCKRD4 138KV 511548 TO DARLINGTNRD4 138KV 511559 CKT 1 and DARLINGTNRD4 138KV 511559 TO MAPLERD4 138KV 511581 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDROCKRD4_138kV_511548 | Apply single-phase fault on: CANGAS4 138KV 511540 TO REDROCKRD4 138KV 511548 CKT 1, near REDROCKRD4 138kV for 7 cycles with stuck breaker at REDROCKRD4 138kV. Clear Fault after 16 cycles and trip: REDROCKRD4 138KV 511548 TO DARLINGTNRD4 138KV 511559 CKT 1 and DARLINGTNRD4 138KV 511559 TO MAPLERD4 138KV 511581 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDSPRG4__EYLAU__4 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138.0 KV 508075 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDSPRG4__EYLAU__4 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDSPRG4 138.0 KV 508075 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | REDSPRG4__IPC_T__4 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC-DOM4 138.0 KV 508060 TO REDSPRG4 138.0 KV 508075 CKT 1 b.2. LOAD 1 508075 b.3. IPC T 4 138.0 KV 508059 TO IPC-DOM4 138.0 KV 508060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDSPRG4__IPC_T__4 | 3 Phase fault on REDSPRG4 (508075) 138 kV Bus a. Apply fault at the REDSPRG4 (508075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IPC-DOM4 138.0 KV 508060 TO REDSPRG4 138.0 KV 508075 CKT 1 b.2. LOAD 1 508075 b.3. IPC T 4 138.0 KV 508059 TO IPC-DOM4 138.0 KV 508060 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | REDWATR4__EYLAU__4 | 3 Phase fault on REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138.0 KV 509654 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REDWATR4__EYLAU__4 | 3 Phase fault on REDWATR4 (509654) 138 kV Bus a. Apply fault at the REDWATR4 (509654) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REDWATR4 138.0 KV 509654 TO EYLAU 4 138.0 KV 509655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | REMPKTP4__REMNGPK4 | 3 Phase fault on REMPKTP4 (514872) 138 kV Bus a. Apply fault at the REMPKTP4 (514872) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMPKTP4 138.0 KV 514872 TO REMNGPK4 138.0 KV 514874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | REMPKTP4__REMNGPK4 | 3 Phase fault on REMPKTP4 (514872) 138 kV Bus a. Apply fault at the REMPKTP4 (514872) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REMPKTP4 138.0 KV 514872 TO REMNGPK4 138.0 KV 514874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENFROW7_345kV_515543 | Apply single-phase fault on: RENFROW7 345KV 515543 TO VIOLA7 345.0 KV 532798 CKT 1, near RENFROW7 345kV for 6 cycles with stuck breaker at RENFROW7 345kV. Clear Fault after 16 cycles and trip: HUNTERS7 345KV 515476 TO RENFROW7 345KV 515543 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENFROW7_345kV_515543 | Apply single-phase fault on: RENFROW7 345KV 515543 TO VIOLA7 345.0 KV 532798 CKT 1, near RENFROW7 345kV for 6 cycles with stuck breaker at RENFROW7 345kV. Clear Fault after 16 cycles and trip: HUNTERS7 345KV 515476 TO RENFROW7 345KV 515543 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENO___2__514973_0 | 3 Phase fault on RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2( 514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENO___2__514973_0 | 3 Phase fault on RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2( 514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 514972 TO RENO 4 514973 TO RENO 1 515753 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENO___2__SUNNYLN2 | 3 Phase fault on RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 69.0 KV 514972 TO SUNNYLN2 69.0 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENO___2__SUNNYLN2 | 3 Phase fault on RENO 2 (514972) 69 kV Bus a. Apply fault at the RENO 2 (514972) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 2 69.0 KV 514972 TO SUNNYLN2 69.0 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENO___4__STNWAL_4 | 3 Phase fault on RENO 4 (514973) 138 kV Bus a. Apply fault at the RENO 4 (514973) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138.0 KV 514973 TO WASHPRK4 138.0 KV 515156 CKT 1 b.2. LOAD 1 515156 b.3. WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. OUMED 4 138.0 KV 514875 TO GATEWAY4 138.0 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. STNWAL 4 138.0 KV 514870 TO OUMED 4 138.0 KV 514875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | RENO___4__STNWAL_4 | 3 Phase fault on RENO 4 (514973) 138 kV Bus a. Apply fault at the RENO 4 (514973) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 4 138.0 KV 514973 TO WASHPRK4 138.0 KV 515156 CKT 1 b.2. LOAD 1 515156 b.3. WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. OUMED 4 138.0 KV 514875 TO GATEWAY4 138.0 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. STNWAL 4 138.0 KV 514870 TO OUMED 4 138.0 KV 514875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RENO4_138kV_514973 | Apply single-phase fault on: RENO4 138KV 514973 TO DUNJEE4 138KV 514884 CKT 1, near RENO 4 138 kV for 7 cycles with stuck breaker at RENO 4 138 kV. Clear Fault after 16 cycles and trip: RENO4 138KV 514973 TO WASHPRK4 138KV 515156 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RENO4_138kV_514973 | Apply single-phase fault on: RENO4 138KV 514973 TO DUNJEE4 138KV 514884 CKT 1, near RENO 4 138 kV for 7 cycles with stuck breaker at RENO 4 138 kV. Clear Fault after 16 cycles and trip: RENO4 138KV 514973 TO WASHPRK4 138KV 515156 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROCKYPT2__515164_0 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ROCKYPT2__515164_0 | 3 Phase fault on ROCKYPT2 (515163) 69 kV Bus a. Apply fault at the ROCKYPT2( 515163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT2 515163 TO ROCKYPT4 515164 TO ROCKYPT1 515754 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROCKYPT4__SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROCKYPT4__SPRNDAL4 | 3 Phase fault on ROCKYPT4 (515164) 138 kV Bus a. Apply fault at the ROCKYPT4 (515164) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROCKYPT4 138.0 KV 515164 TO SPRNDAL4 138.0 KV 515172 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROKHILL2__509083_0 | 3 Phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply fault at the ROKHILL2( 509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROKHILL2__509083_0 | 3 Phase fault on ROKHILL2 (509082) 69 kV Bus a. Apply fault at the ROKHILL2( 509082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL2 509082 TO ROKHILL4 509083 TO RKHIL2-1 509091 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROKHILL4__NEWPROS4 | 3 Phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO NEWPROS4 138.0 KV 509102 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROKHILL4__NEWPROS4 | 3 Phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO NEWPROS4 138.0 KV 509102 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROKHILL4__TATUM__4 | 3 Phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO TATUM 4 138.0 KV 509087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROKHILL4__TATUM__4 | 3 Phase fault on ROKHILL4 (509083) 138 kV Bus a. Apply fault at the ROKHILL4 (509083) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROKHILL4 138.0 KV 509083 TO TATUM 4 138.0 KV 509087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ROMNOSE4__GEARYTP4 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ROMNOSE4__GEARYTP4 | 3 Phase fault on ROMNOSE4 (514823) 138 kV Bus a. Apply fault at the ROMNOSE4 (514823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROMNOSE4 138.0 KV 514823 TO GEARYTP4 138.0 KV 515931 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RSHSPR1_COL1__511979_0 | 3 Phase fault on RSHSPR1_COL1 (511978) 34.5 kV Bus a. Apply fault at the RSHSPR1_COL1( 511978) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RSHSPR1_COL1__511979_0 | 3 Phase fault on RSHSPR1_COL1 (511978) 34.5 kV Bus a. Apply fault at the RSHSPR1_COL1( 511978) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RSS_T1_4__509782_0 | 3 Phase fault on RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4( 509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RSS_T1_4__509782_0 | 3 Phase fault on RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4( 509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 509773 TO R.S.S.-7 509782 TO RSST1 T1 509882 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RSS_T1_4__R_S_S__4 | 3 Phase fault on RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138.0 KV 509773 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RSS_T1_4__R_S_S__4 | 3 Phase fault on RSS T1 4 (509773) 138 kV Bus a. Apply fault at the RSS T1 4 (509773) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T1 4 138.0 KV 509773 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RSS_T2_4__509782_0 | 3 Phase fault on RSS T2 4 (509875) 138 kV Bus a. Apply fault at the RSS T2 4( 509875) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RSS_T2_4__509782_0 | 3 Phase fault on RSS T2 4 (509875) 138 kV Bus a. Apply fault at the RSS T2 4( 509875) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSS T2 4 509875 TO R.S.S.-7 509782 TO RSST2 T1 509876 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | RSS4_138kV_509783 | Apply single-phase fault on: RSS4 138KV 509783 TO ORUETP4 138KV 509849 CKT 1, near R.S.S.-4 138 kV for 7 cycles with stuck breaker at R.S.S.-4 138 kV. Clear Fault after 16 cycles and trip: RSS4 138KV 509783 TO RSST24 138KV 509875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RSS4_138kV_509783 | Apply single-phase fault on: RSS4 138KV 509783 TO ORUETP4 138KV 509849 CKT 1, near R.S.S.-4 138 kV for 7 cycles with stuck breaker at R.S.S.-4 138 kV. Clear Fault after 16 cycles and trip: RSS4 138KV 509783 TO RSST24 138KV 509875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RSS7_345kV_509782 | Apply single-phase fault on: RSS7 345KV 509782 TO ONETA7 345KV 509807 CKT 1, near R.S.S.-7 345 kV for 6 cycles with stuck breaker at R.S.S.-7 345 kV. Clear Fault after 16 cycles and trip: RSS7 345KV 509782 TO SALPRD7 345KV 509870 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RSS7_345kV_509782 | Apply single-phase fault on: RSS7 345KV 509782 TO ONETA7 345KV 509807 CKT 1, near R.S.S.-7 345 kV for 6 cycles with stuck breaker at R.S.S.-7 345 kV. Clear Fault after 16 cycles and trip: RSS7 345KV 509782 TO SALPRD7 345KV 509870 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RUSHING2__515064_0 | 3 Phase fault on RUSHING2 (515063) 69 kV Bus a. Apply fault at the RUSHING2( 515063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHING2 515063 TO RUSHING4 515064 TO RUSHING1 515755 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSHING2__515064_0 | 3 Phase fault on RUSHING2 (515063) 69 kV Bus a. Apply fault at the RUSHING2( 515063) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSHING2 515063 TO RUSHING4 515064 TO RUSHING1 515755 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 (584862) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2015-045 (584862), Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 (584862) trips on Voltage Protection | Disable Voltage Protection for GEN-2015-045 (584862)
04 - Southeast | 25S | Transfer | RUSHSPR7__GEN_2015_092 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | RUSHSPR7__GEN_2015_092 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 (584862) trips on Voltage Protection | Disable Voltage Protection for GEN-2015-045 (584862)
04 - Southeast | 25S | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 (584862) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2015-045 (584862). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 (584862) trips on Voltage Protection | Disable Voltage Protection for GEN-2015-045 (584862)
04 - Southeast | 25S | Transfer | RUSSET4_138kV_515120 | Apply single-phase fault on: RUSSET4 138KV 515120 TO RUSSETT4 138KV 521044 CKT 1, near RUSSET4 138kV for 7 cycles with stuck breaker at RUSSET4 138kV. Clear Fault after 16 cycles and trip: JOHNCO4 138KV 514808 TO RUSSET4 138KV 515120 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | RUSSET4_138kV_515120 | Apply single-phase fault on: RUSSET4 138KV 515120 TO RUSSETT4 138KV 521044 CKT 1, near RUSSET4 138kV for 7 cycles with stuck breaker at RUSSET4 138kV. Clear Fault after 16 cycles and trip: JOHNCO4 138KV 514808 TO RUSSET4 138KV 515120 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | RVRFANT2__MUSKOGE2 | 3 Phase fault on RVRFANT2 (515210) 69 kV Bus a. Apply fault at the RVRFANT2 (515210) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRFANT2 69.0 KV 515210 TO MUSKOGE2 69.0 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. | Lower acceleration to 0.2.
04 - Southeast | 25W | Transfer | RVRFANT2__MUSKOGE2 | 3 Phase fault on RVRFANT2 (515210) 69 kV Bus a. Apply fault at the RVRFANT2 (515210) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRFANT2 69.0 KV 515210 TO MUSKOGE2 69.0 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | RVRSID_2__MUSKOGE2 | 3 Phase fault on RVRSID 2 (515205) 69 kV Bus a. Apply fault at the RVRSID 2 (515205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRSID 2 69.0 KV 515205 TO MUSKOGE2 69.0 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | RVRSID_2__MUSKOGE2 | 3 Phase fault on RVRSID 2 (515205) 69 kV Bus a. Apply fault at the RVRSID 2 (515205) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RVRSID 2 69.0 KV 515205 TO MUSKOGE2 69.0 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_HIL_E4__SHILETP4 | 3 Phase fault on S.HIL E4 (509731) 138 kV Bus a. Apply fault at the S.HIL E4 (509731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138.0 KV 509731 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_HIL_E4__SHILETP4 | 3 Phase fault on S.HIL E4 (509731) 138 kV Bus a. Apply fault at the S.HIL E4 (509731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.HIL E4 138.0 KV 509731 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_S____2__509815_0 | 3 Phase fault on S.S.---2 (509816) 69 kV Bus a. Apply fault at the S.S.---2( 509816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_S____2__509815_0 | 3 Phase fault on S.S.---2 (509816) 69 kV Bus a. Apply fault at the S.S.---2( 509816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---2 509816 TO S.S.---4 509815 TO SS6-1 509878 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_S____4__BLUEBEL4 | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138.0 KV 509758 TO S.S.---4 138.0 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138.0 KV 509758 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_S____4__BLUEBEL4 | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRATTV-4 138.0 KV 509758 TO S.S.---4 138.0 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. PRATTV-4 138.0 KV 509758 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_S____4__DENV_WTAP4 | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_S____4__DENV_WTAP4 | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_S____4__HWY20_T4 | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_S____4__HWY20_T4 | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_S____4__WED_TAP4 | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_S____4__WED_TAP4 | 3 Phase fault on S.S.---4 (509815) 138 kV Bus a. Apply fault at the S.S.---4 (509815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.S.---4 138.0 KV 509815 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_SHV__2__507755_0 | 3 Phase fault on S SHV 2 (507754) 69 kV Bus a. Apply fault at the S SHV 2( 507754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_SHV__2__507755_0 | 3 Phase fault on S SHV 2 (507754) 69 kV Bus a. Apply fault at the S SHV 2( 507754) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 2 507754 TO S SHV 4 507755 TO SSHV2-1 507776 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_SHV__4__CEDARGR4 | 3 Phase fault on S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_SHV__4__CEDARGR4 | 3 Phase fault on S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO CEDARGR4 138.0 KV 507771 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_SHV__4__SW_SHV_4 | 3 Phase fault on S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_SHV__4__SW_SHV_4 | 3 Phase fault on S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_SHV__4__WALLAKE4 | 3 Phase fault on S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WALLAKE4 138.0 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_SHV__4__WALLAKE4 | 3 Phase fault on S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WALLAKE4 138.0 KV 507765 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_SHV__4__WESTELC4 | 3 Phase fault on S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WESTELC4 138.0 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_SHV__4__WESTELC4 | 3 Phase fault on S SHV 4 (507755) 138 kV Bus a. Apply fault at the S SHV 4 (507755) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S SHV 4 138.0 KV 507755 TO WESTELC4 138.0 KV 507767 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_W_S__2__511477_0 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S_W_S__2__511477_0 | 3 Phase fault on S.W.S.-2 (511476) 69 kV Bus a. Apply fault at the S.W.S.-2( 511476) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-2 511476 TO S.W.S.-4 511477 TO SWS#1--1 511413 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | S_W_S__4__511849_0 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | S_W_S__4__511849_0 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4( 511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 511477 TO SWS NG4 511849 TO SWS NG5 511850 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | S_W_S__4__ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | S_W_S__4__ANADARK4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | S_W_S__4__ELSWORTH___4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | S_W_S__4__ELSWORTH___4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | S_W_S__4__G16_097_TAP | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | S_W_S__4__G16_097_TAP | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | S_W_S__4__NORGE__4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | S_W_S__4__NORGE__4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO NORGE--4 138.0 KV 511483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | S_W_S__4__WASHITA4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | S_W_S__4__WASHITA4 | 3 Phase fault on S.W.S.-4 (511477) 138 kV Bus a. Apply fault at the S.W.S.-4 (511477) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S.W.S.-4 138.0 KV 511477 TO WASHITA4 138.0 KV 521089 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | S52DEL_4__52DELTP4 | 3 Phase fault on S52DEL 4 (509716) 138 kV Bus a. Apply fault at the S52DEL 4 (509716) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S52DEL 4 138.0 KV 509716 TO 52DELTP4 138.0 KV 509776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | S52DEL_4__52DELTP4 | 3 Phase fault on S52DEL 4 (509716) 138 kV Bus a. Apply fault at the S52DEL 4 (509716) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S52DEL 4 138.0 KV 509716 TO 52DELTP4 138.0 KV 509776 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SABMINT4__SABINEM4 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SABMINT4__SABINEM4 | 3 Phase fault on SABMINT4 (508566) 138 kV Bus a. Apply fault at the SABMINT4 (508566) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SABMINT4 138.0 KV 508566 TO SABINEM4 138.0 KV 508577 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SAPLPRD4__509870_0 | 3 Phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4( 509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SAPLPRD4__509870_0 | 3 Phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4( 509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 509871 TO SAPLPRD7 509870 TO SAPLPRD1 509872 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SAPLPRD4__72ELWOD4 | 3 Phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO 72ELWOD4 138.0 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SAPLPRD4__72ELWOD4 | 3 Phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO 72ELWOD4 138.0 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SAPLPRD4__DENV_WTAP4 | 3 Phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SAPLPRD4__DENV_WTAP4 | 3 Phase fault on SAPLPRD4 (509871) 138 kV Bus a. Apply fault at the SAPLPRD4 (509871) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAPLPRD4 138.0 KV 509871 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SARA___4__CIMARON4 | 3 Phase fault on SARA 4 (514895) 138 kV Bus a. Apply fault at the SARA 4 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138.0 KV 514895 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SARA___4__CIMARON4 | 3 Phase fault on SARA 4 (514895) 138 kV Bus a. Apply fault at the SARA 4 (514895) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138.0 KV 514895 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SBROWN4_138kV_505602 | Apply single-phase fault on: SBROWN4 138KV 505602 TO RUSSET4 138.0 KV 521044 CKT 1, near SBROWN4 138kV for 7 cycles with stuck breaker at SBROWN4 138kV. Clear Fault after 16 cycles and trip: SBROWN4 138KV 505602 TO COLBRTP4 138.0 KV 515159 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SBROWN4_138kV_505602 | Apply single-phase fault on: SBROWN4 138KV 505602 TO RUSSET4 138.0 KV 521044 CKT 1, near SBROWN4 138kV for 7 cycles with stuck breaker at SBROWN4 138kV. Clear Fault after 16 cycles and trip: SBROWN4 138KV 505602 TO COLBRTP4 138.0 KV 515159 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SCOTTSW4_138kV_520899 | Apply single-phase fault on: ELRENO4 138KV 520893 TO SCOTTSW4 138KV 520899 CKT 1, near SCOTTSW4 138kV for 7 cycles with stuck breaker at SCOTTSW4 138kV. Clear Fault after 16 cycles and trip: CANA4 138KV 520502 TO SCOTTSW4 138KV 520899 CKT 1 and CANA4 138KV 520502 TO CALUMET4 138KV 520839 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SCOTTSW4_138kV_520899 | Apply single-phase fault on: ELRENO4 138KV 520893 TO SCOTTSW4 138KV 520899 CKT 1, near SCOTTSW4 138kV for 7 cycles with stuck breaker at SCOTTSW4 138kV. Clear Fault after 16 cycles and trip: CANA4 138KV 520502 TO SCOTTSW4 138KV 520899 CKT 1 and CANA4 138KV 520502 TO CALUMET4 138KV 520839 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SDIERKS4__BARITERDTP_4 | 3 Phase fault on SDIERKS4 (507433) 138 kV Bus a. Apply fault at the SDIERKS4 (507433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS4 138.0 KV 507433 TO BARITERDTP 4 138.0 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SDIERKS4__BARITERDTP_4 | 3 Phase fault on SDIERKS4 (507433) 138 kV Bus a. Apply fault at the SDIERKS4 (507433) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SDIERKS4 138.0 KV 507433 TO BARITERDTP 4 138.0 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SE15TH_4__BARNES_4 | 3 Phase fault on SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138.0 KV 514993 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SE15TH_4__BARNES_4 | 3 Phase fault on SE15TH 4 (514993) 138 kV Bus a. Apply fault at the SE15TH 4 (514993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE15TH 4 138.0 KV 514993 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEILING4__MOORLND4 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SEILING4__MOORLND4 | 3 Phase fault on SEILING4 (520553) 138 kV Bus a. Apply fault at the SEILING4 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 138.0 KV 520553 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SELNDTP4__SELNDFL4 | 3 Phase fault on SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SELNDTP4 138.0 KV 515965 TO SELNDFL4 138.0 KV 515966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SELNDTP4__SELNDFL4 | 3 Phase fault on SELNDTP4 (515965) 138 kV Bus a. Apply fault at the SELNDTP4 (515965) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SELNDTP4 138.0 KV 515965 TO SELNDFL4 138.0 KV 515966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEMINOL4__515045_0 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SEMINOL4__515045_0 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4( 515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 515044 TO SEMINOL7 515045 TO SEMINO21 515757 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEMINOL4__LKKONWA4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SEMINOL4__LKKONWA4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO LKKONWA4 138.0 KV 515977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEMINOL4__MAUD___4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SEMINOL4__MAUD___4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO MAUD 4 138.0 KV 515055 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEMINOL4__PAOLI__4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SEMINOL4__PAOLI__4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO PAOLI- 4 138.0 KV 515100 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEMINOL4__VANOSTP4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SEMINOL4__VANOSTP4 | 3 Phase fault on SEMINOL4 (515044) 138 kV Bus a. Apply fault at the SEMINOL4 (515044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEMINOL4 138.0 KV 515044 TO VANOSTP4 138.0 KV 515531 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEMINOL7__MUSKOGE7 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SEMINOL7__MUSKOGE7 | 3 Phase fault on SEMINOL7 (515045) 345 kV Bus a. Apply fault at the SEMINOL7 (515045) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SEMINOL7 345.0 KV 515045 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEMINOL7_345kV_515045 | Apply single-phase fault on: ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1, near SEMINOL7 345kV for 6 cycles with stuck breaker at SEMINOL7 345kV. Clear Fault after 16 cycles and trip: PITTSB7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SEMINOL7_345kV_515045 | Apply single-phase fault on: ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1, near SEMINOL7 345kV for 6 cycles with stuck breaker at SEMINOL7 345kV. Clear Fault after 16 cycles and trip: PITTSB7 345.0 KV 510907 TO SEMINOL7 345.0 KV 515045 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | SEQUOYAHJ4__ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SEQUOYAHJ4__ANADARK4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEQUOYAHJ4__CKSHATP4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SEQUOYAHJ4__CKSHATP4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO CKSHATP4 138.0 KV 520473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SEQUOYAHJ4__SEQOYAH4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SEQUOYAHJ4__SEQOYAH4 | 3 Phase fault on SEQUOYAHJ4 (520422) 138 kV Bus a. Apply fault at the SEQUOYAHJ4 (520422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEQUOYAHJ4 138.0 KV 520422 TO SEQOYAH4 138.0 KV 520547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SETEXAR2__508078_0 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2( 508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SETEXAR2__508078_0 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2( 508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 508077 TO SETEXAR4 508078 TO SETEX1-1 508102 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SETEXAR2__TEXARK_2 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 69.0 KV 508077 TO TEXARK 2 69.0 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SETEXAR2__TEXARK_2 | 3 Phase fault on SETEXAR2 (508077) 69 kV Bus a. Apply fault at the SETEXAR2 (508077) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR2 69.0 KV 508077 TO TEXARK 2 69.0 KV 508086 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SETEXAR4__MANDEVILTP4 | 3 Phase fault on SETEXAR4 (508078) 138 kV Bus a. Apply fault at the SETEXAR4 (508078) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR4 138.0 KV 508078 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SETEXAR4__MANDEVILTP4 | 3 Phase fault on SETEXAR4 (508078) 138 kV Bus a. Apply fault at the SETEXAR4 (508078) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETEXAR4 138.0 KV 508078 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SFOREMAN__4__504030_0 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4( 504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SFOREMAN__4__504030_0 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4( 504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 504029 TO SFORE_1 2 504030 TO SFORE_T1 1 504031 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SFOREMAN__4__NNBOSTN4 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO NNBOSTN4 138.0 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SFOREMAN__4__NNBOSTN4 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO NNBOSTN4 138.0 KV 508069 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SFOREMAN__4__PATTERS4 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SFOREMAN__4__PATTERS4 | 3 Phase fault on SFOREMAN 4 (504029) 138 kV Bus a. Apply fault at the SFOREMAN 4 (504029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SFOREMAN 4 138.0 KV 504029 TO PATTERS4 138.0 KV 507431 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SHAWNEE2__SINCPNT2 | 3 Phase fault on SHAWNEE2 (515068) 69 kV Bus a. Apply fault at the SHAWNEE2 (515068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE2 69.0 KV 515068 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SHAWNEE2__SINCPNT2 | 3 Phase fault on SHAWNEE2 (515068) 69 kV Bus a. Apply fault at the SHAWNEE2 (515068) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHAWNEE2 69.0 KV 515068 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SHEFFD_4__WEKIWA_4 | 3 Phase fault on SHEFFD-4 (509812) 138 kV Bus a. Apply fault at the SHEFFD-4 (509812) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFD-4 138.0 KV 509812 TO S.S.---4 138.0 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. WEKIWA-4 138.0 KV 509757 TO SHEFFD-4 138.0 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SHEFFD_4__WEKIWA_4 | 3 Phase fault on SHEFFD-4 (509812) 138 kV Bus a. Apply fault at the SHEFFD-4 (509812) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEFFD-4 138.0 KV 509812 TO S.S.---4 138.0 KV 509815 CKT 1 b.2. LOAD 1 509815 b.3. WEKIWA-4 138.0 KV 509757 TO SHEFFD-4 138.0 KV 509812 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SHILETP4__ORU_WTP4 | 3 Phase fault on SHILETP4 (509813) 138 kV Bus a. Apply fault at the SHILETP4 (509813) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138.0 KV 509813 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SHILETP4__ORU_WTP4 | 3 Phase fault on SHILETP4 (509813) 138 kV Bus a. Apply fault at the SHILETP4 (509813) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHILETP4 138.0 KV 509813 TO ORU-WTP4 138.0 KV 509853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SINCPAN2__SINCPNT2 | 3 Phase fault on SINCPAN2 (515072) 69 kV Bus a. Apply fault at the SINCPAN2 (515072) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCPAN2 69.0 KV 515072 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SINCPAN2__SINCPNT2 | 3 Phase fault on SINCPAN2 (515072) 69 kV Bus a. Apply fault at the SINCPAN2 (515072) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SINCPAN2 69.0 KV 515072 TO SINCPNT2 69.0 KV 515642 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SKYLINE4__CHISHOM4 | 3 Phase fault on SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO CHISHOM4 138.0 KV 515374 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SKYLINE4__CHISHOM4 | 3 Phase fault on SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO CHISHOM4 138.0 KV 515374 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SKYLINE4__KETCH__4 | 3 Phase fault on SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO CHISHOM4 138.0 KV 515374 CKT 1 b.2. LOAD 1 515374 b.3. CHISHOM4 138.0 KV 515374 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.4. LOAD 1 515468 b.5. KETCH 4 138.0 KV 514834 TO FAIRFLD4 138.0 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SKYLINE4__KETCH__4 | 3 Phase fault on SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO CHISHOM4 138.0 KV 515374 CKT 1 b.2. LOAD 1 515374 b.3. CHISHOM4 138.0 KV 515374 TO FAIRFLD4 138.0 KV 515468 CKT 1 b.4. LOAD 1 515468 b.5. KETCH 4 138.0 KV 514834 TO FAIRFLD4 138.0 KV 515468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SKYLINE4__QUAILCK4 | 3 Phase fault on SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SKYLINE4__QUAILCK4 | 3 Phase fault on SKYLINE4 (514850) 138 kV Bus a. Apply fault at the SKYLINE4 (514850) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SKYLINE4 138.0 KV 514850 TO QUAILCK4 138.0 KV 514851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SLNGWND7__515583_0 | 3 Phase fault on SLNGWND7 (515582) 345 kV Bus a. Apply fault at the SLNGWND7( 515582) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SLNGWND7 515582 TO SLINGW11 515583 TO SILNGWT1 515584 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SLNGWND7__515583_0 | 3 Phase fault on SLNGWND7 (515582) 345 kV Bus a. Apply fault at the SLNGWND7( 515582) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SLNGWND7 515582 TO SLINGW11 515583 TO SILNGWT1 515584 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SLNGWND7__515632_0 | 3 Phase fault on SLNGWND7 (515582) 345 kV Bus a. Apply fault at the SLNGWND7( 515582) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SLNGWND7 515582 TO SILNGW21 515632 TO SILNGWT2 515633 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SLNGWND7__515632_0 | 3 Phase fault on SLNGWND7 (515582) 345 kV Bus a. Apply fault at the SLNGWND7( 515582) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SLNGWND7 515582 TO SILNGW21 515632 TO SILNGWT2 515633 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SLVRLAK4__DVISION4 | 3 Phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SLVRLAK4__DVISION4 | 3 Phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO DVISION4 138.0 KV 514853 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SLVRLAK4__NORTWST4 | 3 Phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO BRADEN 4 138.0 KV 514854 CKT 1 b.2. LOAD 1 514854 b.3. BRADEN 4 138.0 KV 514854 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SLVRLAK4__NORTWST4 | 3 Phase fault on SLVRLAK4 (514852) 138 kV Bus a. Apply fault at the SLVRLAK4 (514852) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SLVRLAK4 138.0 KV 514852 TO BRADEN 4 138.0 KV 514854 CKT 1 b.2. LOAD 1 514854 b.3. BRADEN 4 138.0 KV 514854 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SMITH_1G__514891_0 | 3 Phase fault on SMITH 1G (514890) 13.8 kV Bus a. Apply fault at the SMITH 1G( 514890) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMITH 1G 514890 TO SMITHCO4 514891 TO SMITH 1S 514897 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SMITH_1G__514891_0 | 3 Phase fault on SMITH 1G (514890) 13.8 kV Bus a. Apply fault at the SMITH 1G( 514890) 13.8 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMITH 1G 514890 TO SMITHCO4 514891 TO SMITH 1S 514897 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SMITHCO4__DAYTON_4 | 3 Phase fault on SMITHCO4 (514891) 138 kV Bus a. Apply fault at the SMITHCO4 (514891) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMITHCO4 138.0 KV 514891 TO DAYTON 4 138.0 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SMITHCO4__DAYTON_4 | 3 Phase fault on SMITHCO4 (514891) 138 kV Bus a. Apply fault at the SMITHCO4 (514891) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMITHCO4 138.0 KV 514891 TO DAYTON 4 138.0 KV 514892 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | SO4TH__2__514731_0 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SO4TH__2__514731_0 | 3 Phase fault on SO4TH 2 (514730) 69 kV Bus a. Apply fault at the SO4TH 2( 514730) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 2 514730 TO SO4TH 4 514731 TO SO4TH 1 515758 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SO4TH__4__BRECKNR4 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SO4TH__4__BRECKNR4 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SO4TH__4__IMO____4 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SO4TH__4__IMO____4 | 3 Phase fault on SO4TH 4 (514731) 138 kV Bus a. Apply fault at the SO4TH 4 (514731) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SO4TH 4 138.0 KV 514731 TO IMO 4 138.0 KV 514790 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SOUTHRD4__ROMNOSE4 | 3 Phase fault on SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138.0 KV 514822 TO ROMNOSE4 138.0 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SOUTHRD4__ROMNOSE4 | 3 Phase fault on SOUTHRD4 (514822) 138 kV Bus a. Apply fault at the SOUTHRD4 (514822) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SOUTHRD4 138.0 KV 514822 TO ROMNOSE4 138.0 KV 514823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SPGVLLY4_138kV_515574 | Apply single-phase fault on: PAYNESB4 138KV 515039 TO SPGVLLY4 138KV 515574 CKT 1 and CUSHING4 138KV 515033 TO PAYNESB4 138KV 515039 CKT 1, near SPGVLLY4 138kV for 7 cycles with stuck breaker at SPGVLLY4 138kV. Clear Fault after 16 cycles and trip: KNIPE4 138KV 515514 TO SPGVLLY4 138KV 515574 CKT 1 and KNIPE4 138KV 515514 TO TYRON4 138KV 515675 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SPGVLLY4_138kV_515574 | Apply single-phase fault on: PAYNESB4 138KV 515039 TO SPGVLLY4 138KV 515574 CKT 1 and CUSHING4 138KV 515033 TO PAYNESB4 138KV 515039 CKT 1, near SPGVLLY4 138kV for 7 cycles with stuck breaker at SPGVLLY4 138kV. Clear Fault after 16 cycles and trip: KNIPE4 138KV 515514 TO SPGVLLY4 138KV 515574 CKT 1 and KNIPE4 138KV 515514 TO TYRON4 138KV 515675 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SPNSPUR_WND7__SPNSPUR_COL7 | 3 Phase fault on SPNSPUR_WND7 (524296) 345 kV Bus a. Apply fault at the SPNSPUR_WND7 (524296) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPNSPUR_WND7 345.0 KV 524296 TO SPNSPUR_COL7 345.0 KV 524299 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SPPMAINBUS__SPP_CAP1 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO SPP-CAP1 345.0 KV 5921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SPPMAINBUS__SPP_CAP1 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO SPP-CAP1 345.0 KV 5921 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | SPPMAINBUS__SPP_CAP2 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO SPP-CAP2 345.0 KV 5922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SPPMAINBUS__SPP_CAP2 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO SPP-CAP2 345.0 KV 5922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | SPPMAINBUS__SPP_CAP3 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO SPP-CAP3 345.0 KV 5923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SPPMAINBUS__SPP_CAP3 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO SPP-CAP3 345.0 KV 5923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | SPPMAINBUS__SPP_REAC1 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO SPP-REAC1 345.0 KV 5924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SPPMAINBUS__SPP_REAC1 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO SPP-REAC1 345.0 KV 5924 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | SPPMAINBUS__WELSH__7 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SPPMAINBUS__WELSH__7 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSH 7 345.0 KV 508359 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | SPPMAINBUS__WELSHDC1 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSHDC1 345.0 KV 5919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SPPMAINBUS__WELSHDC1 | 3 Phase fault on SPPMAINBUS (5917) 345 kV Bus a. Apply fault at the SPPMAINBUS (5917) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPPMAIN345.0 KV 5917 TO WELSHDC1 345.0 KV 5919 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | SPRHILL4__DIANA__4 | 3 Phase fault on SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138.0 KV 508571 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SPRHILL4__DIANA__4 | 3 Phase fault on SPRHILL4 (508571) 138 kV Bus a. Apply fault at the SPRHILL4 (508571) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRHILL4 138.0 KV 508571 TO DIANA 4 138.0 KV 508831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SQUIRCK4__NE45TAP4 | 3 Phase fault on SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO INGLEWD4 138.0 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138.0 KV 515060 TO STGREG 4 138.0 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138.0 KV 515061 TO NE45TAP4 138.0 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SQUIRCK4__NE45TAP4 | 3 Phase fault on SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO INGLEWD4 138.0 KV 515060 CKT 1 b.2. LOAD 1 515060 b.3. INGLEWD4 138.0 KV 515060 TO STGREG 4 138.0 KV 515061 CKT 1 b.4. LOAD 1 515061 b.5. STGREG 4 138.0 KV 515061 TO NE45TAP4 138.0 KV 515062 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SQUIRCK4__STRLGTP4 | 3 Phase fault on SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SQUIRCK4__STRLGTP4 | 3 Phase fault on SQUIRCK4 (515059) 138 kV Bus a. Apply fault at the SQUIRCK4 (515059) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQUIRCK4 138.0 KV 515059 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | STALOGA2__TALOGA_2 | 3 Phase fault on STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | STALOGA2__TALOGA_2 | 3 Phase fault on STALOGA2 (520454) 69 kV Bus a. Apply fault at the STALOGA2 (520454) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STALOGA2 69.0 KV 520454 TO TALOGA 2 69.0 KV 521064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | STNWAL_4__REMPKTP4 | 3 Phase fault on STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138.0 KV 514870 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | STNWAL_4__REMPKTP4 | 3 Phase fault on STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138.0 KV 514870 TO REMPKTP4 138.0 KV 514872 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | STNWAL_4__RENO___4 | 3 Phase fault on STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138.0 KV 514870 TO OUMED 4 138.0 KV 514875 CKT 1 b.2. LOAD 1 514875 b.3. OUMED 4 138.0 KV 514875 TO GATEWAY4 138.0 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. RENO 4 138.0 KV 514973 TO WASHPRK4 138.0 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | STNWAL_4__RENO___4 | 3 Phase fault on STNWAL 4 (514870) 138 kV Bus a. Apply fault at the STNWAL 4 (514870) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STNWAL 4 138.0 KV 514870 TO OUMED 4 138.0 KV 514875 CKT 1 b.2. LOAD 1 514875 b.3. OUMED 4 138.0 KV 514875 TO GATEWAY4 138.0 KV 515963 CKT 1 b.4. LOAD 1 515963 b.5. WASHPRK4 138.0 KV 515156 TO GATEWAY4 138.0 KV 515963 CKT 1 b.6. LOAD 1 515963 b.7. RENO 4 138.0 KV 514973 TO WASHPRK4 138.0 KV 515156 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | STRLGTP4__STERLNG4 | 3 Phase fault on STRLGTP4 (515286) 138 kV Bus a. Apply fault at the STRLGTP4 (515286) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138.0 KV 515286 TO STERLNG4 138.0 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | STRLGTP4__STERLNG4 | 3 Phase fault on STRLGTP4 (515286) 138 kV Bus a. Apply fault at the STRLGTP4 (515286) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STRLGTP4 138.0 KV 515286 TO STERLNG4 138.0 KV 520449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | STUBMAN4__HOLLYWD4 | 3 Phase fault on STUBMAN4 (514952) 138 kV Bus a. Apply fault at the STUBMAN4 (514952) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STUBMAN4 138.0 KV 514952 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | STUBMAN4__HOLLYWD4 | 3 Phase fault on STUBMAN4 (514952) 138 kV Bus a. Apply fault at the STUBMAN4 (514952) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STUBMAN4 138.0 KV 514952 TO HOLLYWD4 138.0 KV 514953 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUBIACT5_161kV_515440 | Apply single-phase fault on: SUBIACT5 161.0 KV 515440 TO SUBIACO5 161.0 KV 515441 CKT 1, near SUBIACT5 161kV for 7 cycles with stuck breaker at SUBIACT5 161kV. Clear Fault after 16 cycles and trip: RAZRBAK5 161KV 515357 TO SUBIACT5 161.0 KV 515440 CKT 1 and IGO5 161KV 515355 TO RAZRBAK5 161KV 515357 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUBIACT5_161kV_515440 | Apply single-phase fault on: SUBIACT5 161.0 KV 515440 TO SUBIACO5 161.0 KV 515441 CKT 1, near SUBIACT5 161kV for 7 cycles with stuck breaker at SUBIACT5 161kV. Clear Fault after 16 cycles and trip: RAZRBAK5 161KV 515357 TO SUBIACT5 161.0 KV 515440 CKT 1 and IGO5 161KV 515355 TO RAZRBAK5 161KV 515357 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUGARHL2__508080_0 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2( 508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUGARHL2__508080_0 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2( 508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 508079 TO SUGARHL4 508080 TO SHILL1-1 508103 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUGARHL2__SUGHLET2 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69.0 KV 508079 TO SUGHLET2 69.0 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUGARHL2__SUGHLET2 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69.0 KV 508079 TO SUGHLET2 69.0 KV 508081 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUGARHL2__SUGHLWT2 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69.0 KV 508079 TO SUGHLWT2 69.0 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUGARHL2__SUGHLWT2 | 3 Phase fault on SUGARHL2 (508079) 69 kV Bus a. Apply fault at the SUGARHL2 (508079) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGARHL2 69.0 KV 508079 TO SUGHLWT2 69.0 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUGHLWT2__TEX39ST2 | 3 Phase fault on SUGHLWT2 (508082) 69 kV Bus a. Apply fault at the SUGHLWT2 (508082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLWT2 69.0 KV 508082 TO TEX39ST2 69.0 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUGHLWT2__TEX39ST2 | 3 Phase fault on SUGHLWT2 (508082) 69 kV Bus a. Apply fault at the SUGHLWT2 (508082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGHLWT2 69.0 KV 508082 TO TEX39ST2 69.0 KV 508085 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYLN2__TINKER32 | 3 Phase fault on SUNNYLN2 (514980) 69 kV Bus a. Apply fault at the SUNNYLN2 (514980) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYLN2 69.0 KV 514980 TO TINKER32 69.0 KV 514981 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNNYLN2__TINKER32 | 3 Phase fault on SUNNYLN2 (514980) 69 kV Bus a. Apply fault at the SUNNYLN2 (514980) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYLN2 69.0 KV 514980 TO TINKER32 69.0 KV 514981 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SUNNYSD4__CARTER_4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO UNIROY 4 138.0 KV 515137 CKT 1 b.2. LOAD 1 515137 b.3. UNIROY 4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 b.4. LOAD 1 515372 b.5. CARTER 4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SUNNYSD4__CARTRCO4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO CARTRCO4 138.0 KV 515561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4__LONEGRV4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SUNNYSD4__LONEGRV4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO LONEGRV4 138.0 KV 515144 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SUNNYSD4__ROCKYPT4 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4 (515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 138.0 KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD4_138kV_515135 | Apply single-phase fault on: SUNNYSD4 138KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1, near SUNNYSD4 138kV for 7 cycles with stuck breaker at SUNNYSD4 138kV. Clear Fault after 16 cycles and trip: SUNNYSD4 138KV 515135 TO UNIROY4 138.0 KV 515137 CKT 1 and UNIROY4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 and CARTER4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNNYSD4_138kV_515135 | Apply single-phase fault on: SUNNYSD4 138KV 515135 TO ROCKYPT4 138.0 KV 515164 CKT 1, near SUNNYSD4 138kV for 7 cycles with stuck breaker at SUNNYSD4 138kV. Clear Fault after 16 cycles and trip: SUNNYSD4 138KV 515135 TO UNIROY4 138.0 KV 515137 CKT 1 and UNIROY4 138.0 KV 515137 TO ARDWEST4 138.0 KV 515372 CKT 1 and CARTER4 138.0 KV 515138 TO ARDWEST4 138.0 KV 515372 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25W | Transfer | SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25S | Transfer | SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25W | Transfer | SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25S | Transfer | SUNNYSD7__GEN_2017_166 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-166 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded. GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection. Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Lower acceleration to 0.2. Remove Reclose. Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716) . Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SUNNYSD7__GEN_2017_166 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-166 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded. GEN-2017-027 (588713, 588714, 588715, 588716) trips on Voltage Protection | Lower acceleration to 0.2. Remove Reclose. Disable Voltage Protection for GEN-2017-027 (588713, 588714, 588715, 588716)
04 - Southeast | 25S | Transfer | SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G16063TAP 345.0 KV 560088 CKT 1, near SUNNYSD7 345kV for 6 cycles with stuck breaker at SUNNYSD7 345kV. Clear Fault after 16 cycles and trip: TERRYRD7 345KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SUNNYSD7_345kV_515136 | Apply single-phase fault on: SUNNYSD7 345.0 KV 515136 TO G16063TAP 345.0 KV 560088 CKT 1, near SUNNYSD7 345kV for 6 cycles with stuck breaker at SUNNYSD7 345kV. Clear Fault after 16 cycles and trip: TERRYRD7 345KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | SUNSHIN4_138kV_521059 | Apply single-phase fault on: BRIDGCR4 138KV 520501 TO SUNSHIN4 138KV 521059 CKT 1 and BRIDGCR4 138KV 520501 TO TUTLETP4 138KV 521072 CKT 1, near SUNSHIN4 138kV for 7 cycles with stuck breaker at SUNSHIN4 138kV. Clear Fault after 16 cycles and trip: BAILEY4 138KV 520401 TO SUNSHIN4 138KV 521059 CKT 1 and BAILEY4 138KV 520401 TO WMOORE4 138KV 521123 CKT 1 and FRNKLNS4 138KV 520917 TO WMOORE4 138KV 521123 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SUNSHIN4_138kV_521059 | Apply single-phase fault on: BRIDGCR4 138KV 520501 TO SUNSHIN4 138KV 521059 CKT 1 and BRIDGCR4 138KV 520501 TO TUTLETP4 138KV 521072 CKT 1, near SUNSHIN4 138kV for 7 cycles with stuck breaker at SUNSHIN4 138kV. Clear Fault after 16 cycles and trip: BAILEY4 138KV 520401 TO SUNSHIN4 138KV 521059 CKT 1 and BAILEY4 138KV 520401 TO WMOORE4 138KV 521123 CKT 1 and FRNKLNS4 138KV 520917 TO WMOORE4 138KV 521123 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_5TH_2__514920_0 | 3 Phase fault on SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2( 514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 514919 TO SW 5TH 4 514920 TO SW 5TH 1 515763 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_5TH_2__514920_0 | 3 Phase fault on SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2( 514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 514919 TO SW 5TH 4 514920 TO SW 5TH 1 515763 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_5TH_2__KENTUKT2 | 3 Phase fault on SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 69.0 KV 514919 TO SW22ND 2 69.0 KV 514975 CKT 1 b.2. LOAD 1 514975 b.3. SW22ND 2 69.0 KV 514975 TO KENTUKY2 69.0 KV 514976 CKT 1 b.4. LOAD 1 514976 b.5. KENTUKY2 69.0 KV 514976 TO KENTUKT2 69.0 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_5TH_2__KENTUKT2 | 3 Phase fault on SW 5TH 2 (514919) 69 kV Bus a. Apply fault at the SW 5TH 2 (514919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 2 69.0 KV 514919 TO SW22ND 2 69.0 KV 514975 CKT 1 b.2. LOAD 1 514975 b.3. SW22ND 2 69.0 KV 514975 TO KENTUKY2 69.0 KV 514976 CKT 1 b.4. LOAD 1 514976 b.5. KENTUKY2 69.0 KV 514976 TO KENTUKT2 69.0 KV 514977 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_5TH_4__CLASSEN4 | 3 Phase fault on SW 5TH 4 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 138.0 KV 514920 TO CLASSEN4 138.0 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SW_5TH_4__CLASSEN4 | 3 Phase fault on SW 5TH 4 (514920) 138 kV Bus a. Apply fault at the SW 5TH 4 (514920) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW 5TH 4 138.0 KV 514920 TO CLASSEN4 138.0 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 7G (515669), and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 8G (515670), MSTNG 9G (515671), MSTNG 7G (515669), and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | SW_SHV_4__LEASIDE_4 | 3 Phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138.0 KV 507759 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_SHV_4__LEASIDE_4 | 3 Phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW SHV 4 138.0 KV 507759 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_SHV_4__ROKHILL4 | 3 Phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138.0 KV 507757 TO SW SHV 4 138.0 KV 507759 CKT 1 b.2. SPRIDGE4 138.0 KV 507757 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138.0 KV 509083 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_SHV_4__ROKHILL4 | 3 Phase fault on SW SHV 4 (507759) 138 kV Bus a. Apply fault at the SW SHV 4 (507759) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRIDGE4 138.0 KV 507757 TO SW SHV 4 138.0 KV 507759 CKT 1 b.2. SPRIDGE4 138.0 KV 507757 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 b.3. LOAD 1 509103 b.4. ROKHILL4 138.0 KV 509083 TO WLNTSPRINGS4 138.0 KV 509103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_SHV_7__507759_0 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_SHV_7__507759_0 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7( 507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 507760 TO SW SHV 4 507759 TO SWSHV1-1 507778 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_SHV_7__DIANA__7 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_SHV_7__DIANA__7 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO DIANA 7 345.0 KV 508832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW_SHV_7__LONGWD_7 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW_SHV_7__LONGWD_7 | 3 Phase fault on SW SHV 7 (507760) 345 kV Bus a. Apply fault at the SW SHV 7 (507760) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SW SHV 7 345.0 KV 507760 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW134TP4__SOGATE_4 | 3 Phase fault on SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138.0 KV 514876 TO SOGATE 4 138.0 KV 514928 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | SW134TP4__SOGATE_4 | 3 Phase fault on SW134TP4 (514876) 138 kV Bus a. Apply fault at the SW134TP4 (514876) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW134TP4 138.0 KV 514876 TO SOGATE 4 138.0 KV 514928 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SW134TP4_138kV_514876 | Apply single-phase fault on: SW134TP4 138KV 514876 TO G17-152-TAP 138.0 KV 914902 CKT 1, near SW134TP4 138kV for 7 cycles with stuck breaker at SW134TP4 138kV. Clear Fault after 16 cycles and trip: SW134TP4 138KV 514876 TO WESTMOR4 138.0 KV 514887 CKT 1 and WESTMOR4 138.0 KV 514887 TO PENN4 138.0 KV 514925 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SW134TP4_138kV_514876 | Apply single-phase fault on: SW134TP4 138KV 514876 TO G17-152-TAP 138.0 KV 914902 CKT 1, near SW134TP4 138kV for 7 cycles with stuck breaker at SW134TP4 138kV. Clear Fault after 16 cycles and trip: SW134TP4 138KV 514876 TO WESTMOR4 138.0 KV 514887 CKT 1 and WESTMOR4 138.0 KV 514887 TO PENN4 138.0 KV 514925 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWEETWT6__BUFFCK6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO BUFFCK6 230.0 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | SWEETWT6__BUFFCK6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO BUFFCK6 230.0 KV 511542 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25S | Transfer | SWEETWT6__CHISHOLM6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | SWEETWT6__CHISHOLM6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25S | Transfer | SWEETWT6__DEMPSEY6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO DEMPSEY6 230.0 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | SWEETWT6__DEMPSEY6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO DEMPSEY6 230.0 KV 511544 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | SWEETWT6__ROARK6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO ROARK6 230.0 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | SWEETWT6__ROARK6 | 3 Phase fault on SWEETWT6 (511541) 230 kV Bus a. Apply fault at the SWEETWT6 (511541) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWEETWT6 230.0 KV 511541 TO ROARK6 230.0 KV 511547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25S | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | SWSHV7_345kV_507760 | Apply single-phase fault on: LONGWD7 345KV 508809 TO SWSHV7 345.0 KV 507760 CKT 1, near SW SHV 7 345 kV for 6 cycles with stuck breaker at SW SHV 7 345 kV. Clear Fault after 16 cycles and trip: SWSHV7 345.0 KV 507760 TO DIANA7 345KV 508832 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | SWSHV7_345kV_507760 | Apply single-phase fault on: LONGWD7 345KV 508809 TO SWSHV7 345.0 KV 507760 CKT 1, near SW SHV 7 345 kV for 6 cycles with stuck breaker at SW SHV 7 345 kV. Clear Fault after 16 cycles and trip: SWSHV7 345.0 KV 507760 TO DIANA7 345KV 508832 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_NO___7__N_E_S__7 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_NO___7__N_E_S__7 | 3 Phase fault on T.NO.--7 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 345.0 KV 509852 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_P_S__2__509788_0 | 3 Phase fault on T.P.S.-2 (509789) 69 kV Bus a. Apply fault at the T.P.S.-2( 509789) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-2 509789 TO T.P.S.-4 509788 TO TPS5-1 509880 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_P_S__2__509788_0 | 3 Phase fault on T.P.S.-2 (509789) 69 kV Bus a. Apply fault at the T.P.S.-2( 509789) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-2 509789 TO T.P.S.-4 509788 TO TPS5-1 509880 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_P_S__2__OGMARTN2 | 3 Phase fault on T.P.S.-2 (509789) 69 kV Bus a. Apply fault at the T.P.S.-2 (509789) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLPIP2 69.0 KV 509750 TO T.P.S.-2 69.0 KV 509789 CKT 1 b.2. LOAD 1 509789 b.3. WILLPIP2 69.0 KV 509750 TO OGMARTN2 69.0 KV 509751 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | T_P_S__2__OGMARTN2 | 3 Phase fault on T.P.S.-2 (509789) 69 kV Bus a. Apply fault at the T.P.S.-2 (509789) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLPIP2 69.0 KV 509750 TO T.P.S.-2 69.0 KV 509789 CKT 1 b.2. LOAD 1 509789 b.3. WILLPIP2 69.0 KV 509750 TO OGMARTN2 69.0 KV 509751 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25S | Transfer | T_P_S__4__52DELTP4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 36LEWIS4 138.0 KV 509800 CKT 1 b.2. LOAD 1 509800 b.3. 52DELTP4 138.0 KV 509776 TO 36LEWIS4 138.0 KV 509800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_P_S__4__52DELTP4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 36LEWIS4 138.0 KV 509800 CKT 1 b.2. LOAD 1 509800 b.3. 52DELTP4 138.0 KV 509776 TO 36LEWIS4 138.0 KV 509800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_P_S__4__52DELWT4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_P_S__4__52DELWT4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 52DELWT4 138.0 KV 509814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_P_S__4__CARSN_T4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138.0 KV 509724 TO T.P.S.-4 138.0 KV 509788 CKT 1 b.2. LOAD 1 509788 b.3. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_P_S__4__CARSN_T4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&OLY-4 138.0 KV 509724 TO T.P.S.-4 138.0 KV 509788 CKT 1 b.2. LOAD 1 509788 b.3. 36&OLY-4 138.0 KV 509724 TO CARSN-T4 138.0 KV 509739 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_P_S__4__G18_027_TAP | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO G18-027-TAP 138.0 KV 762629 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_P_S__4__G18_027_TAP | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO G18-027-TAP 138.0 KV 762629 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_P_S__4__OAKSWTP4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSWTP4 138.0 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | T_P_S__4__OAKSWTP4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO OAKSWTP4 138.0 KV 509848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | T_P_S__4__SAPLPRD4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 72ELWOD4 138.0 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. SAPLPRD4 138.0 KV 509871 TO 72ELWOD4 138.0 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_P_S__4__SAPLPRD4 | 3 Phase fault on T.P.S.-4 (509788) 138 kV Bus a. Apply fault at the T.P.S.-4 (509788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.P.S.-4 138.0 KV 509788 TO 72ELWOD4 138.0 KV 509888 CKT 1 b.2. LOAD 1 509888 b.3. SAPLPRD4 138.0 KV 509871 TO 72ELWOD4 138.0 KV 509888 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_S_E__2__509811_0 | 3 Phase fault on T.S.E.-2 (509820) 69 kV Bus a. Apply fault at the T.S.E.-2( 509820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-2 509820 TO T.S.E.-4 509811 TO TSE3-1 509873 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_S_E__2__509811_0 | 3 Phase fault on T.S.E.-2 (509820) 69 kV Bus a. Apply fault at the T.S.E.-2( 509820) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-2 509820 TO T.S.E.-4 509811 TO TSE3-1 509873 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_S_E__4__21STTAP4 | 3 Phase fault on T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138.0 KV 509811 TO 21STTAP4 138.0 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_S_E__4__21STTAP4 | 3 Phase fault on T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138.0 KV 509811 TO 21STTAP4 138.0 KV 509828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_S_E__4__E_61ST_4 | 3 Phase fault on T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138.0 KV 509811 TO E.61ST-4 138.0 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_S_E__4__E_61ST_4 | 3 Phase fault on T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138.0 KV 509811 TO E.61ST-4 138.0 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_S_E__4__KENSH_E_TP4 | 3 Phase fault on T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138.0 KV 509811 TO KENSH-E-TP4 138.0 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_S_E__4__KENSH_E_TP4 | 3 Phase fault on T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138.0 KV 509811 TO KENSH-E-TP4 138.0 KV 509830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | T_S_E__4__S_HUD__4 | 3 Phase fault on T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138.0 KV 509811 TO S.HUD.-4 138.0 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | T_S_E__4__S_HUD__4 | 3 Phase fault on T.S.E.-4 (509811) 138 kV Bus a. Apply fault at the T.S.E.-4 (509811) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. T.S.E.-4 138.0 KV 509811 TO S.HUD.-4 138.0 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TAHLQH_5__512647_0 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5( 512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TAHLQH_5__512647_0 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5( 512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 512655 TO TAHLQH 2 512647 TO TAHLQH1 512851 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TAHLQH_5__BRIGSKM_5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TAHLQH_5__BRIGSKM_5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO BRIGSKM 5 161.0 KV 513044 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TAHLQH_5__HWY59TP5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TAHLQH_5__HWY59TP5 | 3 Phase fault on TAHLQH 5 (512655) 161 kV Bus a. Apply fault at the TAHLQH 5 (512655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAHLQH 5 161.0 KV 512655 TO HWY59TP5 161.0 KV 515527 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TALOGA_2__VICI___2 | 3 Phase fault on TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TALOGA_2__VICI___2 | 3 Phase fault on TALOGA 2 (521064) 69 kV Bus a. Apply fault at the TALOGA 2 (521064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 2 69.0 KV 521064 TO VICI 2 69.0 KV 521082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TALOGA_4__521064_0 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4( 521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TALOGA_4__521064_0 | 3 Phase fault on TALOGA 4 (521065) 138 kV Bus a. Apply fault at the TALOGA 4( 521065) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TALOGA 4 521065 TO TALOGA 2 521064 TO TLGTERT 521178 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TATONGA7__CRSRDSW7 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | TATONGA7__CRSRDSW7 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO CRSRDSW7 345.0 KV 515448 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | TATONGA7__MAMTHPW7 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TATONGA7__MAMTHPW7 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MAMTHPW7 345.0 KV 515585 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TATONGA7__MATHWSN7 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TATONGA7__MATHWSN7 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TATONGA7__SLNGWND7 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TATONGA7__SLNGWND7 | 3 Phase fault on TATONGA7 (515407) 345 kV Bus a. Apply fault at the TATONGA7 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 345.0 KV 515407 TO SLNGWND7 345.0 KV 515582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TAYLOR_2__TEXOPER2 | 3 Phase fault on TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69.0 KV 508083 TO TEXOPER2 69.0 KV 508087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TAYLOR_2__TEXOPER2 | 3 Phase fault on TAYLOR 2 (508083) 69 kV Bus a. Apply fault at the TAYLOR 2 (508083) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 2 69.0 KV 508083 TO TEXOPER2 69.0 KV 508087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TECUMSH2__FRSTHIL2 | 3 Phase fault on TECUMSH2 (515071) 69 kV Bus a. Apply fault at the TECUMSH2 (515071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69.0 KV 515071 TO FRSTHIL2 69.0 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TECUMSH2__FRSTHIL2 | 3 Phase fault on TECUMSH2 (515071) 69 kV Bus a. Apply fault at the TECUMSH2 (515071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TECUMSH2 69.0 KV 515071 TO FRSTHIL2 69.0 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TENESTP4__84TH_ST4 | 3 Phase fault on TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO 84TH ST4 138.0 KV 514843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TENESTP4__84TH_ST4 | 3 Phase fault on TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO 84TH ST4 138.0 KV 514843 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TENESTP4__BELISLE4 | 3 Phase fault on TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO 84TH ST4 138.0 KV 514843 CKT 1 b.2. LOAD 1 514843 b.3. 84TH ST4 138.0 KV 514843 TO BELISLE4 138.0 KV 514844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TENESTP4__BELISLE4 | 3 Phase fault on TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO 84TH ST4 138.0 KV 514843 CKT 1 b.2. LOAD 1 514843 b.3. 84TH ST4 138.0 KV 514843 TO BELISLE4 138.0 KV 514844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TENESTP4__TENNESE4 | 3 Phase fault on TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO TENNESE4 138.0 KV 514838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TENESTP4__TENNESE4 | 3 Phase fault on TENESTP4 (514837) 138 kV Bus a. Apply fault at the TENESTP4 (514837) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENESTP4 138.0 KV 514837 TO TENNESE4 138.0 KV 514838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TENRUSK7__CROCKET7 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TENRUSK7__CROCKET7 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO CROCKET7 345.0 KV 509241 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TENRUSK7__TENGEN_7 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TENRUSK7__TENGEN_7 | 3 Phase fault on TENRUSK7 (508585) 345 kV Bus a. Apply fault at the TENRUSK7 (508585) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TENRUSK7 345.0 KV 508585 TO TENGEN 7 345.0 KV 508586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 (584862) trips on Voltage Protection. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable Voltage Protection for GEN-2015-045 (584862). Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25S | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2015-045 (584862) trips on Voltage Protection | Disable Voltage Protection for GEN-2015-045 (584862)
04 - Southeast | 25S | Transfer | TERRYRD7_345kV_511568 | Apply single-phase fault on: TERRRD7 345KV 511568 TO G17171TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345kV for 6 cycles with stuck breaker at TERRYRD7 345kV. Clear Fault after 16 cycles and trip: TERRRD7 345KV 511568 TO SUNNYSD7 345KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TERRYRD7_345kV_511568 | Apply single-phase fault on: TERRRD7 345KV 511568 TO G17171TAP 345.0 KV 760938 CKT 1, near TERRYRD7 345kV for 6 cycles with stuck breaker at TERRYRD7 345kV. Clear Fault after 16 cycles and trip: TERRRD7 345KV 511568 TO SUNNYSD7 345KV 515136 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-055 (762903) trips on Voltage Protection Settings. | Disable Voltage Protection Settings for GEN-2018-055 (762903).
04 - Southeast | 25S | Transfer | THISTLE7__539804_0 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7( 539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | THISTLE7__539804_0 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7( 539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 539801 TO THISTLE4 539804 TO THISTLE T1 539802 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | THISTLE7__GEN_2017_018 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | THISTLE7__GEN_2017_018 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2017-018 345.0 KV 588630 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | THISTLE7__GEN_2018_049 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25W | Transfer | THISTLE7__GEN_2018_049 | 3 Phase fault on THISTLE7 (539801) 345 kV Bus a. Apply fault at the THISTLE7 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 345.0 KV 539801 TO GEN-2018-049 345.0 KV 762834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
04 - Southeast | 25S | Transfer | TOLK_______6__525549_0 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6( 525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 525531 TO TOLK 7 525549 TO TOLK_TR 1 525537 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TOLK_______6__525549_0 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6( 525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 525531 TO TOLK 7 525549 TO TOLK_TR 1 525537 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TPS4_138kV_509788 | Apply single-phase fault on: TPS4 138KV 509788 TO 36LEWIS4 138KV 509800 CKT 1, near T.P.S.-4 138 kV for 7 cycles with stuck breaker at T.P.S.-4 138 kV. Clear Fault after 16 cycles and trip: TPS4 138KV 509788 TO 36&OLY4 138KV 509724 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TPS4_138kV_509788 | Apply single-phase fault on: TPS4 138KV 509788 TO 36LEWIS4 138KV 509800 CKT 1, near T.P.S.-4 138 kV for 7 cycles with stuck breaker at T.P.S.-4 138 kV. Clear Fault after 16 cycles and trip: TPS4 138KV 509788 TO 36&OLY4 138KV 509724 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TROSPER4__CLASSEN4 | 3 Phase fault on TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 b.2. LOAD 1 514963 b.3. LIGHTCK4 138.0 KV 514923 TO CROSTWN4 138.0 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TROSPER4__CLASSEN4 | 3 Phase fault on TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 b.2. LOAD 1 514963 b.3. LIGHTCK4 138.0 KV 514923 TO CROSTWN4 138.0 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TROSPER4__RENO___4 | 3 Phase fault on TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TROSPER4__RENO___4 | 3 Phase fault on TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TROSPER4__SELNDTP4 | 3 Phase fault on TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.2. LOAD 1 515387 b.3. FOSTER 4 138.0 KV 514959 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.4. LOAD 1 515387 b.5. FOSTER 4 138.0 KV 514959 TO DISCVRY4 138.0 KV 514962 CKT 1 b.6. LOAD 1 514962 b.7. DISCVRY4 138.0 KV 514962 TO SELNDTP4 138.0 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TROSPER4__SELNDTP4 | 3 Phase fault on TROSPER4 (514963) 138 kV Bus a. Apply fault at the TROSPER4 (514963) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROSPER4 138.0 KV 514963 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.2. LOAD 1 515387 b.3. FOSTER 4 138.0 KV 514959 TO NEWDOMI4 138.0 KV 515387 CKT 1 b.4. LOAD 1 515387 b.5. FOSTER 4 138.0 KV 514959 TO DISCVRY4 138.0 KV 514962 CKT 1 b.6. LOAD 1 514962 b.7. DISCVRY4 138.0 KV 514962 TO SELNDTP4 138.0 KV 515965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25W | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TULSA__4__GEN_2018_028 | 3 Phase fault on TULSA 4 (514847) 138 kV Bus a. Apply fault at the TULSA 4 (514847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULSA 4 138.0 KV 514847 TO GEN-2018-028 138.0 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25W | Transfer | TULSA__4__GEN_2018_028 | 3 Phase fault on TULSA 4 (514847) 138 kV Bus a. Apply fault at the TULSA 4 (514847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULSA 4 138.0 KV 514847 TO GEN-2018-028 138.0 KV 762636 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | TULSA__4__HEFNER_4 | 3 Phase fault on TULSA 4 (514847) 138 kV Bus a. Apply fault at the TULSA 4 (514847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULSA 4 138.0 KV 514847 TO HEFNER 4 138.0 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | TULSA__4__HEFNER_4 | 3 Phase fault on TULSA 4 (514847) 138 kV Bus a. Apply fault at the TULSA 4 (514847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TULSA 4 138.0 KV 514847 TO HEFNER 4 138.0 KV 514848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | TURCRK_2__TURCRKT2 | 3 Phase fault on TURCRK 2 (514735) 69 kV Bus a. Apply fault at the TURCRK 2 (514735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURCRK 2 69.0 KV 514735 TO TURCRKT2 69.0 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TURCRK_2__TURCRKT2 | 3 Phase fault on TURCRK 2 (514735) 69 kV Bus a. Apply fault at the TURCRK 2 (514735) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURCRK 2 69.0 KV 514735 TO TURCRKT2 69.0 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TURK___3__507454_0 | 3 Phase fault on TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3( 507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TURK___3__507454_0 | 3 Phase fault on TURK 3 (507456) 115 kV Bus a. Apply fault at the TURK 3( 507456) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 3 507456 TO TURK 4 507454 TO TURK1 1 507458 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | TURK___4__507455_0 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4( 507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TURK___4__507455_0 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4( 507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 507454 TO TURK 7 507455 TO TURK 1 507457 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | TURK___4__MANDEVILTP4 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TURK___4__MANDEVILTP4 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO MANDEVILTP4 138.0 KV 508105 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | TURK___4__SUGARHL4 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TURK___4__SUGARHL4 | 3 Phase fault on TURK 4 (507454) 138 kV Bus a. Apply fault at the TURK 4 (507454) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TURK 4 138.0 KV 507454 TO SUGARHL4 138.0 KV 508080 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | TURK___7__NWTXARK7 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | TURK___7__NWTXARK7 | 3 Phase fault on TURK 7 (507455) 345 kV Bus a. Apply fault at the TURK 7 (507455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TURK 7 345.0 KV 507455 TO NWTXARK7 345.0 KV 508072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TUTCONT4__CEMRD_TP4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CEMRD_TP4 138.0 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUTCONT4__CEMRD_TP4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CEMRD_TP4 138.0 KV 511576 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2014-020 (583904) and REDBDPLNW0 W1 (51197) trips on Frequency Protection | Disable Frequency Protection for GEN-2014-020 (583904) and REDBDPLNW0 W1 (51197)
04 - Southeast | 25S | Transfer | TUTCONT4__CIMARON4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUTCONT4__CIMARON4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2014-020 (583904) and REDBDPLNW0 W1 (51197) trips on Frequency Protection | Disable Frequency Protection for GEN-2014-020 (583904) and REDBDPLNW0 W1 (51197)
04 - Southeast | 25S | Transfer | TUTCONT4__TUTTLE4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO TUTTLE4 138.0 KV 511501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUTCONT4__TUTTLE4 | 3 Phase fault on TUTCONT4 (511425) 138 kV Bus a. Apply fault at the TUTCONT4 (511425) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTCONT4 138.0 KV 511425 TO TUTTLE4 138.0 KV 511501 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2014-020 (583904) and REDBDPLNW0 W1 (51197) trips on Frequency Protection | Disable Frequency Protection for GEN-2014-020 (583904) and REDBDPLNW0 W1 (51197)
04 - Southeast | 25S | Transfer | TUTTLE_4__TUTLETP4 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TUTTLE_4__TUTLETP4 | 3 Phase fault on TUTTLE 4 (520496) 138 kV Bus a. Apply fault at the TUTTLE 4 (520496) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUTTLE 4 138.0 KV 520496 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TWNLKJT4__TWNLKSW4 | 3 Phase fault on TWNLKJT4 (520847) 138 kV Bus a. Apply fault at the TWNLKJT4 (520847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138.0 KV 520847 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TWNLKJT4__TWNLKSW4 | 3 Phase fault on TWNLKJT4 (520847) 138 kV Bus a. Apply fault at the TWNLKJT4 (520847) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWNLKJT4 138.0 KV 520847 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TWNLKSW4_138kV_521073 | Apply single-phase fault on: TWNLKSW4 138KV 521073 TO TWNLKJT4 138KV 520847 CKT 1, near TWNLKSW4 138 kV for 7 cycles with stuck breaker at TWNLKSW4 138 kV. Clear Fault after 16 cycles and trip: TWNLKSW4 138KV 521073 TO TWNLAKE4 138KV 520540 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TWNLKSW4_138kV_521073 | Apply single-phase fault on: TWNLKSW4 138KV 521073 TO TWNLKJT4 138KV 520847 CKT 1, near TWNLKSW4 138 kV for 7 cycles with stuck breaker at TWNLKSW4 138 kV. Clear Fault after 16 cycles and trip: TWNLKSW4 138KV 521073 TO TWNLAKE4 138KV 520540 CKT Z1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TXPLSTE2__TXPLSTP2 | 3 Phase fault on TXPLSTE2 (514989) 69 kV Bus a. Apply fault at the TXPLSTE2 (514989) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPLSTE2 69.0 KV 514989 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TXPLSTE2__TXPLSTP2 | 3 Phase fault on TXPLSTE2 (514989) 69 kV Bus a. Apply fault at the TXPLSTE2 (514989) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXPLSTE2 69.0 KV 514989 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TXSTELA2__LITLAXT2 | 3 Phase fault on TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TXSTELA2__LITLAXT2 | 3 Phase fault on TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO LITLAXT2 69.0 KV 515502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TXSTELA2__TXPLSTP2 | 3 Phase fault on TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TXSTELA2__TXPLSTP2 | 3 Phase fault on TXSTELA2 (514985) 69 kV Bus a. Apply fault at the TXSTELA2 (514985) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TXSTELA2 69.0 KV 514985 TO TXPLSTP2 69.0 KV 515516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | TYRON4_138kV_515675 | Apply single-phase fault on: LNWOODT4 138KV 515453 TO TYRON4 138KV 515675 CKT 1, near TYRON4 138kV for 7 cycles with stuck breaker at TYRON4 138kV. Clear Fault after 16 cycles and trip: KNIPE4 138KV 515514 TO TYRON4 138KV 515675 CKT 1 and KNIPE4 138KV 515514 TO SPGVLLY4 138KV 515574 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | TYRON4_138kV_515675 | Apply single-phase fault on: LNWOODT4 138KV 515453 TO TYRON4 138KV 515675 CKT 1, near TYRON4 138kV for 7 cycles with stuck breaker at TYRON4 138kV. Clear Fault after 16 cycles and trip: KNIPE4 138KV 515514 TO TYRON4 138KV 515675 CKT 1 and KNIPE4 138KV 515514 TO SPGVLLY4 138KV 515574 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VALIANT4__510911_0 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | VALIANT4__510911_0 | 3 Phase fault on VALIANT4 (510918) 138 kV Bus a. Apply fault at the VALIANT4( 510918) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALIANT4 510918 TO VALIANT7 510911 TO VALN3-1 510939 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VALIANT7__HUGO___7 | 3 Phase fault on VALIANT7 (510911) 345 kV Bus a. Apply fault at the VALIANT7 (510911) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VALIANT7 345.0 KV 510911 TO HUGO 7 345.0 KV 521157 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VALIANT7_345kV_510911 | Apply single-phase fault on: PITTSB7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1, near VALIANT7 345kV for 6 cycles with stuck breaker at VALIANT7 345kV. Clear Fault after 16 cycles and trip: LYDIA7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VALIANT7_345kV_510911 | Apply single-phase fault on: PITTSB7 345.0 KV 510907 TO VALIANT7 345.0 KV 510911 CKT 1, near VALIANT7 345kV for 6 cycles with stuck breaker at VALIANT7 345kV. Clear Fault after 16 cycles and trip: LYDIA7 345.0 KV 508298 TO VALIANT7 345.0 KV 510911 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VBI5_161kV_515339 | Apply single-phase fault on: VANBUR5 161KV 505522 TO VBI5 161KV 515339 CKT Z1, near VBI5 161kV for 7 cycles with stuck breaker at VBI5 161kV. Clear Fault after 16 cycles and trip: VBI5 161KV 515339 TO HWY59TP5 161KV 515527 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VBI5_161kV_515339 | Apply single-phase fault on: VANBUR5 161KV 505522 TO VBI5 161KV 515339 CKT Z1, near VBI5 161kV for 7 cycles with stuck breaker at VBI5 161kV. Clear Fault after 16 cycles and trip: VBI5 161KV 515339 TO HWY59TP5 161KV 515527 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VERDEN_4__S_W_S__4 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VERDEN_4__S_W_S__4 | 3 Phase fault on VERDEN 4 (511421) 138 kV Bus a. Apply fault at the VERDEN 4 (511421) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VERDEN 4 138.0 KV 511421 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | VIOLA7_345kV_532798 | Apply single-phase fault on: RENFROW7 345.0 KV 515543 TO VIOLA7 345.0 KV 532798 CKT 1, near VIOLA7 345kV for 6 cycles with stuck breaker at VIOLA7 345kV. Clear Fault after 16 cycles and trip: WICHITA7 345.0 KV 532796 TO VIOLA7 345.0 KV 532798 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | VIOLA7_345kV_532798 | Apply single-phase fault on: RENFROW7 345.0 KV 515543 TO VIOLA7 345.0 KV 532798 CKT 1, near VIOLA7 345kV for 6 cycles with stuck breaker at VIOLA7 345kV. Clear Fault after 16 cycles and trip: WICHITA7 345.0 KV 532796 TO VIOLA7 345.0 KV 532798 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WARNTAP4__77MEM_W4 | 3 Phase fault on WARNTAP4 (509858) 138 kV Bus a. Apply fault at the WARNTAP4 (509858) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138.0 KV 509847 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 77MEM-W4 138.0 KV 509766 TO 96YALE-4 138.0 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WARNTAP4__77MEM_W4 | 3 Phase fault on WARNTAP4 (509858) 138 kV Bus a. Apply fault at the WARNTAP4 (509858) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 96YALE-4 138.0 KV 509847 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 77MEM-W4 138.0 KV 509766 TO 96YALE-4 138.0 KV 509847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WARNTAP4__WAREN_W4 | 3 Phase fault on WARNTAP4 (509858) 138 kV Bus a. Apply fault at the WARNTAP4 (509858) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138.0 KV 509810 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 81YALES4 138.0 KV 509810 TO WAREN-W4 138.0 KV 509857 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WARNTAP4__WAREN_W4 | 3 Phase fault on WARNTAP4 (509858) 138 kV Bus a. Apply fault at the WARNTAP4 (509858) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALES4 138.0 KV 509810 TO WARNTAP4 138.0 KV 509858 CKT 1 b.2. 81YALES4 138.0 KV 509810 TO WAREN-W4 138.0 KV 509857 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WARWICK4__BELLCOW4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO BELLCOW4 138.0 KV 515369 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WARWICK4__BELLCOW4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO BELLCOW4 138.0 KV 515369 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WARWICK4__TRYON_4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO TRYON 4 138.0 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WARWICK4__TRYON_4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO TRYON 4 138.0 KV 515675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WARWICK4__WFROSST4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO WFROSST4 138.0 KV 515366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WARWICK4__WFROSST4 | 3 Phase fault on WARWICK4 (515047) 138 kV Bus a. Apply fault at the WARWICK4 (515047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARWICK4 138.0 KV 515047 TO WFROSST4 138.0 KV 515366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WARWICK4_138kV_515047 | Apply single-phase fault on: WARWICK4 138KV 515047 TO WFROSST4 138KV 515366 CKT 1, near WARWICK4 138kV for 7 cycles with stuck breaker at WARWICK4 138kV. Clear Fault after 16 cycles and trip: WARWICK4 138KV 515047 TO BELLCOW4 138KV 515369 CKT 1 and KEYWEST4 138KV 515048 TO BELLCOW4 138KV 515369 CKT 1 and BRISTOW4 138KV 515035 TO KEYWEST4 138KV 515048 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WARWICK4_138kV_515047 | Apply single-phase fault on: WARWICK4 138KV 515047 TO WFROSST4 138KV 515366 CKT 1, near WARWICK4 138kV for 7 cycles with stuck breaker at WARWICK4 138kV. Clear Fault after 16 cycles and trip: WARWICK4 138KV 515047 TO BELLCOW4 138KV 515369 CKT 1 and KEYWEST4 138KV 515048 TO BELLCOW4 138KV 515369 CKT 1 and BRISTOW4 138KV 515035 TO KEYWEST4 138KV 515048 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WASHITA4__521088_0 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4( 521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | WASHITA4__521088_0 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4( 521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 521089 TO WASHITA2 521088 TO WASHTERT 521179 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | WASHITA4__BINGERJ4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 b.2. BINGERJ4 138.0 KV 520827 TO ONEY 4 138.0 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | WASHITA4__BINGERJ4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ONEY 4 138.0 KV 521017 TO WASHITA4 138.0 KV 521089 CKT 1 b.2. BINGERJ4 138.0 KV 520827 TO ONEY 4 138.0 KV 521017 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BLUCAN2-WTG2 (920002) trips on Voltage Protection | Disable Voltage Protection for BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | WASHITA4__SLKHILLS_4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | WASHITA4__SLKHILLS_4 | 3 Phase fault on WASHITA4 (521089) 138 kV Bus a. Apply fault at the WASHITA4 (521089) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHITA4 138.0 KV 521089 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | BCVI_WTG1 (520522) and BLUCAN2-WTG2 (920002) trip on Voltage Protection | Disable Voltage Protection for BCVI_WTG1 (520522) and BLUCAN2-WTG2 (920002)
04 - Southeast | 25S | Transfer | WATLANT2__508090_0 | 3 Phase fault on WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2( 508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATLANT2__508090_0 | 3 Phase fault on WATLANT2 (508089) 69 kV Bus a. Apply fault at the WATLANT2( 508089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT2 508089 TO WATLANT4 508090 TO WATL2-1 508046 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATLANT4__CASSTP4 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATLANT4__CASSTP4 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO CASSTP4 138.0 KV 508106 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATLANT4__WILKES_4 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATLANT4__WILKES_4 | 3 Phase fault on WATLANT4 (508090) 138 kV Bus a. Apply fault at the WATLANT4 (508090) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATLANT4 138.0 KV 508090 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATNGSW4__CALUMET4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATNGSW4__CALUMET4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATNGSW4__FAY____4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO WATONGA4 138.0 KV 521091 CKT 1 b.2. LOAD 1 521091 b.3. FAY 4 138.0 KV 520538 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATNGSW4__FAY____4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO WATONGA4 138.0 KV 521091 CKT 1 b.2. LOAD 1 521091 b.3. FAY 4 138.0 KV 520538 TO WATONGA4 138.0 KV 521091 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATNGSW4__KGFSHSW4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OMEGA 4 138.0 KV 520964 CKT 1 b.2. LOAD 1 520964 b.3. PARKCOM4 138.0 KV 520475 TO OMEGA 4 138.0 KV 520964 CKT 1 b.4. LOAD 1 520964 b.5. PARKCOM4 138.0 KV 520475 TO KGFSHSW4 138.0 KV 520533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATNGSW4__KGFSHSW4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OMEGA 4 138.0 KV 520964 CKT 1 b.2. LOAD 1 520964 b.3. PARKCOM4 138.0 KV 520475 TO OMEGA 4 138.0 KV 520964 CKT 1 b.4. LOAD 1 520964 b.5. PARKCOM4 138.0 KV 520475 TO KGFSHSW4 138.0 KV 520533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WATNGSW4__OKEENE_4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WATNGSW4__OKEENE_4 | 3 Phase fault on WATNGSW4 (520536) 138 kV Bus a. Apply fault at the WATNGSW4 (520536) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATNGSW4 138.0 KV 520536 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WAUKOTP4__SO4TH__4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WAUKOTP4__SO4TH__4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WAUKOTP4__WOODRNG4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WAUKOTP4__WOODRNG4 | 3 Phase fault on WAUKOTP4 (514711) 138 kV Bus a. Apply fault at the WAUKOTP4 (514711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WAUKOTP4 138.0 KV 514711 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WED_TAP4__CARSONT4 | 3 Phase fault on WED-TAP4 (509823) 138 kV Bus a. Apply fault at the WED-TAP4 (509823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138.0 KV 509823 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WED_TAP4__CARSONT4 | 3 Phase fault on WED-TAP4 (509823) 138 kV Bus a. Apply fault at the WED-TAP4 (509823) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WED-TAP4 138.0 KV 509823 TO CARSONT4 138.0 KV 509865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_4__509755_0 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_4__509755_0 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4( 509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 509757 TO WEKIWA-7 509755 TO WEKIW1-1 509879 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_4__GEN_2010_055 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO GEN-2010-055 138.0 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_4__GEN_2010_055 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO GEN-2010-055 138.0 KV 560389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_4__P&P_WTP4 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_4__P&P_WTP4 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO P&P WTP4 138.0 KV 509851 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_4__SILVCTYGR4 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_4__SILVCTYGR4 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO SILVCTYGR4 138.0 KV 512726 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_4__WED_TAP4 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_4__WED_TAP4 | 3 Phase fault on WEKIWA-4 (509757) 138 kV Bus a. Apply fault at the WEKIWA-4 (509757) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEKIWA-4 138.0 KV 509757 TO WED-TAP4 138.0 KV 509823 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_7__SAPLPRD7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_7__SAPLPRD7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SAPLPRD7 345.0 KV 509870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_7__SOONER_7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_7__SOONER_7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO SOONER 7 345.0 KV 514803 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WEKIWA_7__T_NO___7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WEKIWA_7__T_NO___7 | 3 Phase fault on WEKIWA-7 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 345.0 KV 509755 TO T.NO.--7 345.0 KV 509852 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WELLSPA2__ONAPA__2 | 3 Phase fault on WELLSPA2 (515215) 69 kV Bus a. Apply fault at the WELLSPA2 (515215) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELLSPA2 69.0 KV 515215 TO ONAPA 2 69.0 KV 521020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WELLSPA2__ONAPA__2 | 3 Phase fault on WELLSPA2 (515215) 69 kV Bus a. Apply fault at the WELLSPA2 (515215) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELLSPA2 69.0 KV 515215 TO ONAPA 2 69.0 KV 521020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WELSH__7__DIANA__7 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | WELSH__7__DIANA__7 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO DIANA 7 345.0 KV 508832 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | WELSH__7__WILKES_7 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | WELSH__7__WILKES_7 | 3 Phase fault on WELSH 7 (508359) 345 kV Bus a. Apply fault at the WELSH 7 (508359) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WELSH 7 345.0 KV 508359 TO WILKES 7 345.0 KV 508841 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25S | Transfer | WELSHRE4__WILKES_4 | 3 Phase fault on WELSHRE4 (508355) 138 kV Bus a. Apply fault at the WELSHRE4 (508355) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WELSHRE4__WILKES_4 | 3 Phase fault on WELSHRE4 (508355) 138 kV Bus a. Apply fault at the WELSHRE4 (508355) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WESTELC4__LEASIDE_4 | 3 Phase fault on WESTELC4 (507767) 138 kV Bus a. Apply fault at the WESTELC4 (507767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138.0 KV 507767 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WESTELC4__LEASIDE_4 | 3 Phase fault on WESTELC4 (507767) 138 kV Bus a. Apply fault at the WESTELC4 (507767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTELC4 138.0 KV 507767 TO LEASIDE 4 138.0 KV 507793 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WESTERN4__STNWAL_4 | 3 Phase fault on WESTERN4 (514869) 138 kV Bus a. Apply fault at the WESTERN4 (514869) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | WESTERN4__STNWAL_4 | 3 Phase fault on WESTERN4 (514869) 138 kV Bus a. Apply fault at the WESTERN4 (514869) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTERN4 138.0 KV 514869 TO STNWAL 4 138.0 KV 514870 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | WESTHSE4__INDNHIL4 | 3 Phase fault on WESTHSE4 (514904) 138 kV Bus a. Apply fault at the WESTHSE4 (514904) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 138.0 KV 514904 TO INDNHIL4 138.0 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WESTHSE4__INDNHIL4 | 3 Phase fault on WESTHSE4 (514904) 138 kV Bus a. Apply fault at the WESTHSE4 (514904) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTHSE4 138.0 KV 514904 TO INDNHIL4 138.0 KV 514954 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WESTMOR4__PENN___4 | 3 Phase fault on WESTMOR4 (514887) 138 kV Bus a. Apply fault at the WESTMOR4 (514887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTMOR4 138.0 KV 514887 TO PENN 4 138.0 KV 514925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | WESTMOR4__PENN___4 | 3 Phase fault on WESTMOR4 (514887) 138 kV Bus a. Apply fault at the WESTMOR4 (514887) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WESTMOR4 138.0 KV 514887 TO PENN 4 138.0 KV 514925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WFROSST4__LINCOLN4 | 3 Phase fault on WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WFROSST4__LINCOLN4 | 3 Phase fault on WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO LINCOLN4 138.0 KV 515442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WFROSST4__RSSVILE4 | 3 Phase fault on WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO RSSVILE4 138.0 KV 521107 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WFROSST4__RSSVILE4 | 3 Phase fault on WFROSST4 (515366) 138 kV Bus a. Apply fault at the WFROSST4 (515366) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WFROSST4 138.0 KV 515366 TO RSSVILE4 138.0 KV 521107 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WHITNEY2__508575_0 | 3 Phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2( 508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WHITNEY2__508575_0 | 3 Phase fault on WHITNEY2 (508574) 69 kV Bus a. Apply fault at the WHITNEY2( 508574) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY2 508574 TO WHITNEY4 508575 TO WHIT2-1 508590 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WHITNEY4__EASTEX_4 | 3 Phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WHITNEY4__EASTEX_4 | 3 Phase fault on WHITNEY4 (508575) 138 kV Bus a. Apply fault at the WHITNEY4 (508575) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITNEY4 138.0 KV 508575 TO EASTEX 4 138.0 KV 508582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WHORSE_4__HWY20_T4 | 3 Phase fault on WHORSE-4 (509754) 138 kV Bus a. Apply fault at the WHORSE-4 (509754) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138.0 KV 509754 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WHORSE_4__HWY20_T4 | 3 Phase fault on WHORSE-4 (509754) 138 kV Bus a. Apply fault at the WHORSE-4 (509754) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHORSE-4 138.0 KV 509754 TO HWY20-T4 138.0 KV 509821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WILKES_4__508841_0 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4( 508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WILKES_4__508841_0 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4( 508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILKES 4 508840 TO WILKES 7 508841 TO WILKES-1 508826 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WILKES_4__CHAPELH4 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 b.2. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WILKES_4__CHAPELH4 | 3 Phase fault on WILKES 4 (508840) 138 kV Bus a. Apply fault at the WILKES 4 (508840) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WELSHRE4 138.0 KV 508355 TO WILKES 4 138.0 KV 508840 CKT 1 b.2. CHAPELH4 138.0 KV 508337 TO WELSHRE4 138.0 KV 508355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WINDFRM4__MOORLND4 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WINDFRM4__MOORLND4 | 3 Phase fault on WINDFRM4 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 138.0 KV 515785 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOLVERN4__WOLVRNT4 | 3 Phase fault on WOLVERN4 (515056) 138 kV Bus a. Apply fault at the WOLVERN4 (515056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLVERN4 138.0 KV 515056 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOLVERN4__WOLVRNT4 | 3 Phase fault on WOLVERN4 (515056) 138 kV Bus a. Apply fault at the WOLVERN4 (515056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLVERN4 138.0 KV 515056 TO WOLVRNT4 138.0 KV 515532 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG4__514715_0 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG4__514715_0 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4( 514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 514714 TO WOODRNG7 514715 TO WOODRNG1 515770 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG4__MARSHL_4 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG4__MARSHL_4 | 3 Phase fault on WOODRNG4 (514714) 138 kV Bus a. Apply fault at the WOODRNG4 (514714) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODRNG4 138.0 KV 514714 TO MARSHL 4 138.0 KV 514733 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG4_138kV_514714 | Apply single-phase fault on: WOODRNG4 138KV 514714 TO OTTER4 138KV 514708 CKT 1, near WOODRNG4 138 kV for 7 cycles with stuck breaker at WOODRNG4 138 kV. Clear Fault after 16 cycles and trip: WOODRNG4 138KV 514714 TO FRMNTAP4 138KV 514709 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG4_138kV_514714 | Apply single-phase fault on: WOODRNG4 138KV 514714 TO OTTER4 138KV 514708 CKT 1, near WOODRNG4 138 kV for 7 cycles with stuck breaker at WOODRNG4 138 kV. Clear Fault after 16 cycles and trip: WOODRNG4 138KV 514714 TO FRMNTAP4 138KV 514709 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__GEN_2017_164 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25W | Transfer | WOODRNG7__GEN_2017_164 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO GEN-2017-164 345.0 KV 762321 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | WOODRNG7__HUNTERS7 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | WOODRNG7__HUNTERS7 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__PINTAIL7 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7__PINTAIL7 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO PINTAIL7 345.0 KV 516010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__REDNGTN7 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7__REDNGTN7 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO REDNGTN7 345.0 KV 515875 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7__SKELTON7 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7__SKELTON7 | 3 Phase fault on WOODRNG7 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 345.0 KV 514715 TO SKELTON7 345.0 KV 515990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODRNG7_345kV_514715 | Apply single-phase fault on: WOODRNG7 345KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1, near WOODRNG7 345kV for 6 cycles with stuck breaker at WOODRNG7 345kV. Clear Fault after 16 cycles and trip: WOODRNG7 345KV 514715 TO REDGNTN7 345.0 KV 515875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODRNG7_345kV_514715 | Apply single-phase fault on: WOODRNG7 345KV 514715 TO HUNTERS7 345.0 KV 515476 CKT 1, near WOODRNG7 345kV for 6 cycles with stuck breaker at WOODRNG7 345kV. Clear Fault after 16 cycles and trip: WOODRNG7 345KV 514715 TO REDGNTN7 345.0 KV 515875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WOODWRD4__WWRDEHV4 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WOODWRD4__WWRDEHV4 | 3 Phase fault on WOODWRD4 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 138.0 KV 514785 TO WWRDEHV4 138.0 KV 515376 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WRAIRPT4__PENN___4 | 3 Phase fault on WRAIRPT4 (514889) 138 kV Bus a. Apply fault at the WRAIRPT4 (514889) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRAIRPT4 138.0 KV 514889 TO PENN 4 138.0 KV 514925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WRAIRPT4__PENN___4 | 3 Phase fault on WRAIRPT4 (514889) 138 kV Bus a. Apply fault at the WRAIRPT4 (514889) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRAIRPT4 138.0 KV 514889 TO PENN 4 138.0 KV 514925 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WRN_MED4__WRNMEDT4 | 3 Phase fault on WRN-MED4 (509729) 138 kV Bus a. Apply fault at the WRN-MED4 (509729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRN-MED4 138.0 KV 509729 TO WRNMEDT4 138.0 KV 509764 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WRN_MED4__WRNMEDT4 | 3 Phase fault on WRN-MED4 (509729) 138 kV Bus a. Apply fault at the WRN-MED4 (509729) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRN-MED4 138.0 KV 509729 TO WRNMEDT4 138.0 KV 509764 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WRNMEDT4__81YALTP4 | 3 Phase fault on WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138.0 KV 509764 TO 81YALTP4 138.0 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WRNMEDT4__81YALTP4 | 3 Phase fault on WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138.0 KV 509764 TO 81YALTP4 138.0 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WRNMEDT4__S_HUD__4 | 3 Phase fault on WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138.0 KV 509764 TO S.HUD.-4 138.0 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WRNMEDT4__S_HUD__4 | 3 Phase fault on WRNMEDT4 (509764) 138 kV Bus a. Apply fault at the WRNMEDT4 (509764) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WRNMEDT4 138.0 KV 509764 TO S.HUD.-4 138.0 KV 509833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWDBORDT_345kV_755000 | Apply single-phase fault on: WWDBORDT 345KV 755000 TO CHISHOLM7 345KV 511553 CKT 1, near WWDBORDT 345 kV for 6 cycles with stuck breaker at WWDBORDT 345 kV. Clear Fault after 16 cycles and trip: BORDER7 345KV 515458 TO WWDBORDT 345KV 755000 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWDBORDT_345kV_755000 | Apply single-phase fault on: WWDBORDT 345KV 755000 TO CHISHOLM7 345KV 511553 CKT 1, near WWDBORDT 345 kV for 6 cycles with stuck breaker at WWDBORDT 345 kV. Clear Fault after 16 cycles and trip: BORDER7 345KV 515458 TO WWDBORDT 345KV 755000 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | WWRDEHV4__KEENAN_4 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25W | Transfer | WWRDEHV4__KEENAN_4 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO KEENAN 4 138.0 KV 515394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | WWRDEHV4__OUSPRT_4 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25W | Transfer | WWRDEHV4__OUSPRT_4 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO OUSPRT 4 138.0 KV 515398 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | WWRDEHV4__WWDPST_4 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | WWRDEHV4__WWDPST_4 | 3 Phase fault on WWRDEHV4 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 138.0 KV 515376 TO WWDPST 4 138.0 KV 515425 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.1
04 - Southeast | 25S | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25W | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.1. Remove Reclose
04 - Southeast | 25S | Transfer | WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.1
04 - Southeast | 25S | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.1
04 - Southeast | 25S | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.1
04 - Southeast | 25S | Transfer | WWRDEHV7__WWDBORDT | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | WWRDEHV7__WWDBORDT | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.1
04 - Southeast | 25W | Transfer | WWRDEHV7_345kV_515375 | Apply single-phase fault on: WWRDEHV7 345KV 515375 TO DGRASSE7 345KV 515852 CKT 1, near WWRDEHV7 345 kV for 6 cycles with stuck breaker at WWRDEHV7 345 kV. Clear Fault after 16 cycles and trip: WWRDEHV7 345KV 515375 TO TATONGA7 345KV 515407 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | WWRDEHV7_345kV_515375 | Apply single-phase fault on: WWRDEHV7 345KV 515375 TO DGRASSE7 345KV 515852 CKT 1, near WWRDEHV7 345 kV for 6 cycles with stuck breaker at WWRDEHV7 345 kV. Clear Fault after 16 cycles and trip: WWRDEHV7 345KV 515375 TO TATONGA7 345KV 515407 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | YOAKUM_345__CROSSROADS_7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | YOAKUM_345__CROSSROADS_7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | YUKON__2__ELRENO_2 | 3 Phase fault on YUKON 2 (514816) 69 kV Bus a. Apply fault at the YUKON 2 (514816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUKON 2 69.0 KV 514816 TO SVCELRN2 69.0 KV 514817 CKT 1 b.2. LOAD 1 514817 b.3. SVCELRN2 69.0 KV 514817 TO ELRENO 2 69.0 KV 514818 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | YUKON__2__ELRENO_2 | 3 Phase fault on YUKON 2 (514816) 69 kV Bus a. Apply fault at the YUKON 2 (514816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUKON 2 69.0 KV 514816 TO SVCELRN2 69.0 KV 514817 CKT 1 b.2. LOAD 1 514817 b.3. SVCELRN2 69.0 KV 514817 TO ELRENO 2 69.0 KV 514818 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | YUKON__2__MSTANG_2 | 3 Phase fault on YUKON 2 (514816) 69 kV Bus a. Apply fault at the YUKON 2 (514816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUKON 2 69.0 KV 514816 TO MSTANG 2 69.0 KV 514860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | YUKON__2__MSTANG_2 | 3 Phase fault on YUKON 2 (514816) 69 kV Bus a. Apply fault at the YUKON 2 (514816) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YUKON 2 69.0 KV 514816 TO MSTANG 2 69.0 KV 514860 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | 7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | 7_RIVERS___6__528094_0 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6( 528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 528095 TO 7-RIVERS 3 528094 TO 7-RIVER_TR11 528090 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | 7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | 7_RIVERS___6__PECOS______6 | 3 Phase fault on 7-RIVERS 6 (528095) 230 kV Bus a. Apply fault at the 7-RIVERS 6 (528095) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 7-RIVERS 6 230.0 KV 528095 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | AMA_SOUTH__6__SWISHER____6 | 3 Phase fault on AMA_SOUTH 6 (524415) 230 kV Bus a. Apply fault at the AMA_SOUTH 6 (524415) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMA_SOUTH 6 230.0 KV 524415 TO SWISHER 6 230.0 KV 525213 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | AMOCO_SS___6__YOAKUM_____6 | 3 Phase fault on AMOCO_SS 6 (526460) 230 kV Bus a. Apply fault at the AMOCO_SS 6 (526460) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | AMOCO_SS___6__YOAKUM_____6 | 3 Phase fault on AMOCO_SS 6 (526460) 230 kV Bus a. Apply fault at the AMOCO_SS 6 (526460) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AMOCO_SS 6 230.0 KV 526460 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ANDREWS____3__NA_ENRICH__3 | 3 Phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ANDREWS____3__NA_ENRICH__3 | 3 Phase fault on ANDREWS 3 (528602) 115 kV Bus a. Apply fault at the ANDREWS 3 (528602) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 3 115.0 KV 528602 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ANDREWS____6__528602_0 | 3 Phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply fault at the ANDREWS 6( 528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 6 528604 TO ANDREWS 3 528602 TO ANDREWS_TR11 528601 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ANDREWS____6__528602_0 | 3 Phase fault on ANDREWS 6 (528604) 230 kV Bus a. Apply fault at the ANDREWS 6( 528604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDREWS 6 528604 TO ANDREWS 3 528602 TO ANDREWS_TR11 528601 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BLCKRVR_DST3__CHINA_DRAW_3 | 3 Phase fault on BLCKRVR_DST3 (528206) 115 kV Bus a. Apply fault at the BLCKRVR_DST3 (528206) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLCKRVR_DST3 115.0 KV 528206 TO CHINA_DRAW 3 115.0 KV 528222 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BORDER_____7__WWDBORDT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BORDER_____7__WWDBORDT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BORDER7_345kV_515458 | Apply single-phase fault on: BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, near BORDER7 345kV for 6 cycles with stuck breaker at BORDER7 345kV. Clear Fault after 16 cycles and trip: BORDER7 345KV 515458 TO WWDBORDT 345KV 755000 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BORDER7_345kV_515458 | Apply single-phase fault on: BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, near BORDER7 345kV for 6 cycles with stuck breaker at BORDER7 345kV. Clear Fault after 16 cycles and trip: BORDER7 345KV 515458 TO WWDBORDT 345KV 755000 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BUCKEYE_TP_3__BUCKEYE____3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO BUCKEYE 3 115.0 KV 528385 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BUCKEYE_TP_3__LE_TXACO_TP3 | 3 Phase fault on BUCKEYE_TP 3 (528348) 115 kV Bus a. Apply fault at the BUCKEYE_TP 3 (528348) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUCKEYE_TP 3 115.0 KV 528348 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BUSHLAND6_230kV_524267 | Apply single-phase fault on: POTTERCO6 230.0 KV 523959 TO BUSHLAND6 230.0 KV 524267 CKT 1, near BUSHLAND6 230kV for 7 cycles with stuck breaker at BUSHLAND6 230kV. Clear Fault after 16 cycles and trip: BUSHLAND6 230.0 KV 524267 TO DEAFSMITH6 230.0 KV 524623 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BUSHLAND6_230kV_524267 | Apply single-phase fault on: POTTERCO6 230.0 KV 523959 TO BUSHLAND6 230.0 KV 524267 CKT 1, near BUSHLAND6 230kV for 7 cycles with stuck breaker at BUSHLAND6 230kV. Clear Fault after 16 cycles and trip: BUSHLAND6 230.0 KV 524267 TO DEAFSMITH6 230.0 KV 524623 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | BYRD_TP____3__BYRD_______3 | 3 Phase fault on BYRD_TP 3 (528581) 115 kV Bus a. Apply fault at the BYRD_TP 3 (528581) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BYRD_TP 3 115.0 KV 528581 TO BYRD 3 115.0 KV 528582 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARDINAL___3__TARGA______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARDINAL___3__TARGA______3 | 3 Phase fault on CARDINAL 3 (528596) 115 kV Bus a. Apply fault at the CARDINAL 3 (528596) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARLISLE___6__526160_0 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6( 526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 526161 TO CARLISLE 3 526160 TO CRLSLE_TR1 1 526157 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CARLISLE___6__WOLFFORTH__6 | 3 Phase fault on CARLISLE 6 (526161) 230 kV Bus a. Apply fault at the CARLISLE 6 (526161) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARLISLE 6 230.0 KV 526161 TO WOLFFORTH 6 230.0 KV 526525 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHAVES_CNTY6__527482_0 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHAVES_CNTY6__527482_0 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6( 527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 527483 TO CHAVES_CNTY3 527482 TO CHAVES_TR2 1 527479 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHAVES_CNTY6__EDDY_NORTH_6 | 3 Phase fault on CHAVES_CNTY6 (527483) 230 kV Bus a. Apply fault at the CHAVES_CNTY6 (527483) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAVES_CNTY6 230.0 KV 527483 TO EDDY_NORTH 6 230.0 KV 527799 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHINA_DRAW_3__CD_SVC_HV__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CD_SVC_HV 3 115.0 KV 528225 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHINA_DRAW_3__CHVRN_EDDYS3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO CHVRN_EDDYS3 115.0 KV 528252 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHINA_DRAW_3__WOOD_DRAW__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHINA_DRAW_3__WOOD_DRAW__3 | 3 Phase fault on CHINA_DRAW 3 (528222) 115 kV Bus a. Apply fault at the CHINA_DRAW 3 (528222) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHINA_DRAW 3 115.0 KV 528222 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHINA_DRAW_7__528222_0 | 3 Phase fault on CHINA_DRAW 7 (528223) 345 kV Bus a. Apply fault at the CHINA_DRAW 7( 528223) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHINA_DRAW 7 528223 TO CHINA_DRAW 3 528222 TO CHINA_DRAW 1 528219 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | CHISHOLM7__WWDBORDT | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | CHISHOLM7__WWDBORDT | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | COOPER_RNCH3__BYRD_TP____3 | 3 Phase fault on COOPER_RNCH3 (528554) 115 kV Bus a. Apply fault at the COOPER_RNCH3 (528554) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER_RNCH3 115.0 KV 528554 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CROSSROADS_345kV_527656 | Apply single-phase fault on: CROSSROADS7 345KV 527656 TO EDDYCNTY7 345.0 KV 527802 CKT 1, near CROSSROADS 345kV for 6 cycles with stuck breaker at CROSSROADS 345kV. Clear Fault after 16 cycles and trip: TOLK7 345KV 525549 TO CROSSROADS7 345KV 527656 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CROSSROADS_345kV_527656 | Apply single-phase fault on: CROSSROADS7 345KV 527656 TO EDDYCNTY7 345.0 KV 527802 CKT 1, near CROSSROADS 345kV for 6 cycles with stuck breaker at CROSSROADS 345kV. Clear Fault after 16 cycles and trip: TOLK7 345KV 525549 TO CROSSROADS7 345KV 527656 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CROSSROADS_7__EDDY_CNTY__7 | 3 Phase fault on CROSSROADS 7 (527656) 345 kV Bus a. Apply fault at the CROSSROADS 7 (527656) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CROSSROADS 7 345.0 KV 527656 TO EDDY_CNTY 7 345.0 KV 527802 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNIGHM_N_6__POTASH_JCT_6 | 3 Phase fault on CUNNIGHM_N 6 (527865) 230 kV Bus a. Apply fault at the CUNNIGHM_N 6 (527865) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_N 6 230.0 KV 527865 TO POTASH_JCT 6 230.0 KV 527963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNIGHM_S_6__527864_0 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNIGHM_S_6__527864_0 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6( 527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 527867 TO CUNNINHAM 3 527864 TO CUNNHM_TR1 1 527863 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNIGHM_S_6__HOBBS_INT__6 | 3 Phase fault on CUNNIGHM_S 6 (527867) 230 kV Bus a. Apply fault at the CUNNIGHM_S 6 (527867) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNIGHM_S 6 230.0 KV 527867 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Cunningham_115kV_527864 | Apply single-phase fault on: Cunningham 115KV 527864 TO Monument TP 115KV 528568 CKT 1, near CUNNINHAM 3 115 kV for 7 cycles with stuck breaker at CUNNINHAM 3 115 kV. Clear Fault after 16 cycles and trip: Cunningham 115KV 527864 TO Quahada 115KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Cunningham_115kV_527864 | Apply single-phase fault on: Cunningham 115KV 527864 TO Monument TP 115KV 528568 CKT 1, near CUNNINHAM 3 115 kV for 7 cycles with stuck breaker at CUNNINHAM 3 115 kV. Clear Fault after 16 cycles and trip: Cunningham 115KV 527864 TO Quahada 115KV 528394 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM__3__BUCKEYE_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO BUCKEYE_TP 3 115.0 KV 528348 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM__3__HOBBS_INT__3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO HOBBS_INT 3 115.0 KV 527891 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM__3__MADDOX_____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM__3__MONUMNT_TP_3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO MONUMNT_TP 3 115.0 KV 528568 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUNNINHAM__3__QUAHADA____3 | 3 Phase fault on CUNNINHAM 3 (527864) 115 kV Bus a. Apply fault at the CUNNINHAM 3 (527864) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUNNINHAM 3 115.0 KV 527864 TO QUAHADA 3 115.0 KV 528394 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUSTERMTN__3__PONDEROSA__3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO PONDEROSA 3 115.0 KV 528240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | CUSTERMTN__3__WHITTEN____3 | 3 Phase fault on CUSTERMTN 3 (528239) 115 kV Bus a. Apply fault at the CUSTERMTN 3 (528239) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CUSTERMTN 3 115.0 KV 528239 TO WHITTEN 3 115.0 KV 528540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DCP_ZIA_TP_3__DCP_ZIA____3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DCP_ZIA TP 3 115.0 KV 528422 TO DCP_ZIA 3 115.0 KV 528423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DCP_ZIA_TP_3__MALJMAR1&2_3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 b.2. MALJMAR1&2 3 115.0 KV 528406 TO ZIA 3 115.0 KV 528420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DCP_ZIA_TP_3__MALJMAR1&2_3 | 3 Phase fault on DCP_ZIA TP 3 (528422) 115 kV Bus a. Apply fault at the DCP_ZIA TP 3 (528422) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ZIA 3 115.0 KV 528420 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 b.2. MALJMAR1&2 3 115.0 KV 528406 TO ZIA 3 115.0 KV 528420 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DEAFSMITH6_230kV_524623 | Apply single-phase fault on: DEAFSMITH6 230.0 KV 524623 TO G17146TAP 230.0 KV 760498 CKT 1, near DEAFSMITH6 230kV for 7 cycles with stuck breaker at DEAFSMITH6 230kV. Clear Fault after 16 cycles and trip: BUSHLAND6 230.0 KV 524267 TO DEAFSMITH6 230.0 KV 524623 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DEAFSMITH6_230kV_524623 | Apply single-phase fault on: DEAFSMITH6 230.0 KV 524623 TO G17146TAP 230.0 KV 760498 CKT 1, near DEAFSMITH6 230kV for 7 cycles with stuck breaker at DEAFSMITH6 230kV. Clear Fault after 16 cycles and trip: BUSHLAND6 230.0 KV 524267 TO DEAFSMITH6 230.0 KV 524623 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DENVER_N___3__527125_0 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3( 527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 527130 TO DENVER_CTY 2 527125 TO DNVER_N_TR11 527122 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DENVER_N___3__MUSTANG____3 | 3 Phase fault on DENVER_N 3 (527130) 115 kV Bus a. Apply fault at the DENVER_N 3 (527130) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVER_N 3 115.0 KV 527130 TO MUSTANG 3 115.0 KV 527146 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DIAMONDBACK2_69kV_527211 | Apply single-phase fault on: DIAMONBACK2 69.0 KV 527211 TO OXYCEDRLKE2 69.0 KV 527250 CKT 1 and CEDARLAKE2 69.0 KV 527247 TO OXYCEDRLKE2 69.0 KV 527250 CKT 1, near DIAMONDBACK2 69kV for 7 cycles with stuck breaker at DIAMONDBACK2 69kV. Clear Fault after 16 cycles and trip: DIAMONBACK2 69.0 KV 527211 TO OZRKMAH02 69.0 KV 527229 CKT 1 and OZRKMAH02 69.0 KV 527229 TO LGSAWYERFL2 69.0 KV 527305 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DIAMONDBACK2_69kV_527211 | Apply single-phase fault on: DIAMONBACK2 69.0 KV 527211 TO OXYCEDRLKE2 69.0 KV 527250 CKT 1 and CEDARLAKE2 69.0 KV 527247 TO OXYCEDRLKE2 69.0 KV 527250 CKT 1, near DIAMONDBACK2 69kV for 7 cycles with stuck breaker at DIAMONDBACK2 69kV. Clear Fault after 16 cycles and trip: DIAMONBACK2 69.0 KV 527211 TO OZRKMAH02 69.0 KV 527229 CKT 1 and OZRKMAH02 69.0 KV 527229 TO LGSAWYERFL2 69.0 KV 527305 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DRINKARD___3__NA_ENRICH__3 | 3 Phase fault on DRINKARD 3 (528589) 115 kV Bus a. Apply fault at the DRINKARD 3 (528589) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DRINKARD___3__NA_ENRICH__3 | 3 Phase fault on DRINKARD 3 (528589) 115 kV Bus a. Apply fault at the DRINKARD 3 (528589) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD 3 115.0 KV 528589 TO NA_ENRICH 3 115.0 KV 528603 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | DRINKARD_TP3__DRINKARD___3 | 3 Phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | DRINKARD_TP3__DRINKARD___3 | 3 Phase fault on DRINKARD_TP3 (528533) 115 kV Bus a. Apply fault at the DRINKARD_TP3 (528533) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRINKARD_TP3 115.0 KV 528533 TO DRINKARD 3 115.0 KV 528589 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EAGLE_CREEK3__EDDY_NTH___3 | 3 Phase fault on EAGLE_CREEK3 (527711) 115 kV Bus a. Apply fault at the EAGLE_CREEK3 (527711) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EAGLE_CREEK3 115.0 KV 527711 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_CNTY__7__527799_0 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7( 527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 527802 TO EDDY_NORTH 6 527799 TO EDDY_TR 1 527796 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_CNTY__7__KIOWA______7 | 3 Phase fault on EDDY_CNTY 7 (527802) 345 kV Bus a. Apply fault at the EDDY_CNTY 7 (527802) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EDDY_CNTY 7 345.0 KV 527802 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_NORTH_6__527793_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_STH 3 527793 TO EDDY_TR3 1 527795 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_NORTH_6__527798_0 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6( 527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 527799 TO EDDY_NTH 3 527798 TO EDDY_TR2 1 527797 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_NORTH_6__7_RIVERS___6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO 7-RIVERS 6 230.0 KV 528095 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_NORTH_6__CUNNIGHM_N_6 | 3 Phase fault on EDDY_NORTH 6 (527799) 230 kV Bus a. Apply fault at the EDDY_NORTH 6 (527799) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NORTH 6 230.0 KV 527799 TO CUNNIGHM_N 6 230.0 KV 527865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_NTH___3__CV_8_MILE__3 | 3 Phase fault on EDDY_NTH 3 (527798) 115 kV Bus a. Apply fault at the EDDY_NTH 3 (527798) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_NTH 3 115.0 KV 527798 TO CV-8_MILE 3 115.0 KV 527809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_STH___3__CV_DAYTON_+3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_STH___3__CV_DAYTON_+3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO CV-DAYTON +3 115.0 KV 527821 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDY_STH___3__PECOS______3 | 3 Phase fault on EDDY_STH 3 (527793) 115 kV Bus a. Apply fault at the EDDY_STH 3 (527793) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDDY_STH 3 115.0 KV 527793 TO PECOS 3 115.0 KV 528178 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EDDYCNTY7_345kV_527802 | Apply single-phase fault on: CROSSROADS7 345KV 527656 TO EDDYCNTY7 345.0 KV 527802 CKT 1, near EDDYCNTY7 345kV for 6 cycles with stuck breaker at EDDYCNTY7 345kV. Clear Fault after 16 cycles and trip: EDDYCNTY7 345.0 KV 527802 TO KIOWA 345KV 527965 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EDDYCNTY7_345kV_527802 | Apply single-phase fault on: CROSSROADS7 345KV 527656 TO EDDYCNTY7 345.0 KV 527802 CKT 1, near EDDYCNTY7 345kV for 6 cycles with stuck breaker at EDDYCNTY7 345kV. Clear Fault after 16 cycles and trip: EDDYCNTY7 345.0 KV 527802 TO KIOWA 345KV 527965 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EL_PASO____3__DENVER_N___3 | 3 Phase fault on EL_PASO 3 (527080) 115 kV Bus a. Apply fault at the EL_PASO 3 (527080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL_PASO 3 115.0 KV 527080 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ENRON_TP___3__ENRON______3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO ENRON 3 115.0 KV 528318 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ENRON_TP___3__LEA_NATIONL3 | 3 Phase fault on ENRON_TP 3 (528317) 115 kV Bus a. Apply fault at the ENRON_TP 3 (528317) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ENRON_TP 3 115.0 KV 528317 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EUNICE_____3__CARDINAL___3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | EUNICE_____3__DRINKARD_TP3 | 3 Phase fault on EUNICE 3 (528512) 115 kV Bus a. Apply fault at the EUNICE 3 (528512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUNICE 3 115.0 KV 528512 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | FLOYD_CNTY_3__TUCO_INT___3 | 3 Phase fault on FLOYD_CNTY 3 (525780) 115 kV Bus a. Apply fault at the FLOYD_CNTY 3 (525780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOYD_CNTY 3 115.0 KV 525780 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G16_037_TAP__GEN_2016_037 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2016-037 345.0 KV 587230 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G16_037_TAP__GEN_2018_021 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2018-021 345.0 KV 762570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
05 - Southwest | 25W | Transfer | G16_037_TAP__GEN_2018_021 | 3 Phase fault on G16-037-TAP (560078) 345 kV Bus a. Apply fault at the G16-037-TAP (560078) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-037-TAP 345.0 KV 560078 TO GEN-2018-021 345.0 KV 762570 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded | Remove Reclose
05 - Southwest | 25S | Transfer | G16_091_TAP__GEN_2016_095 | 3 Phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345.0 KV 587744 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G16_091_TAP__GEN_2016_095 | 3 Phase fault on G16-091-TAP (587744) 345 kV Bus a. Apply fault at the G16-091-TAP (587744) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-091-TAP 345.0 KV 587744 TO GEN-2016-095 345.0 KV 587770 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G17_151TAP__G18_015_TAP | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G17_151TAP__GEN_2017_151 | 3 Phase fault on G17-151TAP (762216) 345 kV Bus a. Apply fault at the G17-151TAP (762216) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-151TAP 345.0 KV 762216 TO GEN-2017-151 345.0 KV 762217 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | G17_171_TAP__GEN_2017_171 | 3 Phase fault on G17-171-TAP (760938) 345 kV Bus a. Apply fault at the G17-171-TAP (760938) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-171-TAP 345.0 KV 760938 TO GEN-2017-171 345.0 KV 760939 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GAINES_____3__OXY_WSEM_TP3 | 3 Phase fault on GAINES 3 (527322) 115 kV Bus a. Apply fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAINES 3 115.0 KV 527322 TO OXY_WSEM_TP3 115.0 KV 527325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GAINES_____3__OXY_WSEM_TP3 | 3 Phase fault on GAINES 3 (527322) 115 kV Bus a. Apply fault at the GAINES 3 (527322) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GAINES 3 115.0 KV 527322 TO OXY_WSEM_TP3 115.0 KV 527325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2016_091__G16_091_TAP | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2016_091__G16_091_TAP | 3 Phase fault on GEN-2016-091 (587740) 345 kV Bus a. Apply fault at the GEN-2016-091 (587740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2016-091 345.0 KV 587740 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25W | Transfer | GEN_2018_004__G18_004_TAP | 3 Phase fault on GEN-2018-004 (762438) 115 kV Bus a. Apply fault at the GEN-2018-004 (762438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GEN-2018-004 115.0 KV 762438 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GEN_2018_015__G18_015_TAP | 3 Phase fault on GEN-2018-015 (762460) 345 kV Bus a. Apply fault at the GEN-2018-015 (762460) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEN-2018-015 345.0 KV 762460 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRACMNT4__515800_0 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4( 515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 515802 TO GRACMNT7 515800 TO GRCMNT11 515801 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRACMNT4__ANADARK4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO ANADARK4 138.0 KV 520814 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRACMNT4__WASHITA4 | 3 Phase fault on GRACMNT4 (515802) 138 kV Bus a. Apply fault at the GRACMNT4 (515802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRACMNT4 138.0 KV 515802 TO WASHITA4 138.0 KV 521089 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRACMNT7__G16_037_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRACMNT7__G16_091_TAP | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | GRACMNT7__GEN_2015_093 | 3 Phase fault on GRACMNT7 (515800) 345 kV Bus a. Apply fault at the GRACMNT7 (515800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRACMNT7 345.0 KV 515800 TO GEN-2015-093 345.0 KV 563269 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HALE_CNTY__3__TUCO_INT___3 | 3 Phase fault on HALE_CNTY 3 (525454) 115 kV Bus a. Apply fault at the HALE_CNTY 3 (525454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALE_CNTY 3 115.0 KV 525454 TO TUCO_INT 3 115.0 KV 525828 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HIGG_______3__DENVER_N___3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 b.2. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HIGG_______3__DENVER_N___3 | 3 Phase fault on HIGG 3 (527363) 115 kV Bus a. Apply fault at the HIGG 3 (527363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HIGGEAST 3 115.0 KV 527286 TO HIGG 3 115.0 KV 527363 CKT 1 b.2. DENVER_N 3 115.0 KV 527130 TO HIGGEAST 3 115.0 KV 527286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25W | Transfer | HOBBS_INT__3__HIGG_______3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO BENSING 3 115.0 KV 528433 CKT 1 b.2. LOAD 1 528433 b.3. LOAD 1* 528433 b.4. HIGG 3 115.0 KV 527363 TO BENSING 3 115.0 KV 528433 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25S | Transfer | HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25W | Transfer | HOBBS_INT__3__LE_WEST_SUB3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO LE-WEST_SUB3 115.0 KV 528333 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25S | Transfer | HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25W | Transfer | HOBBS_INT__3__MADDOX_____3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MADDOX 3 115.0 KV 528355 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25S | Transfer | HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25W | Transfer | HOBBS_INT__3__MILLEN_TPW_3 | 3 Phase fault on HOBBS_INT 3 (527891) 115 kV Bus a. Apply fault at the HOBBS_INT 3 (527891) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 3 115.0 KV 527891 TO MILLEN_TPW 3 115.0 KV 528434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25S | Transfer | HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HOBBS_INT__6__527891_0 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6( 527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 527894 TO HOBBS_INT 3 527891 TO HOBBS_TR1 1 527890 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__6__ANDREWS____6 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 230.0 KV 527894 TO ANDREWS 6 230.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HOBBS_INT__6__ANDREWS____6 | 3 Phase fault on HOBBS_INT 6 (527894) 230 kV Bus a. Apply fault at the HOBBS_INT 6 (527894) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOBBS_INT 6 230.0 KV 527894 TO ANDREWS 6 230.0 KV 528604 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HOBBS_INT__7__527894_0 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7( 527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 527896 TO HOBBS_INT 6 527894 TO HOBBS_TR3 1 527895 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | HOBBS_INT__7__KIOWA______7 | 3 Phase fault on HOBBS_INT 7 (527896) 345 kV Bus a. Apply fault at the HOBBS_INT 7 (527896) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOBBS_INT 7 345.0 KV 527896 TO KIOWA 7 345.0 KV 527965 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Hobbs_Int_115kV_527891 | Apply single-phase fault on: Cunningham 115KV 527864 TO Hobbs Int 115KV 527891 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 16 cycles and trip: Maddox 115KV 528355 TO Hobbs Int 115KV 527891 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Hobbs_Int_115kV_527891 | Apply single-phase fault on: Cunningham 115KV 527864 TO Hobbs Int 115KV 527891 CKT 1, near HOBBS_INT 3 115 kV for 7 cycles with stuck breaker at HOBBS_INT 3 115 kV. Clear Fault after 16 cycles and trip: Maddox 115KV 528355 TO Hobbs Int 115KV 527891 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | IMC_#1_TP__3__XTO_DI9_TP_3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | IMC_#1_TP__3__XTO_DI9_TP_3 | 3 Phase fault on IMC_#1_TP 3 (528035) 115 kV Bus a. Apply fault at the IMC_#1_TP 3 (528035) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. IMC_#1_TP 3 115.0 KV 528035 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | ASGI-2016-008 trips on Voltage Protection | Disable Voltage Protection for ASGI-2016-008
05 - Southwest | 25W | Transfer | INK_BASIN__3__LE_WAITS___3 | 3 Phase fault on INK_BASIN 3 (527027) 115 kV Bus a. Apply fault at the INK_BASIN 3 (527027) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 3 115.0 KV 527027 TO LE-WAITS 3 115.0 KV 528325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | ASGI-2016-008 trips on Voltage Protection | Disable Voltage Protection for ASGI-2016-008
05 - Southwest | 25S | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | INK_BASIN__6__HOBBS_INT__6 | 3 Phase fault on INK_BASIN 6 (527028) 230 kV Bus a. Apply fault at the INK_BASIN 6 (527028) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INK_BASIN 6 230.0 KV 527028 TO HOBBS_INT 6 230.0 KV 527894 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JOHNCO_7__SUNNYSD7 | 3 Phase fault on JOHNCO 7 (514809) 345 kV Bus a. Apply fault at the JOHNCO 7 (514809) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JOHNCO 7 345.0 KV 514809 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNSON_DRW3__AM_FRAC____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 b.2. AM_FRAC 3 115.0 KV 527300 TO MAPCO 3 115.0 KV 527360 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JOHNSON_DRW3__AM_FRAC____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAPCO 3 115.0 KV 527360 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 b.2. AM_FRAC 3 115.0 KV 527300 TO MAPCO 3 115.0 KV 527360 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JOHNSON_DRW3__HIGG_______3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JOHNSON_DRW3__TAYLOR_____3 | 3 Phase fault on JOHNSON_DRW3 (527362) 115 kV Bus a. Apply fault at the JOHNSON_DRW3 (527362) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JOHNSON_DRW3 115.0 KV 527362 TO TAYLOR 3 115.0 KV 528413 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JONES______6__GRASSLAND__6 | 3 Phase fault on JONES 6 (526337) 230 kV Bus a. Apply fault at the JONES 6 (526337) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 6 230.0 KV 526337 TO GRASSLAND 6 230.0 KV 526677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | JONES6_230kV_526337 | Apply single-phase fault on: TUCOINT6 230.0 KV 525830 TO JONES6 230.0 KV 526337 CKT 1, near JONES6 230kV for 7 cycles with stuck breaker at JONES6 230kV. Clear Fault after 16 cycles and trip: LUBBCKSTH6 230.0 KV 526269 TO JONES6 230.0 KV 526337 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | JONES6_230kV_526337 | Apply single-phase fault on: TUCOINT6 230.0 KV 525830 TO JONES6 230.0 KV 526337 CKT 1, near JONES6 230kV for 7 cycles with stuck breaker at JONES6 230kV. Clear Fault after 16 cycles and trip: LUBBCKSTH6 230.0 KV 526269 TO JONES6 230.0 KV 526337 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KIOWA______7__527966_0 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7( 527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 527965 TO KIOWA 3 527966 TO KIOWA_TR1 1 527964 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KIOWA______7__N_LOVING___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO N_LOVING 7 345.0 KV 528185 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | KIOWA______7__RDRUNNER___7 | 3 Phase fault on KIOWA 7 (527965) 345 kV Bus a. Apply fault at the KIOWA 7 (527965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KIOWA 7 345.0 KV 527965 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__2__511467_0 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2( 511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 511466 TO L.E.S.-4 511467 TO LES#1-1 511416 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__2__LGORE_N2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__2__LGORE_N2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-N2 69.0 KV 511469 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__2__LGORE_S2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__2__LGORE_S2 | 3 Phase fault on L.E.S.-2 (511466) 69 kV Bus a. Apply fault at the L.E.S.-2 (511466) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-2 69.0 KV 511466 TO LGORE-S2 69.0 KV 511470 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__4__511468_0 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4( 511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 511467 TO L.E.S.-7 511468 TO LES#4-1 511414 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__4__ARTVLTP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO SHERID4 138.0 KV 511474 CKT 1 b.2. LOAD 1 511474 b.3. SHERID4 138.0 KV 511474 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__4__COMMTAP4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__4__ELGINJT4 | 3 Phase fault on L.E.S.-4 (511467) 138 kV Bus a. Apply fault at the L.E.S.-4 (511467) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. L.E.S.-4 138.0 KV 511467 TO ELGINJT4 138.0 KV 511486 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__7__G16_091_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G16-091-TAP 345.0 KV 587744 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | L_E_S__7__G17_171_TAP | 3 Phase fault on L.E.S.-7 (511468) 345 kV Bus a. Apply fault at the L.E.S.-7 (511468) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. L.E.S.-7 345.0 KV 511468 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_ERF_____3__528774_0 | 3 Phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply fault at the LE-ERF 3( 528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-ERF 3 528775 TO LE-ERF 2 528774 TO LE-ERF_TR 1 528773 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_ERF_____3__528774_0 | 3 Phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply fault at the LE-ERF 3( 528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-ERF 3 528775 TO LE-ERF 2 528774 TO LE-ERF_TR 1 528773 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_ERF_____3__LE_TALLCOTN3 | 3 Phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-ERF 3 115.0 KV 528775 TO LE-TALLCOTN3 115.0 KV 528779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_ERF_____3__LE_TALLCOTN3 | 3 Phase fault on LE-ERF 3 (528775) 115 kV Bus a. Apply fault at the LE-ERF 3 (528775) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-ERF 3 115.0 KV 528775 TO LE-TALLCOTN3 115.0 KV 528779 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_LOVINTON2__LE_DSYSRPOI2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-DSYSRPOI2 69.0 KV 528677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_LOVINTON2__LE_DSYSRPOI2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-DSYSRPOI2 69.0 KV 528677 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_LOVINTON2__LE_FAMARISS2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-FAMARISS2 69.0 KV 528675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_LOVINTON2__LE_FAMARISS2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-FAMARISS2 69.0 KV 528675 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_LOVINTON2__LE_GRAY____2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-GRAY 2 69.0 KV 528699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_LOVINTON2__LE_GRAY____2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-GRAY 2 69.0 KV 528699 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_LOVINTON2__LE_SAUNDRTP2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-SAUNDRTP2 69.0 KV 528638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_LOVINTON2__LE_SAUNDRTP2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-SAUNDRTP2 69.0 KV 528638 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_LOVINTON2__LE_TATMGOAB2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-TATMGOAB2 69.0 KV 528679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_LOVINTON2__LE_TATMGOAB2 | 3 Phase fault on LE-LOVINTON2 (528618) 69 kV Bus a. Apply fault at the LE-LOVINTON2 (528618) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-LOVINTON2 69.0 KV 528618 TO LE-TATMGOAB2 69.0 KV 528679 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_SANANDRS3__LE_TXACO_TP3 | 3 Phase fault on LE-SANANDRS3 (528341) 115 kV Bus a. Apply fault at the LE-SANANDRS3 (528341) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-SANANDRS3 115.0 KV 528341 TO LE-TXACO_TP3 115.0 KV 528627 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_TXACO_TP3__LE_TEXACO__3 | 3 Phase fault on LE-TXACO_TP3 (528627) 115 kV Bus a. Apply fault at the LE-TXACO_TP3 (528627) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-TXACO_TP3 115.0 KV 528627 TO LE-TEXACO 3 115.0 KV 528792 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_WAITS___3__LE_NRTH_INT3 | 3 Phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3 115.0 KV 528325 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_WAITS___3__LE_NRTH_INT3 | 3 Phase fault on LE-WAITS 3 (528325) 115 kV Bus a. Apply fault at the LE-WAITS 3 (528325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WAITS 3 115.0 KV 528325 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_WEST_SUB3__528337_0 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_WEST_SUB3__528337_0 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3( 528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 528333 TO WC_SEC 1 528337 TO WC_TER 1 528336 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LE_WEST_SUB3__LE_NRTH_INT3 | 3 Phase fault on LE-WEST_SUB3 (528333) 115 kV Bus a. Apply fault at the LE-WEST_SUB3 (528333) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LE-WEST_SUB3 115.0 KV 528333 TO LE-NRTH_INT3 115.0 KV 528334 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LEA_NATIONL3__SUMMIT_3 | 3 Phase fault on LEA_NATIONL3 (528399) 115 kV Bus a. Apply fault at the LEA_NATIONL3 (528399) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_NATIONL3 115.0 KV 528399 TO SUMMIT_3 115.0 KV 528404 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LEA_ROAD___3__OIL_CENTER_3 | 3 Phase fault on LEA_ROAD 3 (528505) 115 kV Bus a. Apply fault at the LEA_ROAD 3 (528505) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEA_ROAD 3 115.0 KV 528505 TO OIL_CENTER 3 115.0 KV 528552 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LES_138kV_511467 | Apply single-phase fault on: LWSTAP4 138KV 511439 TO LES4 138KV 511467 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 16 cycles and trip: LES4 138KV 511467 TO SHERID4 138KV 511474 CKT 1 SHERID4 138KV 511474 TO ARTVLTP4 138KV 511537 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LES_138kV_511467 | Apply single-phase fault on: LWSTAP4 138KV 511439 TO LES4 138KV 511467 CKT 1, near L.E.S.-4 138 kV for 7 cycles with stuck breaker at L.E.S.-4 138 kV. Clear Fault after 16 cycles and trip: LES4 138KV 511467 TO SHERID4 138KV 511474 CKT 1 SHERID4 138KV 511474 TO ARTVLTP4 138KV 511537 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LES_345kV_511468 | Apply single-phase fault on: LES7 345KV 511468 TO G17171TAP 345.0 KV 760938 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 16 cycles and trip: OKU7 345KV 511456 TO LES7 345KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LES_345kV_511468 | Apply single-phase fault on: LES7 345KV 511468 TO G17171TAP 345.0 KV 760938 CKT 1, near L.E.S.-7 345 kV for 6 cycles with stuck breaker at L.E.S.-7 345 kV. Clear Fault after 16 cycles and trip: OKU7 345KV 511456 TO LES7 345KV 511468 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LIVSTNRIDGE3__CARDINAL___3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 b.2. LOAD 1 527954 b.3. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.4. LOAD 1 527955 b.5. LOAD 1* 527955 b.6. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LIVSTNRIDGE3__CARDINAL___3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO MEDANOS 3 115.0 KV 527954 CKT 1 b.2. LOAD 1 527954 b.3. MEDANOS 3 115.0 KV 527954 TO SAGE_BRUSH 3 115.0 KV 527955 CKT 1 b.4. LOAD 1 527955 b.5. LOAD 1* 527955 b.6. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LIVSTNRIDGE3__WIPP_______3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO WIPP 3 115.0 KV 528009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LIVSTNRIDGE3__XTO_DI9_TP_3 | 3 Phase fault on LIVSTNRIDGE3 (527953) 115 kV Bus a. Apply fault at the LIVSTNRIDGE3 (527953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIVSTNRIDGE3 115.0 KV 527953 TO XTO_DI9_TP 3 115.0 KV 528064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_108_P4_2_CARPENTER | Apply single-phase fault on LINE 523823 TO 523853 CKT 1 and DISCONNECT 523823, near CARPENTER 7 for 21 cycles with stuck breaker at CARPENTER 7 (523823) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_109_P4_2_CROSSROADS | Apply single-phase fault on LINE 527802 TO 527656 CKT 1 and LINE 525549 TO 527656 CKT 1 and DISCONNECT 527655 and DISCONNECT 527653 and DISCONNECT 527651 and DISCONNECT 527652 and DISCONNECT 527654 and trip GENERATOR 1 527605 and trip GENERATOR 1 527607 and trip GENERATOR 1 527614 and trip GENERATOR 1 527615 and trip GENERATOR 1 527617 and trip GENERATOR 1 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629 and DISCONNECT 527656 and DISCONNECT 527658 and DISCONNECT 527659 and DISCONNECT 527660 and DISCONNECT 527661 and DISCONNECT 527662 and DISCONNECT 527663 and DISCONNECT 527666 and DISCONNECT 527667 and DISCONNECT 577120 and DISCONNECT 577121, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_110_P4_2_CROSSROADS | Apply single-phase fault on and LINE 527656 TO 525549 CKT 1 and LINE 527656 TO 527610 CKT 1 and DISCONNECT 527605 and DISCONNECT 527606 and DISCONNECT 527607 and DISCONNECT 527608 and DISCONNECT 527609 and DISCONNECT 527613 and DISCONNECT 527614 and DISCONNECT 527615 and DISCONNECT 527616 and DISCONNECT 527617 and DISCONNECT 527618 and drop LOAD 1 527610 and drop LOAD 2 527610 and DISCONNECT 527598 and DISCONNECT 527599 and DISCONNECT 527600 and DISCONNECT 527601 and DISCONNECT 527602 and DISCONNECT 527603 and DISCONNECT 527604 and DISCONNECT 527610 and DISCONNECT 527611 and DISCONNECT 527612 and DISCONNECT 527621 and DISCONNECT 527622 and DISCONNECT 527623 and DISCONNECT 527624 and DISCONNECT 527628 and DISCONNECT 527629, near CROSSROADS 7 for 21 cycles with stuck breaker at CROSSROADS 7 (527656) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_111_P4_2_CHINA_DRAW | Apply single-phase fault on LINE 528223 TO 528015 CKT 1, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and DISCONNECT 528219 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_113_P4_2_CHINA_DRAW | Apply single-phase fault on and DISCONNECT 528219, near CHINA_DRAW 7 for 16 cycles with stuck breaker at CHINA_DRAW 7 (528223) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528223 TO 528185 CKT 1 and LINE 528223 TO 528015 CKT 1 and DISCONNECT 528219 and DISCONNECT 523823 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_114_P4_2_EDDY_CNTY | Apply single-phase fault on LINE 527802 TO 527965 CKT 1, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and DISCONNECT 527796 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_115_P4_2_EDDY_CNTY | Apply single-phase fault on and DISCONNECT 527796, near EDDY_CNTY 7 for 16 cycles with stuck breaker at EDDY_CNTY 7 (527802) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 527802 TO 527656 CKT 1 and LINE 527802 TO 527965 CKT 1 and DISCONNECT 527796 and DISCONNECT 527802 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_117_P4_2_FINNEY | Apply single-phase fault on LINE 531449 TO 523853 CKT 1 LINE 523823 TO 523853 CKT 1 and DISCONNECT 523853 and DISCONNECT 599950 and DISCONNECT 599951 and DISCONNECT 523118 and DISCONNECT 523114 and DISCONNECT 523115 and DISCONNECT 523116 and DISCONNECT 523117 and trip GENERATOR 1 523061 and trip GENERATOR 1 523062 and DISCONNECT 523061 and DISCONNECT 523062 and DISCONNECT 523063 and DISCONNECT 523064, near FINNEY 7 for 21 cycles with stuck breaker at FINNEY 7 (523853) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-100 trips on Voltage Protection | Disable Voltage Protection for GEN-2017-100
05 - Southwest | 25W | Transfer | LT__SPS_All_118_P4_2_HITCHLAND | Apply single-phase fault on LINE 523097 TO 515554 CKT 2 and DISCONNECT 523112 and DISCONNECT 523111 and DISCONNECT 523109 and DISCONNECT 523107 and DISCONNECT 523110, near HITCHLAND 7 for 21 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 526936 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_119_P4_2_HOBBS_INT | Apply single-phase fault on LINE 527896 TO 527965 CKT 1 and LINE 527896 TO 526936 CKT 1 and DISCONNECT 527895 and DISCONNECT 527896, near HOBBS_INT 7 for 21 cycles with stuck breaker at HOBBS_INT 7 (527896) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_120_P4_3_KIOWA | Apply single-phase fault on and DISCONNECT 527964, near KIOWA 7 for 5 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus . Clear Fault after 16 cycles and trip LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_121_P4_2_KIOWA | Apply single-phase fault on LINE 527965 TO 528027 CKT 1 and DISCONNECT 527964 and DISCONNECT 527964, near KIOWA 7 for 20 cycles with stuck breaker at KIOWA 7 (527965) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_122_P4_2_N_LOVING | Apply single-phase fault on LINE 528185 TO 528223 CKT 1, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_124_P4_2_N_LOVING | Apply single-phase fault on and DISCONNECT 528186, near N_LOVING 7 for 16 cycles with stuck breaker at N_LOVING 7 (528185) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528185 TO 528223 CKT 1 and LINE 528185 TO 527965 CKT 1 and DISCONNECT 528186 and DISCONNECT 528185 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_125_P4_2_POTTERCO | Apply single-phase fault on LINE 523097 TO 523961 CKT 1 and DISCONNECT 523957 and DISCONNECT 523957 and DISCONNECT 523961 and DISCONNECT 524296 and DISCONNECT 524299 and DISCONNECT 524298 and DISCONNECT 524294 and DISCONNECT 524295 and DISCONNECT 524297, near POTTER_CO 7 for 21 cycles with stuck breaker at POTTER_CO 7 (523961) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_126_P4_2_ROADRUNNER | Apply single-phase fault on LINE 528027 TO 528015 CKT 1, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_128_P4_2_ROADRUNNER | Apply single-phase fault on and DISCONNECT 528023, near RDRUNNER 7 for 16 cycles with stuck breaker at RDRUNNER 7 (528027) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 528027 TO 528015 CKT 1 and LINE 528027 TO 527965 CKT 1 and DISCONNECT 528023 and DISCONNECT 528027 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_129_P4_2_YOAKUM | Apply single-phase fault on LINE 526936 TO 525832 CKT 1, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 525832 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_131_P4_2_YOAKUM | Apply single-phase fault on and DISCONNECT 526937, near YOAKUM_345 for 16 cycles with stuck breaker at YOAKUM_345 (526936) 345 kV Bus . Clear Fault after 5 cycles and trip LINE 526936 TO 525832 CKT 1 and LINE 526936 TO 527896 CKT 1 and DISCONNECT 526937 and DISCONNECT 526936 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 515458 TO 525832 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_132_P4_3_TUCO | Apply single-phase fault on and DISCONNECT 525824, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 515458 TO 525832 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_133_P4_1_MUSTANG | Apply single-phase fault on and DISCONNECT 527162, near MUSTANG 3 for 5 cycles with stuck breaker at MUSTANG 3 (527146) 115 kV Bus . Clear Fault after 11 cycles and trip LINE 527202 TO 527146 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | LT__SPS_All_134_P4_2_NICHOLS | Apply single-phase fault on LINE 523978 TO 524044 CKT 2 and LINE 523551 TO 524044 CKT 1, near NICHOLS 6 for 21 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | LT__SPS_All_135_P4_3_NICHOLS | Apply single-phase fault on and DISCONNECT 524041, near NICHOLS 6 for 5 cycles with stuck breaker at NICHOLS 6 (524044) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524023 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | LT__SPS_All_136_P4_2_POTTERCO | Apply single-phase fault on LINE 524267 TO 523959 CKT 1 and LINE 524010 TO 523959 CKT 1, near POTTER_CO 6 for 21 cycles with stuck breaker at POTTER_CO 6 (523959) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_137_P4_3_YOAKUM | Apply single-phase fault on and DISCONNECT 526931, near YOAKUM 6 for 5 cycles with stuck breaker at YOAKUM 6 (526935) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525586 TO 526935 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_138_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525824, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_139_P4_2_TUCO_INT | Apply single-phase fault on LINE 525832 TO 515458 CKT 1 and DISCONNECT 525825, near TUCO_INT 7 for 21 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_140_P4_2_WHEELER | Apply single-phase fault on LINE 523777 TO 511541 CKT &1 and DISCONNECT 523777 and DISCONNECT 523774, near WHEELER 6 for 21 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 515458 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_141_P4_3_TUCO_INT | Apply single-phase fault on and DISCONNECT 525825, near TUCO_INT 7 for 5 cycles with stuck breaker at TUCO_INT 7 (525832) 345 kV Bus . Clear Fault after 11 cycles and trip LINE 525832 TO 515458 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-100 trips on Voltage Protection | Disable Voltage Protection for GEN-2017-100
05 - Southwest | 25W | Transfer | LT__SPS_All_142_P4_3_HITCHLAND | Apply single-phase fault on and DISCONNECT 523091, near HITCHLAND 7 for 5 cycles with stuck breaker at HITCHLAND 7 (523097) 345 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523091 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2017-100 trips on Voltage Protection | Disable Voltage Protection for GEN-2017-100
05 - Southwest | 25S | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_143_P4_3_WHEELER | Apply single-phase fault on WHEELER 523777 TO WHEELER 523776 TO WHEELER 523774 CKT 1 and DISCONNECT 523774, near WHEELER 6 for 5 cycles with stuck breaker at WHEELER 6 (523777) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 523777 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_145_P4_4_BUSHLAND | Apply single-phase fault on and Drop Shunt at Bus 524267, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 524267 and DISCONNECT 524285 and DISCONNECT 524287 and DISCONNECT 524263 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_146_P4_4_SWISHER | Apply single-phase fault on and Drop Shunt at Bus 525213, near SWISHER 6 for 5 cycles with stuck breaker at SWISHER 6 (525213) 230 kV Bus . Clear Fault after 11 cycles and trip LINE 525213 TO 525830 CKT 1 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_147_P4_4_TUCO_INT | Apply single-phase fault on and Drop Shunt at Bus 525830, near TUCO_INT 6 for 5 cycles with stuck breaker at TUCO_INT 6 (525830) 230 kV Bus . Clear Fault after 11 cycles and DISCONNECT 525819 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_148_P4_5_BUSHLAND | Apply single-phase fault on LINE 524267 TO 524290 CKT 1 and DISCONNECT 524263 and DISCONNECT 524285 and DISCONNECT 524287 and LINE 524267 TO 523959 CKT 1, near BUSHLAND 6 for 5 cycles with stuck breaker at BUSHLAND 6 (524267) 230 kV Bus . Clear Fault after 16 cycles and trip LINE 524267 TO 524623 CKT 1 and DISCONNECT 524275 and DISCONNECT 524276 and DISCONNECT 524289 and DISCONNECT 524290 | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | LT__SPS_All_149_P4_1_HARRINGTON_G1 | Apply single-phase fault on LINE 523977 TO 524010 CKT 1 and LINE 523977 TO 524163 CKT 1 and LINE 523977 TO 524044 CKT 1 and DISCONNECT 523977 and DISCONNECT 523971, near HARRNG_WST 6 for 16 cycles with stuck breaker at HARRNG_WST 6 (523977) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | LT__SPS_All_150_P4_1_HARRINGTON_G2 | Apply single-phase fault on LINE 523978 TO 524365 CKT 1 and LINE 523978 TO 524044 CKT 2 and DISCONNECT 523978 and DISCONNECT 523972, near HARRNG_MID 6 for 16 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | LT__SPS_All_151_P4_1_HARRINGTON_G3 | Apply single-phase fault on LINE 523979 TO 523267 CKT 1 and LINE 523979 TO 523959 CKT 1 and DISCONNECT 523979 and DISCONNECT 523973, near HARRNG_EST 6 for 16 cycles with stuck breaker at HARRNG_EST 6 (523979) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_152_P4_1_JONES_G1 | Apply single-phase fault on and DISCONNECT 526331, near JONES 6 for 18 cycles with stuck breaker at JONES 6 (526337) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | LT__SPS_All_153_P4_6_HARRINGTON_M | Apply single-phase fault on and DISCONNECT 523978 and trip GENERATOR 1 523972 and drop LOAD S1 523972 and DISCONNECT 523972, near HARRNG_MID 6 for 5 cycles with stuck breaker at HARRNG_MID 6 (523978) 230 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LT__SPS_All_154_P4_6_MOORE_EAST | Apply single-phase fault on and DISCONNECT 523308 and trip GENERATOR 1 523297 and trip GENERATOR 3 523301 and drop LOAD F1 523297 and drop LOAD 1 523301 and drop LOAD A3 523301 and DISCONNECT 523294 and DISCONNECT 523295 and DISCONNECT 523296 and DISCONNECT 523297 and DISCONNECT 523301 and DISCONNECT 523302, near MOORE_E 3 for 5 cycles with stuck breaker at MOORE_E 3 (523308) 115 kV Bus | P4_Member | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_EST_6__JONES______6 | 3 Phase fault on LUBBCK_EST 6 (526299) 230 kV Bus a. Apply fault at the LUBBCK_EST 6 (526299) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_EST 6 230.0 KV 526299 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LUBBCK_STH_6__JONES______6 | 3 Phase fault on LUBBCK_STH 6 (526269) 230 kV Bus a. Apply fault at the LUBBCK_STH 6 (526269) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LUBBCK_STH 6 230.0 KV 526269 TO JONES 6 230.0 KV 526337 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LWS___S4__LWSTAP_4 | 3 Phase fault on LWS S4 (511431) 138 kV Bus a. Apply fault at the LWS S4 (511431) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWS S4 138.0 KV 511431 TO LWSTAP 4 138.0 KV 511439 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LWSTAP_4__L_E_S__4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | LWSTAP_4__RPPAPER4 | 3 Phase fault on LWSTAP 4 (511439) 138 kV Bus a. Apply fault at the LWSTAP 4 (511439) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LWSTAP 4 138.0 KV 511439 TO RPPAPER4 138.0 KV 511512 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25W | Transfer | MADDOX_____3__ENRON_TP___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO PEARLE 3 115.0 KV 528392 CKT 1 b.2. LOAD 1 528392 b.3. LOAD 1* 528392 b.4. ENRON_TP 3 115.0 KV 528317 TO PEARLE 3 115.0 KV 528392 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25S | Transfer | MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25W | Transfer | MADDOX_____3__G18_004_TAP | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25S | Transfer | MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25W | Transfer | MADDOX_____3__MONUMENT___3 | 3 Phase fault on MADDOX 3 (528355) 115 kV Bus a. Apply fault at the MADDOX 3 (528355) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MADDOX 3 115.0 KV 528355 TO MONUMENT 3 115.0 KV 528491 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2018-004 trips on Frequency Protection | Disable Frequency Protection for GEN-2018-004
05 - Southwest | 25W | Transfer | Maddox_115kV_528355 | Apply single-phase fault on: Maddox 115KV 528355 TO Hobbs Int 115KV 527891 CKT 1, near MADDOX 3 115 kV for 7 cycles with stuck breaker at MADDOX 3 115 kV. Clear Fault after 16 cycles and trip: Maddox 115KV 528355 TO Monument 115KV 528491 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Maddox_115kV_528355 | Apply single-phase fault on: Maddox 115KV 528355 TO Hobbs Int 115KV 527891 CKT 1, near MADDOX 3 115 kV for 7 cycles with stuck breaker at MADDOX 3 115 kV. Clear Fault after 16 cycles and trip: Maddox 115KV 528355 TO Monument 115KV 528491 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MILLEN_TPW_3__MILLEN_TPE_3 | 3 Phase fault on MILLEN_TPW 3 (528434) 115 kV Bus a. Apply fault at the MILLEN_TPW 3 (528434) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLEN_TPW 3 115.0 KV 528434 TO MILLEN_TPE 3 115.0 KV 528436 CKT *1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__CIMARON7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__GEN_2017_233 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GEN-2017-233 345.0 KV 761250 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__GRACMNT7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO GRACMNT7 345.0 KV 515800 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__MCNOWND7 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MCNOWND7 345.0 KV 515444 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__MNCWND37 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO MNCWND37 345.0 KV 515549 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MINCO__7__NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MINCO__7__NSUB345 | 3 Phase fault on MINCO 7 (514801) 345 kV Bus a. Apply fault at the MINCO 7 (514801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINCO 7 345.0 KV 514801 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MONUMENT___3__MONUMNT_TP_3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO MONUMNT_TP 3 115.0 KV 528568 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MONUMENT___3__W_HOBBS____3 | 3 Phase fault on MONUMENT 3 (528491) 115 kV Bus a. Apply fault at the MONUMENT 3 (528491) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMENT 3 115.0 KV 528491 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MONUMNT_TP_3__BYRD_TP____3 | 3 Phase fault on MONUMNT_TP 3 (528568) 115 kV Bus a. Apply fault at the MONUMNT_TP 3 (528568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MONUMNT_TP 3 115.0 KV 528568 TO BYRD_TP 3 115.0 KV 528581 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | MUSTANG6_230kV_527149 | Apply single-phase fault on: MUSTANG6 230.0 KV 527149 TO SEMINOLE6 230.0 KV 527276 CKT 1, near MUSTANG6 230kV for 7 cycles with stuck breaker at MUSTANG6 230kV. Clear Fault after 16 cycles and trip: YOAKUM6 230.0 KV 526935 TO MUSTANG6 230.0 KV 527149 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | MUSTANG6_230kV_527149 | Apply single-phase fault on: MUSTANG6 230.0 KV 527149 TO SEMINOLE6 230.0 KV 527276 CKT 1, near MUSTANG6 230kV for 7 cycles with stuck breaker at MUSTANG6 230kV. Clear Fault after 16 cycles and trip: YOAKUM6 230.0 KV 526935 TO MUSTANG6 230.0 KV 527149 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | N_LOVING___7__528182_0 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7( 528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 528185 TO NORTH_LOVNG3 528182 TO N_LOVING TR1 528186 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | N_LOVING___7__CHINA_DRAW_7 | 3 Phase fault on N_LOVING 7 (528185) 345 kV Bus a. Apply fault at the N_LOVING 7 (528185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. N_LOVING 7 345.0 KV 528185 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NA_ENRICH__3__CARDINAL___3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 b.2. LOAD 1 528605 b.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NA_ENRICH__3__CARDINAL___3 | 3 Phase fault on NA_ENRICH 3 (528603) 115 kV Bus a. Apply fault at the NA_ENRICH 3 (528603) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NA_ENRICH 3 115.0 KV 528603 TO TARGA 3 115.0 KV 528605 CKT 1 b.2. LOAD 1 528605 b.3. CARDINAL 3 115.0 KV 528596 TO TARGA 3 115.0 KV 528605 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NEEDMORE___6__YOAKUM_____6 | 3 Phase fault on NEEDMORE 6 (525586) 230 kV Bus a. Apply fault at the NEEDMORE 6 (525586) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEEDMORE 6 230.0 KV 525586 TO YOAKUM 6 230.0 KV 526935 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NEWHART3_115kV_525460 | Apply single-phase fault on: KRESSINT3 115.0 KV 525192 TO NEWHART3 115.0 KV 525460 CKT 1, near NEWHART3 115kV for 7 cycles with stuck breaker at NEWHART3 115kV. Clear Fault after 16 cycles and trip: HARTINDUST3 115.0 KV 525124 TO NEWHART3 115.0 KV 525460 CKT 1 and HARTINDUST3 115.0 KV 525124 TO LAMTON3 115.0 KV 525414 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NEWHART3_115kV_525460 | Apply single-phase fault on: KRESSINT3 115.0 KV 525192 TO NEWHART3 115.0 KV 525460 CKT 1, near NEWHART3 115kV for 7 cycles with stuck breaker at NEWHART3 115kV. Clear Fault after 16 cycles and trip: HARTINDUST3 115.0 KV 525124 TO NEWHART3 115.0 KV 525460 CKT 1 and HARTINDUST3 115.0 KV 525124 TO LAMTON3 115.0 KV 525414 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NEWHART6_230kV_525461 | Apply single-phase fault on: NEWHART6 230.0 KV 525461 TO PLANTX6 230.0 KV 525481 CKT 1, near NEWHART6 230kV for 7 cycles with stuck breaker at NEWHART6 230kV. Clear Fault after 16 cycles and trip: POTTERCO6 230.0 KV 523959 TO NEWHART6 230.0 KV 525461 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NEWHART6_230kV_525461 | Apply single-phase fault on: NEWHART6 230.0 KV 525461 TO PLANTX6 230.0 KV 525481 CKT 1, near NEWHART6 230kV for 7 cycles with stuck breaker at NEWHART6 230kV. Clear Fault after 16 cycles and trip: POTTERCO6 230.0 KV 523959 TO NEWHART6 230.0 KV 525461 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NORTH_LOVNG3__AGAVE_PDURO3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO AGAVE_PDURO3 115.0 KV 528195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NORTH_LOVNG3__AGAVE_PDURO3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO AGAVE_PDURO3 115.0 KV 528195 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NORTH_LOVNG3__BLACKRIVER_3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO BLACKRIVER 3 115.0 KV 528193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NORTH_LOVNG3__BLACKRIVER_3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO BLACKRIVER 3 115.0 KV 528193 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | NORTH_LOVNG3__HOPI_SUB___3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | NORTH_LOVNG3__HOPI_SUB___3 | 3 Phase fault on NORTH_LOVNG3 (528182) 115 kV Bus a. Apply fault at the NORTH_LOVNG3 (528182) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORTH_LOVNG3 115.0 KV 528182 TO HOPI_SUB 3 115.0 KV 528226 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | O_K_U__7__G17_151TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | O_K_U__7__G18_015_TAP | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO G18-015-TAP 345.0 KV 762467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | O_K_U__7__GEN_2017_033 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO GEN-2017-033 345.0 KV 588760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | O_K_U__7__L_E_S__7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO L.E.S.-7 345.0 KV 511468 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | O_K_U__7__OKLAUN_HVDC7 | 3 Phase fault on O.K.U.-7 (511456) 345 kV Bus a. Apply fault at the O.K.U.-7 (511456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. O.K.U.-7 345.0 KV 511456 TO OKLAUN HVDC7 345.0 KV 511565 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS3_115kV_524874 | Apply single-phase fault on: OASIS3 115.0 KV 524874 TO PORTALES3 115.0 KV 524924 CKT 1, near OASIS3 115kV for 7 cycles with stuck breaker at OASIS3 115kV. Clear Fault after 16 cycles and trip: FECHZPLT3 115.0 KV 524863 TO OASIS3 115.0 KV 524874 CKT 1 and NORRISTP3 115.0 KV 524764 TO FECHZPLT3 115.0 KV 524863 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OASIS3_115kV_524874 | Apply single-phase fault on: OASIS3 115.0 KV 524874 TO PORTALES3 115.0 KV 524924 CKT 1, near OASIS3 115kV for 7 cycles with stuck breaker at OASIS3 115kV. Clear Fault after 16 cycles and trip: FECHZPLT3 115.0 KV 524863 TO OASIS3 115.0 KV 524874 CKT 1 and NORRISTP3 115.0 KV 524764 TO FECHZPLT3 115.0 KV 524863 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OASIS6_230kV_524875 | Apply single-phase fault on: OASIS6 230.0 KV 524875 TO SANJUANTAP6 230.0 KV 524885 CKT 1, near OASIS6 230kV for 7 cycles with stuck breaker at OASIS6 230kV. Clear Fault after 16 cycles and trip: OASIS6 230.0 KV 524875 TO ROOSEVELT6 230.0 KV 524909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OASIS6_230kV_524875 | Apply single-phase fault on: OASIS6 230.0 KV 524875 TO SANJUANTAP6 230.0 KV 524885 CKT 1, near OASIS6 230kV for 7 cycles with stuck breaker at OASIS6 230kV. Clear Fault after 16 cycles and trip: OASIS6 230.0 KV 524875 TO ROOSEVELT6 230.0 KV 524909 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OKLAUN_7__590003_0 | 3 Phase fault on OKLAUN 7 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7( 599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 599891 TO OKLEHV14 590003 TO OK1TERT 590004 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OKLAUN_7__590003_0 | 3 Phase fault on OKLAUN 7 (599891) 345 kV Bus a. Apply fault at the OKLAUN 7( 599891) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OKLAUN 7 599891 TO OKLEHV14 590003 TO OK1TERT 590004 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OXY_WSEM_TP3__JOHNSON_DRW3 | 3 Phase fault on OXY_WSEM_TP3 (527325) 115 kV Bus a. Apply fault at the OXY_WSEM_TP3 (527325) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSEM_TP3 115.0 KV 527325 TO JOHNSON_DRW3 115.0 KV 527362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | OXY_WSTSEM_3__OXY_WSEM_TP3 | 3 Phase fault on OXY_WSTSEM 3 (527323) 115 kV Bus a. Apply fault at the OXY_WSTSEM 3 (527323) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSTSEM 3 115.0 KV 527323 TO OXY_WSEM_TP3 115.0 KV 527325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | OXY_WSTSEM_3__OXY_WSEM_TP3 | 3 Phase fault on OXY_WSTSEM 3 (527323) 115 kV Bus a. Apply fault at the OXY_WSTSEM 3 (527323) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OXY_WSTSEM 3 115.0 KV 527323 TO OXY_WSEM_TP3 115.0 KV 527325 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PCA________3__527929_0 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PCA________3__527929_0 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3( 527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 527930 TO PCA 2 527929 TO PCA_TR1 1 527928 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PCA________3__CARLSBAD___3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PCA________3__CV_LUSK_TP_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO CV-LUSK_TP 3 115.0 KV 527948 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PCA________3__POTASH_JCT_3 | 3 Phase fault on PCA 3 (527930) 115 kV Bus a. Apply fault at the PCA 3 (527930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PCA 3 115.0 KV 527930 TO POTASH_JCT 3 115.0 KV 527962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PECOS______6__528178_0 | 3 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PECOS______6__528178_0 | 3 Phase fault on PECOS 6 (528179) 230 kV Bus a. Apply fault at the PECOS 6( 528179) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PECOS 6 528179 TO PECOS 3 528178 TO PECOS_TR1 1 528176 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____3__NORTH_LOVNG3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 b.2. LOAD 1 528194 b.3. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 b.4. LOAD 1 528194 b.5. NORTH_LOVNG3 115.0 KV 528182 TO SOUTH_LOVNG3 115.0 KV 528192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PHANTOM____3__NORTH_LOVNG3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO MALAGABEND 3 115.0 KV 528194 CKT 1 b.2. LOAD 1 528194 b.3. SOUTH_LOVNG3 115.0 KV 528192 TO MALAGABEND 3 115.0 KV 528194 CKT 1 b.4. LOAD 1 528194 b.5. NORTH_LOVNG3 115.0 KV 528182 TO SOUTH_LOVNG3 115.0 KV 528192 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____3__WOOD_DRAW__3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PHANTOM____3__WOOD_DRAW__3 | 3 Phase fault on PHANTOM 3 (528013) 115 kV Bus a. Apply fault at the PHANTOM 3 (528013) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHANTOM 3 115.0 KV 528013 TO WOOD_DRAW 3 115.0 KV 528228 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PHANTOM____7__528013_0 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7( 528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 528015 TO PHANTOM 3 528013 TO PHANTOM TR21 528012 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PHANTOM____7__CHINA_DRAW_7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO CHINA_DRAW 7 345.0 KV 528223 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PHANTOM____7__RDRUNNER___7 | 3 Phase fault on PHANTOM 7 (528015) 345 kV Bus a. Apply fault at the PHANTOM 7 (528015) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHANTOM 7 345.0 KV 528015 TO RDRUNNER 7 345.0 KV 528027 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLANT_X____6__TOLK_______6 | 3 Phase fault on PLANT_X 6 (525481) 230 kV Bus a. Apply fault at the PLANT_X 6 (525481) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLANT_X 6 230.0 KV 525481 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLANTX_115kV_525480 | Apply single-phase fault on: RKYFORDTP3 115.0 KV 525446 TO PLANTX3 115.0 KV 525480 CKT 1, near PLANTX 115kV for 7 cycles with stuck breaker at PLANTX 115kV. Clear Fault after 16 cycles and trip: MULSHVLY_TP3 115.0 KV 525019 TO PLANTX3 115.0 KV 525480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLANTX_115kV_525480 | Apply single-phase fault on: RKYFORDTP3 115.0 KV 525446 TO PLANTX3 115.0 KV 525480 CKT 1, near PLANTX 115kV for 7 cycles with stuck breaker at PLANTX 115kV. Clear Fault after 16 cycles and trip: MULSHVLY_TP3 115.0 KV 525019 TO PLANTX3 115.0 KV 525480 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLANTX_230kV_525481 | Apply single-phase fault on: PLANTX6 230.0 KV 525481 TO TOLK6 230.0 KV 525531 CKT 1, near PLANTX 230kV for 7 cycles with stuck breaker at PLANTX 230kV. Clear Fault after 16 cycles and trip: PLANTX6 230.0 KV 525481 TO SUNDOWN6 230.0 KV 526435 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLANTX_230kV_525481 | Apply single-phase fault on: PLANTX6 230.0 KV 525481 TO TOLK6 230.0 KV 525531 CKT 1, near PLANTX 230kV for 7 cycles with stuck breaker at PLANTX 230kV. Clear Fault after 16 cycles and trip: PLANTX6 230.0 KV 525481 TO SUNDOWN6 230.0 KV 526435 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLSNTHILL3_115kV_524768 | Apply single-phase fault on: PLSNTHILL3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1, near PLSNTHILL3 115kV for 7 cycles with stuck breaker at PLSNTHILL3 115kV. Clear Fault after 16 cycles and trip: PLSNTHILL3 115.0 KV 524768 TO ECLOVIS3 115.0 KV 524773 CKT 1 and ECLOVIS3 115.0 KV 524773 TO CURRY3 115.0 KV 524822 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLSNTHILL3_115kV_524768 | Apply single-phase fault on: PLSNTHILL3 115.0 KV 524768 TO N_CLOVIS_TP3 115.0 KV 524776 CKT 1, near PLSNTHILL3 115kV for 7 cycles with stuck breaker at PLSNTHILL3 115kV. Clear Fault after 16 cycles and trip: PLSNTHILL3 115.0 KV 524768 TO ECLOVIS3 115.0 KV 524773 CKT 1 and ECLOVIS3 115.0 KV 524773 TO CURRY3 115.0 KV 524822 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | PLSNTHILL6_230kV_524770 | Apply single-phase fault on: PLSNTHILL6 230.0 KV 524770 TO ROOSEVELT6 230.0 KV 524909 CKT 1, near PLSNTHILL6 230kV for 7 cycles with stuck breaker at PLSNTHILL6 230kV. Clear Fault after 16 cycles and trip: PLSNTHILL6 230.0 KV 524770 TO OASIS6 230.0 KV 524875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | PLSNTHILL6_230kV_524770 | Apply single-phase fault on: PLSNTHILL6 230.0 KV 524770 TO ROOSEVELT6 230.0 KV 524909 CKT 1, near PLSNTHILL6 230kV for 7 cycles with stuck breaker at PLSNTHILL6 230kV. Clear Fault after 16 cycles and trip: PLSNTHILL6 230.0 KV 524770 TO OASIS6 230.0 KV 524875 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_3__527961_0 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTASH_JCT_3__527961_0 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3( 527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 527962 TO POTASH_JCT 2 527961 TO POTASH_TR3 1 527960 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTASH_JCT_3__CARLSBAD___3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO CARLSBAD 3 115.0 KV 528160 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTASH_JCT_3__INTREPDW_TP3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO INTREPDW_TP3 115.0 KV 527999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTASH_JCT_3__KIOWA______3 | 3 Phase fault on POTASH_JCT 3 (527962) 115 kV Bus a. Apply fault at the POTASH_JCT 3 (527962) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 3 115.0 KV 527962 TO KIOWA 3 115.0 KV 527966 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_6__527962_0 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTASH_JCT_6__527962_0 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6( 527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 527963 TO POTASH_JCT 3 527962 TO POTASH_TR1 1 527958 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | POTASH_JCT_6__PECOS______6 | 3 Phase fault on POTASH_JCT 6 (527963) 230 kV Bus a. Apply fault at the POTASH_JCT 6 (527963) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POTASH_JCT 6 230.0 KV 527963 TO PECOS 6 230.0 KV 528179 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | POTTERCO6_230kV_523959 | Apply single-phase fault on: POTTERCO6 230.0 KV 523959 TO HARRNG_EST6 230.0 KV 523979 CKT 1, near POTTERCO6 230kV for 7 cycles with stuck breaker at POTTERCO6 230kV. Clear Fault after 16 cycles and trip: POTTERCO6 230.0 KV 523959 TO ROLLHILLS6 230.0 KV 524010 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (523812) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (523812)
05 - Southwest | 25W | Transfer | POTTERCO6_230kV_523959 | Apply single-phase fault on: POTTERCO6 230.0 KV 523959 TO HARRNG_EST6 230.0 KV 523979 CKT 1, near POTTERCO6 230kV for 7 cycles with stuck breaker at POTTERCO6 230kV. Clear Fault after 16 cycles and trip: POTTERCO6 230.0 KV 523959 TO ROLLHILLS6 230.0 KV 524010 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Lano GSU (52381) trips on Voltage Protection | Disable Voltage Protection for Lano GSU (52381)
05 - Southwest | 25S | Transfer | QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | QUAHADA____3__DCP_ZIA_TP_3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO DCP_ZIA TP 3 115.0 KV 528422 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | QUAHADA____3__LEA_NATIONL3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO LEA_NATIONL3 115.0 KV 528399 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | QUAHADA____3__PCA________3 | 3 Phase fault on QUAHADA 3 (528394) 115 kV Bus a. Apply fault at the QUAHADA 3 (528394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUAHADA 3 115.0 KV 528394 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 b.2. LOAD 1 528396 b.3. PCA 3 115.0 KV 527930 TO XTO_BIGEDDY3 115.0 KV 528396 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER___3__AGAVE_RHIL23 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHIL23 115.0 KV 528231 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER___3__BATTLE_AXE_3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO BATTLE_AXE 3 115.0 KV 528040 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER___3__CUSTERMTN__3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO CUSTERMTN 3 115.0 KV 528239 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER___3__GEN_2016_121 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO GEN-2016-121 115.0 KV 587990 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER___3__OCHOA______3 | 3 Phase fault on RDRUNNER 3 (528025) 115 kV Bus a. Apply fault at the RDRUNNER 3 (528025) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNER 3 115.0 KV 528025 TO AGAVE_RHILL3 115.0 KV 528230 CKT 1 b.2. LOAD 1 528230 b.3. AGAVE_RHILL3 115.0 KV 528230 TO OCHOA 3 115.0 KV 528232 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER___7__528025_0 | 3 Phase fault on RDRUNNER 7 (528027) 345 kV Bus a. Apply fault at the RDRUNNER 7( 528027) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RDRUNNER 7 528027 TO RDRUNNER 3 528025 TO RDRNNER_TR11 528023 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Rdrunner_115kV_528025 | Apply single-phase fault on: RDRUNNER 115KV 528025 TO AGAVERHILL 115KV 528230 CKT 1, near RDRUNNER 3 115 kV for 7 cycles with stuck breaker at RDRUNNER 3 115 kV. Clear Fault after 16 cycles and trip: RDRUNNER 115KV 528025 TO BATTLE AXE 115KV 528040 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Rdrunner_115kV_528025 | Apply single-phase fault on: RDRUNNER 115KV 528025 TO AGAVERHILL 115KV 528230 CKT 1, near RDRUNNER 3 115 kV for 7 cycles with stuck breaker at RDRUNNER 3 115 kV. Clear Fault after 16 cycles and trip: RDRUNNER 115KV 528025 TO BATTLE AXE 115KV 528040 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RDRUNNER_345kV_528027 | Apply single-phase fault on: RDRUNNER 345KV 528027 TO KIOWA 345KV 527965 CKT 1, near RDRUNNER 7 345 kV for 6 cycles with stuck breaker at RDRUNNER 7 345 kV. Clear Fault after 16 cycles and trip: RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RDRUNNER_345kV_528027 | Apply single-phase fault on: RDRUNNER 345KV 528027 TO KIOWA 345KV 527965 CKT 1, near RDRUNNER 7 345 kV for 6 cycles with stuck breaker at RDRUNNER 7 345 kV. Clear Fault after 16 cycles and trip: RDRUNNER 345KV 528027 TO PHANTOM 345KV 528015 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RED_BLUFF__3__RDRUNNER___3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO RDRUNNER 3 115.0 KV 528025 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RED_BLUFF__3__WIPP_______3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAND_DUNES 3 115.0 KV 528016 TO RED_BLUFF 3 115.0 KV 528018 CKT 1 b.2. WIPP 3 115.0 KV 528009 TO SAND_DUNES 3 115.0 KV 528016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RED_BLUFF__3__WOLFCAMP_TP3 | 3 Phase fault on RED_BLUFF 3 (528018) 115 kV Bus a. Apply fault at the RED_BLUFF 3 (528018) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RED_BLUFF 3 115.0 KV 528018 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RED_BLUFF_115kV_528018 | Apply single-phase fault on: REDBLUFF 115KV 528018 TO WOLFCAMPTP 115KV 528235 CKT 1, near RED_BLUFF 3 115 kV for 7 cycles with stuck breaker at RED_BLUFF 3 115 kV. Clear Fault after 16 cycles and trip: REDBLUFF 115KV 528018 TO RDRUNNER 115KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RED_BLUFF_115kV_528018 | Apply single-phase fault on: REDBLUFF 115KV 528018 TO WOLFCAMPTP 115KV 528235 CKT 1, near RED_BLUFF 3 115 kV for 7 cycles with stuck breaker at RED_BLUFF 3 115 kV. Clear Fault after 16 cycles and trip: REDBLUFF 115KV 528018 TO RDRUNNER 115KV 528025 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROOSEVELT__6__TOLK_______6 | 3 Phase fault on ROOSEVELT 6 (524909) 230 kV Bus a. Apply fault at the ROOSEVELT 6 (524909) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROOSEVELT 6 230.0 KV 524909 TO TOLK 6 230.0 KV 525531 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | ROOSEVELT6_230kV_524909 | Apply single-phase fault on: OASIS6 230.0 KV 524875 TO ROOSEVELT6 230.0 KV 524909 CKT 1, near ROOSEVELT6 230kV for 7 cycles with stuck breaker at ROOSEVELT6 230kV. Clear Fault after 16 cycles and trip: ROOSEVELT6 230.0 KV 524909 TO TOLK6 230.0 KV 525531 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | ROOSEVELT6_230kV_524909 | Apply single-phase fault on: OASIS6 230.0 KV 524875 TO ROOSEVELT6 230.0 KV 524909 CKT 1, near ROOSEVELT6 230kV for 7 cycles with stuck breaker at ROOSEVELT6 230kV. Clear Fault after 16 cycles and trip: ROOSEVELT6 230.0 KV 524909 TO TOLK6 230.0 KV 525531 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RSHSPR1_COL1__511979_0 | 3 Phase fault on RSHSPR1_COL1 (511978) 34.5 kV Bus a. Apply fault at the RSHSPR1_COL1( 511978) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RSHSPR1_COL1__511979_0 | 3 Phase fault on RSHSPR1_COL1 (511978) 34.5 kV Bus a. Apply fault at the RSHSPR1_COL1( 511978) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RSHSPR1_COL1 511978 TO RSHSPR1_MPT1 511979 TO RSHSPR1_TER1 511583 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RSVLT_CC_E_7__CROSSROADS_7 | 3 Phase fault on RSVLT_CC_E 7 (527655) 345 kV Bus a. Apply fault at the RSVLT_CC_E 7 (527655) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RSVLT_CC_E 7 345.0 KV 527655 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RUSHSPR7__511965_0 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7( 511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 511571 TO RUSHSPRW1-1 511965 TO RUSHSPR1-1 511572 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RUSHSPR7__GEN_2015_092 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RUSHSPR7__GEN_2015_092 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2015-092 345.0 KV 563259 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RUSHSPR7__GEN_2018_055 | 3 Phase fault on RUSHSPR7 (511571) 345 kV Bus a. Apply fault at the RUSHSPR7 (511571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RUSHSPR7 345.0 KV 511571 TO GEN-2018-055 345.0 KV 762900 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | RUSSELL____3__HIGG_______3 | 3 Phase fault on RUSSELL 3 (527284) 115 kV Bus a. Apply fault at the RUSSELL 3 (527284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RUSSELL 3 115.0 KV 527284 TO HIGG 3 115.0 KV 527363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | S_JAL______3__DOLLARHIDE_3 | 3 Phase fault on S_JAL 3 (528547) 115 kV Bus a. Apply fault at the S_JAL 3 (528547) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S_JAL 3 115.0 KV 528547 TO DOLLARHIDE 3 115.0 KV 528561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SAGA_SCOL__7__CROSSROADS_7 | 3 Phase fault on SAGA_SCOL 7 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
05 - Southwest | 25W | Transfer | SAGA_SCOL__7__CROSSROADS_7 | 3 Phase fault on SAGA_SCOL 7 (527610) 345 kV Bus a. Apply fault at the SAGA_SCOL 7 (527610) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SAGA_SCOL 7 345.0 KV 527610 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
05 - Southwest | 25S | Transfer | SAGE_BRUSH_3__CARDINAL___3 | 3 Phase fault on SAGE_BRUSH 3 (527955) 115 kV Bus a. Apply fault at the SAGE_BRUSH 3 (527955) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SAGE_BRUSH_3__CARDINAL___3 | 3 Phase fault on SAGE_BRUSH 3 (527955) 115 kV Bus a. Apply fault at the SAGE_BRUSH 3 (527955) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAGE_BRUSH 3 115.0 KV 527955 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SANGER_SW__3__G18_004_TAP | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO G18-004-TAP 115.0 KV 762442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SANGER_SW__3__SW_4J44____3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SANGER_SW__3__W_BENDER___3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.2. LOAD 1 528575 b.3. LOAD 2 528575 b.4. OXY_NHU_RCF3 115.0 KV 528574 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.5. LOAD 1 528575 b.6. LOAD 2 528575 b.7. W_BENDER 3 115.0 KV 528449 TO OXY_NHU_RCF3 115.0 KV 528574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SANGER_SW__3__W_BENDER___3 | 3 Phase fault on SANGER_SW 3 (528463) 115 kV Bus a. Apply fault at the SANGER_SW 3 (528463) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SANGER_SW 3 115.0 KV 528463 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.2. LOAD 1 528575 b.3. LOAD 2 528575 b.4. OXY_NHU_RCF3 115.0 KV 528574 TO OXYPERMIAN 3 115.0 KV 528575 CKT 1 b.5. LOAD 1 528575 b.6. LOAD 2 528575 b.7. W_BENDER 3 115.0 KV 528449 TO OXY_NHU_RCF3 115.0 KV 528574 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SEAGRAVES3_115kV_527202 | Apply single-phase fault on: SEAGRAVES3 115.0 KV 527202 TO SULPHUR3 115.0 KV 527262 CKT 1, near SEAGRAVES3 115kV for 7 cycles with stuck breaker at SEAGRAVES3 115kV. Clear Fault after 16 cycles and trip: MUSTANG3 115.0 KV 527146 TO SEAGRAVES3 115.0 KV 527202 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SEAGRAVES3_115kV_527202 | Apply single-phase fault on: SEAGRAVES3 115.0 KV 527202 TO SULPHUR3 115.0 KV 527262 CKT 1, near SEAGRAVES3 115kV for 7 cycles with stuck breaker at SEAGRAVES3 115kV. Clear Fault after 16 cycles and trip: MUSTANG3 115.0 KV 527146 TO SEAGRAVES3 115.0 KV 527202 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SN_JUAN_TAP6__CHAVES_CNTY6 | 3 Phase fault on SN_JUAN_TAP6 (524885) 230 kV Bus a. Apply fault at the SN_JUAN_TAP6 (524885) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SN_JUAN_TAP6 230.0 KV 524885 TO CHAVES_CNTY6 230.0 KV 527483 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SULPHUR2_69kV_527261 | Apply single-phase fault on: ADAIR2 69.0 KV 527253 TO SULPHUR2 69.0 KV 527261 CKT 1, near SULPHUR2 69kV for 7 cycles with stuck breaker at SULPHUR2 69kV. Clear Fault after 16 cycles and trip: SULPHUR2 69.0 KV 527261 TO LGFOSTER2 69.0 KV 527271 CKT 1 and UNIONTX2 69.0 KV 526999 TO LGFOSTER2 69.0 KV 527271 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SULPHUR2_69kV_527261 | Apply single-phase fault on: ADAIR2 69.0 KV 527253 TO SULPHUR2 69.0 KV 527261 CKT 1, near SULPHUR2 69kV for 7 cycles with stuck breaker at SULPHUR2 69kV. Clear Fault after 16 cycles and trip: SULPHUR2 69.0 KV 527261 TO LGFOSTER2 69.0 KV 527271 CKT 1 and UNIONTX2 69.0 KV 526999 TO LGFOSTER2 69.0 KV 527271 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SULPHUR3_115kV_527262 | Apply single-phase fault on: SEAGRAVES3 115.0 KV 527202 TO SULPHUR3 115.0 KV 527262 CKT 1, near SULPHUR3 115kV for 7 cycles with stuck breaker at SULPHUR3 115kV. Clear Fault after 16 cycles and trip: DIAMONDBACK3 115.0 KV 527212 TO SULPHUR3 115.0 KV 527262 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SULPHUR3_115kV_527262 | Apply single-phase fault on: SEAGRAVES3 115.0 KV 527202 TO SULPHUR3 115.0 KV 527262 CKT 1, near SULPHUR3 115kV for 7 cycles with stuck breaker at SULPHUR3 115kV. Clear Fault after 16 cycles and trip: DIAMONDBACK3 115.0 KV 527212 TO SULPHUR3 115.0 KV 527262 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNDOWN3_115kV_526434 | Apply single-phase fault on: SUNDOWN3 115.0 KV 526434 TO AMOCOTP3 115.0 KV 526445 CKT 1, near SUNDOWN3 115kV for 7 cycles with stuck breaker at SUNDOWN3 115kV. Clear Fault after 16 cycles and trip: PACIFIC3 115.0 KV 526424 TO SUNDOWN3 115.0 KV 526434 CKT 1 COCHRAN3 115.0 KV 526361 TO PACIFIC3 115.0 KV 526424 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNDOWN3_115kV_526434 | Apply single-phase fault on: SUNDOWN3 115.0 KV 526434 TO AMOCOTP3 115.0 KV 526445 CKT 1, near SUNDOWN3 115kV for 7 cycles with stuck breaker at SUNDOWN3 115kV. Clear Fault after 16 cycles and trip: PACIFIC3 115.0 KV 526424 TO SUNDOWN3 115.0 KV 526434 CKT 1 COCHRAN3 115.0 KV 526361 TO PACIFIC3 115.0 KV 526424 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD4__515136_0 | 3 Phase fault on SUNNYSD4 (515135) 138 kV Bus a. Apply fault at the SUNNYSD4( 515135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNNYSD4 515135 TO SUNNYSD7 515136 TO SUNNYSD1 515762 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD7__515135_0 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7( 515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 515136 TO SUNNYSD4 515135 TO SUNYSD 1 515405 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SUNNYSD7__G16_063_TAP | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO G16-063-TAP 345.0 KV 560088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SUNNYSD7__GEN_2017_166 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-166 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
05 - Southwest | 25W | Transfer | SUNNYSD7__GEN_2017_166 | 3 Phase fault on SUNNYSD7 (515136) 345 kV Bus a. Apply fault at the SUNNYSD7 (515136) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUNNYSD7 345.0 KV 515136 TO GEN-2017-166 345.0 KV 761859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
05 - Southwest | 25S | Transfer | SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SW_4J44____3__W_HOBBS____3 | 3 Phase fault on SW_4J44 3 (528484) 115 kV Bus a. Apply fault at the SW_4J44 3 (528484) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW_4J44 3 115.0 KV 528484 TO W_HOBBS 3 115.0 KV 528498 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SWISHER____6__525212_0 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6( 525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 525213 TO SWISHER 3 525212 TO SWISHER_TR11 525211 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SWISHER____6__NEWHART____6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO NEWHART 6 230.0 KV 525461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SWISHER____6__TUCO_INT___6 | 3 Phase fault on SWISHER 6 (525213) 230 kV Bus a. Apply fault at the SWISHER 6 (525213) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SWISHER 6 230.0 KV 525213 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | SWISHER6_230kV_525213 | Apply single-phase fault on: AMASOUTH6 230.0 KV 524415 TO SWISHER6 230.0 KV 525213 CKT 1, near SWISHER6 230kV for 7 cycles with stuck breaker at SWISHER6 230kV. Clear Fault after 16 cycles and trip: SWISHER6 230.0 KV 525213 TO TUCO_INT6 230.0 KV 525830 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | SWISHER6_230kV_525213 | Apply single-phase fault on: AMASOUTH6 230.0 KV 524415 TO SWISHER6 230.0 KV 525213 CKT 1, near SWISHER6 230kV for 7 cycles with stuck breaker at SWISHER6 230kV. Clear Fault after 16 cycles and trip: SWISHER6 230.0 KV 525213 TO TUCO_INT6 230.0 KV 525830 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TAYLOR_____3__MILLEN_TPE_3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TAYLOR_____3__MILLEN_TPE_3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 b.2. LOAD 1 528442 b.3. MILLEN_TPE 3 115.0 KV 528436 TO NE_HOBBS 3 115.0 KV 528442 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TAYLOR_____3__SW_4J44____3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 b.2. LOAD 1 528470 b.3. E_SANGER 3 115.0 KV 528470 TO S_HOBBS 3 115.0 KV 528477 CKT 1 b.4. LOAD 1 528477 b.5. LOAD 2 528477 b.6. S_HOBBS 3 115.0 KV 528477 TO OXY_S_HOBBS3 115.0 KV 528480 CKT 1 b.7. LOAD 1 528480 b.8. LOAD 2 528480 b.9. LOAD 3 528480 b.10. OXY_S_HOBBS3 115.0 KV 528480 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TAYLOR_____3__SW_4J44____3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO E_SANGER 3 115.0 KV 528470 CKT 1 b.2. LOAD 1 528470 b.3. E_SANGER 3 115.0 KV 528470 TO S_HOBBS 3 115.0 KV 528477 CKT 1 b.4. LOAD 1 528477 b.5. LOAD 2 528477 b.6. S_HOBBS 3 115.0 KV 528477 TO OXY_S_HOBBS3 115.0 KV 528480 CKT 1 b.7. LOAD 1 528480 b.8. LOAD 2 528480 b.9. LOAD 3 528480 b.10. OXY_S_HOBBS3 115.0 KV 528480 TO SW_4J44 3 115.0 KV 528484 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TAYLOR_____3__W_BENDER___3 | 3 Phase fault on TAYLOR 3 (528413) 115 kV Bus a. Apply fault at the TAYLOR 3 (528413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TAYLOR 3 115.0 KV 528413 TO W_BENDER 3 115.0 KV 528449 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | Taylor_115kV_528413 | Apply single-phase fault on: Taylor 115KV 528413 TO E Sanger 115KV 528470 CKT 1, near TAYLOR 3 115 kV for 7 cycles with stuck breaker at TAYLOR 3 115 kV. Clear Fault after 16 cycles and trip: Taylor 115KV 528413 TO NE Hobbs 115KV 528442 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | Taylor_115kV_528413 | Apply single-phase fault on: Taylor 115KV 528413 TO E Sanger 115KV 528470 CKT 1, near TAYLOR 3 115 kV for 7 cycles with stuck breaker at TAYLOR 3 115 kV. Clear Fault after 16 cycles and trip: Taylor 115KV 528413 TO NE Hobbs 115KV 528442 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TEAGUE_____3__CARDINAL___3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TEAGUE_____3__CARDINAL___3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO CARDINAL 3 115.0 KV 528596 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TEAGUE_____3__S_JAL______3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TEAGUE_____3__S_JAL______3 | 3 Phase fault on TEAGUE 3 (528526) 115 kV Bus a. Apply fault at the TEAGUE 3 (528526) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEAGUE 3 115.0 KV 528526 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRY_CNTY_3__DENVER_N___3 | 3 Phase fault on TERRY_CNTY 3 (526736) 115 kV Bus a. Apply fault at the TERRY_CNTY 3 (526736) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRY_CNTY 3 115.0 KV 526736 TO DENVER_N 3 115.0 KV 527130 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRYCNTY3_115kV_526736 | Apply single-phase fault on: WOLFFORTH3 115.0 KV 526524 TO TERTRYCNTY3 115.0 KV 526736 CKT 1, near TERRYCNTY3 115kV for 7 cycles with stuck breaker at TERRYCNTY3 115kV. Clear Fault after 16 cycles and trip: TERTRYCNTY3 115.0 KV 526736 TO DENVERN3 115.0 KV 527130 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRYCNTY3_115kV_526736 | Apply single-phase fault on: WOLFFORTH3 115.0 KV 526524 TO TERTRYCNTY3 115.0 KV 526736 CKT 1, near TERRYCNTY3 115kV for 7 cycles with stuck breaker at TERRYCNTY3 115kV. Clear Fault after 16 cycles and trip: TERTRYCNTY3 115.0 KV 526736 TO DENVERN3 115.0 KV 527130 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRYRD7__G17_171_TAP | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO G17-171-TAP 345.0 KV 760938 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRYRD7__RSHSPR1_MPT1 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RSHSPR1_MPT1 345.0 KV 511979 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
05 - Southwest | 25W | Transfer | TERRYRD7__RUSHSPR7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO RUSHSPR7 345.0 KV 511571 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
05 - Southwest | 25S | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TERRYRD7__SUNNYSD7 | 3 Phase fault on TERRYRD7 (511568) 345 kV Bus a. Apply fault at the TERRYRD7 (511568) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TERRYRD7 345.0 KV 511568 TO SUNNYSD7 345.0 KV 515136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TIERABLANCA3_115kV_524630 | Apply single-phase fault on: DFSMTHEST3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1, near TIERABLANCA3 115kV for 7 cycles with stuck breaker at TIERABLANCA3 115kV. Clear Fault after 16 cycles and trip: NEHEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TIERABLANCA3_115kV_524630 | Apply single-phase fault on: DFSMTHEST3 115.0 KV 524619 TO TIERABLANCA3 115.0 KV 524630 CKT 1, near TIERABLANCA3 115kV for 7 cycles with stuck breaker at TIERABLANCA3 115kV. Clear Fault after 16 cycles and trip: NEHEREFORD3 115.0 KV 524567 TO TIERABLANCA3 115.0 KV 524630 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______6__525549_0 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6( 525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 525531 TO TOLK 7 525549 TO TOLK_TR 1 525537 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______6__525549_0 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6( 525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 525531 TO TOLK 7 525549 TO TOLK_TR 1 525537 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______6__GEN_2017_158 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO GEN-2017-158 230.0 KV 762132 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______6__LAMB_CNTY__6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO LAMB_CNTY 6 230.0 KV 525637 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______6__NEEDMORE___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO NEEDMORE 6 230.0 KV 525586 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______6__TUCO_INT___6 | 3 Phase fault on TOLK 6 (525531) 230 kV Bus a. Apply fault at the TOLK 6 (525531) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TOLK 6 230.0 KV 525531 TO TUCO_INT 6 230.0 KV 525830 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______7__525531_0 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7( 525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 525549 TO TOLK 6 525531 TO TOLK_TR 1 525537 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK_______7__CROSSROADS_7 | 3 Phase fault on TOLK 7 (525549) 345 kV Bus a. Apply fault at the TOLK 7 (525549) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TOLK 7 345.0 KV 525549 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TOLK6_230kV_525531 | Apply single-phase fault on: ROOSEVELT6 230.0 KV 524909 TO TOLK6 230.0 KV 525531 CKT 1, near TOLK6 230kV for 7 cycles with stuck breaker at TOLK6 230kV. Clear Fault after 16 cycles and trip: PLANT_X6 230.0 KV 525481 TO TOLK6 230.0 KV 525531 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TOLK6_230kV_525531 | Apply single-phase fault on: ROOSEVELT6 230.0 KV 524909 TO TOLK6 230.0 KV 525531 CKT 1, near TOLK6 230kV for 7 cycles with stuck breaker at TOLK6 230kV. Clear Fault after 16 cycles and trip: PLANT_X6 230.0 KV 525481 TO TOLK6 230.0 KV 525531 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___3__525816_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT2 2 525816 TO TUCO_TR7 1 525814 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___3__525826_0 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3( 525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 525828 TO TUCO_INT 2 525826 TO TUCO_TR6 1 525823 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___3__LUBBCK_EST_3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO LUBBCK_EST 3 115.0 KV 526298 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___3__STANTON_W__3 | 3 Phase fault on TUCO_INT 3 (525828) 115 kV Bus a. Apply fault at the TUCO_INT 3 (525828) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 3 115.0 KV 525828 TO STANTON_W 3 115.0 KV 526076 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___6__525828_0 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6( 525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 525830 TO TUCO_INT 3 525828 TO TUCO_TR4 1 525821 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
05 - Southwest | 25W | Transfer | TUCO_INT___6__ANTELOPE_1_6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO ANTELOPE_1 6 230.0 KV 525840 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
05 - Southwest | 25S | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___6__CARLISLE___6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO CARLISLE 6 230.0 KV 526161 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
05 - Southwest | 25W | Transfer | TUCO_INT___6__HALE_WNDCL16 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO HALE_WNDCL16 230.0 KV 525957 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
05 - Southwest | 25S | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___6__JONES______6 | 3 Phase fault on TUCO_INT 6 (525830) 230 kV Bus a. Apply fault at the TUCO_INT 6 (525830) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TUCO_INT 6 230.0 KV 525830 TO JONES 6 230.0 KV 526337 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___7__525830_0 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7( 525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 525832 TO TUCO_INT 6 525830 TO TUCO_TR2 1 525825 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___7__ELK_CT1 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO ELK_CT1 345.0 KV 525850 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___7__G17_151TAP | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO G17-151TAP 345.0 KV 762216 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCO_INT___7__YOAKUM_345 | 3 Phase fault on TUCO_INT 7 (525832) 345 kV Bus a. Apply fault at the TUCO_INT 7 (525832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TUCO_INT 7 345.0 KV 525832 TO YOAKUM_345 345.0 KV 526936 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCOINT6_230kV_525830 | Apply single-phase fault on: TUCOINT6 230.0 KV 525830 TO JONES6 230.0 KV 526337 CKT 1, near TUCOINT6 230kV for 7 cycles with stuck breaker at TUCOINT6 230kV. Clear Fault after 16 cycles and trip: TUCOINT6 230.0 KV 525830 TO CARLISLE6 230.0 KV 526161 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCOINT6_230kV_525830 | Apply single-phase fault on: TUCOINT6 230.0 KV 525830 TO JONES6 230.0 KV 526337 CKT 1, near TUCOINT6 230kV for 7 cycles with stuck breaker at TUCOINT6 230kV. Clear Fault after 16 cycles and trip: TUCOINT6 230.0 KV 525830 TO CARLISLE6 230.0 KV 526161 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TUCOINT7_345kV_525832 | Apply single-phase fault on: BORDER7 345KV 515458 TO TUCOINT7 345KV 525832 CKT 1, near TUCOINT7 345kV for 6 cycles with stuck breaker at TUCOINT7 345kV. Clear Fault after 16 cycles and trip: TUCOINT7 345KV 525832 TO YOAKUM_345 345KV 526936 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TUCOINT7_345kV_525832 | Apply single-phase fault on: BORDER7 345KV 515458 TO TUCOINT7 345KV 525832 CKT 1, near TUCOINT7 345kV for 6 cycles with stuck breaker at TUCOINT7 345kV. Clear Fault after 16 cycles and trip: TUCOINT7 345KV 525832 TO YOAKUM_345 345KV 526936 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | TWEEDY_____3__EDDY_NTH___3 | 3 Phase fault on TWEEDY 3 (527597) 115 kV Bus a. Apply fault at the TWEEDY 3 (527597) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | TWEEDY_____3__EDDY_NTH___3 | 3 Phase fault on TWEEDY 3 (527597) 115 kV Bus a. Apply fault at the TWEEDY 3 (527597) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWEEDY 3 115.0 KV 527597 TO EDDY_NTH 3 115.0 KV 527798 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | W_BENDER___3__N_HOBBS____3 | 3 Phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BENDER 3 115.0 KV 528449 TO N_HOBBS 3 115.0 KV 528456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | W_BENDER___3__N_HOBBS____3 | 3 Phase fault on W_BENDER 3 (528449) 115 kV Bus a. Apply fault at the W_BENDER 3 (528449) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_BENDER 3 115.0 KV 528449 TO N_HOBBS 3 115.0 KV 528456 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | W_HOBBS____3__DRINKARD_TP3 | 3 Phase fault on W_HOBBS 3 (528498) 115 kV Bus a. Apply fault at the W_HOBBS 3 (528498) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W_HOBBS 3 115.0 KV 528498 TO DRINKARD_TP3 115.0 KV 528533 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WHITTEN____3__LEA_ROAD___3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WARD 3 115.0 KV 528519 TO WHITTEN 3 115.0 KV 528540 CKT 1 b.2. LOAD 1 528540 b.3. LEA_ROAD 3 115.0 KV 528505 TO WARD 3 115.0 KV 528519 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WHITTEN____3__S_JAL______3 | 3 Phase fault on WHITTEN 3 (528540) 115 kV Bus a. Apply fault at the WHITTEN 3 (528540) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHITTEN 3 115.0 KV 528540 TO S_JAL 3 115.0 KV 528547 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WOLFCAMP_TP3__PHANTOM____3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 b.2. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WOLFCAMP_TP3__PHANTOM____3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOPCO_PKRLK3 115.0 KV 528020 TO WOLFCAMP_TP3 115.0 KV 528235 CKT 1 b.2. PHANTOM 3 115.0 KV 528013 TO BOPCO_PKRLK3 115.0 KV 528020 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WOLFCAMP_TP3__WOLFCAMP___3 | 3 Phase fault on WOLFCAMP_TP3 (528235) 115 kV Bus a. Apply fault at the WOLFCAMP_TP3 (528235) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCAMP_TP3 115.0 KV 528235 TO WOLFCAMP 3 115.0 KV 528236 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV4__515375_0 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 515376 TO WWRDEHV7 515375 TO WWDEHV21 515799 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV7__DGRASSE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO DGRASSE7 345.0 KV 515852 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV7__G07621119_20 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G07621119-20 345.0 KV 515599 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV7__G16_003_TAP | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV7__GUTHRIE7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO GUTHRIE7 345.0 KV 515961 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV7__TATONGA7 | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO TATONGA7 345.0 KV 515407 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | WWRDEHV7__WWDBORDT | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | WWRDEHV7__WWDBORDT | 3 Phase fault on WWRDEHV7 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 345.0 KV 515375 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | XTO_DI9_TP_3__XTO_DI9____3 | 3 Phase fault on XTO_DI9_TP 3 (528064) 115 kV Bus a. Apply fault at the XTO_DI9_TP 3 (528064) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_DI9_TP 3 115.0 KV 528064 TO XTO_DI9 3 115.0 KV 528066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | XTO_DI9_TP_3__XTO_DI9____3 | 3 Phase fault on XTO_DI9_TP 3 (528064) 115 kV Bus a. Apply fault at the XTO_DI9_TP 3 (528064) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. XTO_DI9_TP 3 115.0 KV 528064 TO XTO_DI9 3 115.0 KV 528066 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | XTOMAHONEY6_230kV_527011 | Apply single-phase fault on: BRUSUB6 230.0 KV 527009 TO XTOMAHONEY6 230.0 KV 527011 CKT 1, near XTOMAHONEY6 230kV for 7 cycles with stuck breaker at XTOMAHONEY6 230kV. Clear Fault after 16 cycles and trip: AMOCOWASSON6 230.0 KV 526784 TO XTOMAHONEY6 230.0 KV 527011 CKT 1 and AMOCOWASSON6 230.0 KV 526784 TO MUSTANG6 230.0 KV 527149 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | XTOMAHONEY6_230kV_527011 | Apply single-phase fault on: BRUSUB6 230.0 KV 527009 TO XTOMAHONEY6 230.0 KV 527011 CKT 1, near XTOMAHONEY6 230kV for 7 cycles with stuck breaker at XTOMAHONEY6 230kV. Clear Fault after 16 cycles and trip: AMOCOWASSON6 230.0 KV 526784 TO XTOMAHONEY6 230.0 KV 527011 CKT 1 and AMOCOWASSON6 230.0 KV 526784 TO MUSTANG6 230.0 KV 527149 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_____6__526934_0 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6( 526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 526935 TO YOAKUM 3 526934 TO YOAKUM_TR2 1 526932 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_____6__BRU_SUB____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO BRU_SUB 6 230.0 KV 527009 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_____6__INK_BASIN__6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO INK_BASIN 6 230.0 KV 527028 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_____6__MUSTANG____6 | 3 Phase fault on YOAKUM 6 (526935) 230 kV Bus a. Apply fault at the YOAKUM 6 (526935) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. YOAKUM 6 230.0 KV 526935 TO MUSTANG 6 230.0 KV 527149 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_345__526935_0 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345( 526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 526936 TO YOAKUM 6 526935 TO YOAKUM_TR1 526937 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_345__CROSSROADS_7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_345__CROSSROADS_7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO CROSSROADS 7 345.0 KV 527656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM_345__HOBBS_INT__7 | 3 Phase fault on YOAKUM_345 (526936) 345 kV Bus a. Apply fault at the YOAKUM_345 (526936) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. YOAKUM_345 345.0 KV 526936 TO HOBBS_INT 7 345.0 KV 527896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM345_345kV_526936 | Apply single-phase fault on: TUCOINT7 345KV 525832 TO YOAKUM345 345KV 526936 CKT 1, near YOAKUM345 345kV for 6 cycles with stuck breaker at YOAKUM345 345kV. Clear Fault after 16 cycles and trip: YOAKUM345 345KV 526936 TO HOBBSINT7 345KV 527896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM345_345kV_526936 | Apply single-phase fault on: TUCOINT7 345KV 525832 TO YOAKUM345 345KV 526936 CKT 1, near YOAKUM345 345kV for 6 cycles with stuck breaker at YOAKUM345 345kV. Clear Fault after 16 cycles and trip: YOAKUM345 345KV 526936 TO HOBBSINT7 345KV 527896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25S | Transfer | YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM6 230.0 KV 526935 TO BRUSUB6 230.0 KV 527009 CKT 1, near YOAKUM6 230kV for 7 cycles with stuck breaker at YOAKUM6 230kV. Clear Fault after 16 cycles and trip: YOAKUM6 230.0 KV 526935 TO MUSTANG6 230.0 KV 527149 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
05 - Southwest | 25W | Transfer | YOAKUM6_230kV_526935 | Apply single-phase fault on: YOAKUM6 230.0 KV 526935 TO BRUSUB6 230.0 KV 527009 CKT 1, near YOAKUM6 230kV for 7 cycles with stuck breaker at YOAKUM6 230kV. Clear Fault after 16 cycles and trip: YOAKUM6 230.0 KV 526935 TO MUSTANG6 230.0 KV 527149 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes

## Short Circuit Analysis
Gen Number | Group | Bus Number | Bus Name | Bus Voltage (kV) | Request Not In Service 25SP Fault Current 3-Phase (A) | Request In Service 25SP Fault Current 3-Phase (A) | Change in Fault Current (A) | Circuit Breakers Exceeding Capacity | Facilities Required to Interconnect
ASGI-2017-013 | 01 - North | 652284 | HURON 8 | 69 | 3826.1 | 4112.7 | 286.6
ASGI-2017-013 | 01 - North | 652515 | HURON 7 | 115 | 15663.1 | 15824.9 | 161.8
ASGI-2017-013 | 01 - North | 655053 | MOS-MILR-ER8 | 69 | 2486.5 | 2602.7 | 116.2
ASGI-2017-013 | 01 - North | 655055 | SW-YALE-ER8 | 69 | 1232.8 | 1258 | 25.2
ASGI-2017-013 | 01 - North | 655058 | MOS-HRON-ER8 | 69 | 2757.6 | 3053.1 | 295.5
ASGI-2017-013 | 01 - North | 655060 | MOS-POLO-ER8 | 69 | 1018.4 | 1036.9 | 18.5
ASGI-2017-013 | 01 - North | 655062 | MOS-YALE-ER8 | 69 | 1466 | 1502.7 | 36.7
ASGI-2017-013 | 01 - North | 655063 | SW-HURN1-ER8 | 69 | 3770.7 | 4057.7 | 287
ASGI-2017-013 | 01 - North | 655064 | SW-HURN4-ER8 | 69 | 3745.1 | 4019.2 | 274.1
ASGI-2017-013 | 01 - North | 655065 | MOS-YLTI-ER8 | 69 | 1705 | 1755.8 | 50.8
ASGI-2017-013 | 01 - North | 655066 | SW-HURN2-ER8 | 69 | 3809.9 | 4093.9 | 284
ASGI-2017-013 | 01 - North | 655067 | SW-HURN3-ER8 | 69 | 3814 | 4098.7 | 284.7
ASGI-2017-013 | 01 - North | 655069 | MOS-WOLS-ER8 | 69 | 2272.2 | 2571.3 | 299.1
ASGI-2017-013 | 01 - North | 655070 | MOS-VRCV-ER8 | 69 | 1252.9 | 1339.3 | 86.4
ASGI-2017-013 | 01 - North | 655071 | MOS-DAK-ER8 | 69 | 1069.3 | 1131.4 | 62.1
ASGI-2017-013 | 01 - North | 655228 | YALE-ER8 | 69 | 1214 | 1238.4 | 24.4
ASGI-2017-013 | 01 - North | 655231 | HURON-ER8 | 69 | 2754.5 | 3049.3 | 294.8
ASGI-2017-013 | 01 - North | 655233 | POLO-ER8 | 69 | 648.7 | 655.5 | 6.8
ASGI-2017-013 | 01 - North | 655234 | MILLER-ER8 | 69 | 1026.4 | 1045.2 | 18.8
ASGI-2017-013 | 01 - North | 655236 | MORNINGS-ER8 | 69 | 1950.5 | 2018.4 | 67.9
ASGI-2017-013 | 01 - North | 655237 | BONILLA-ER8 | 69 | 1677.4 | 1728.6 | 51.2
ASGI-2017-013 | 01 - North | 655239 | WOLSEY-ER8 | 69 | 1349.3 | 1652.8 | 303.5
ASGI-2017-013 | 01 - North | 655241 | VIRGIL-ER8 | 69 | 1881.9 | 2084.4 | 202.5
ASGI-2017-013 | 01 - North | 655242 | CAVOUR-ER8 | 69 | 1204.5 | 1284 | 79.5
ASGI-2017-013 | 01 - North | 655244 | DAKOTA-ER8 | 69 | 994.1 | 1047.5 | 53.4
ASGI-2017-013 | 01 - North | 655378 | NWPS3680-ER8 | 69 | 1043.7 | 1063.2 | 19.5
ASGI-2017-013 | 01 - North | 655509 | SW-MILRC-ER8 | 69 | 1055.6 | 1075.6 | 20
ASGI-2017-013 | 01 - North | 762350 | ASGI-2017-01 | 69 | Project Bus - Disconnected | 1652.8 | Project Bus - Disconnected
GEN-2018-008 | 01 - North | 67030 | MPC04000MPT | 230 | 11238 | 11238.5 | 0.5
GEN-2018-008 | 01 - North | 587030 | GEN-2016-004 | 230 | 7656 | 7664 | 8
GEN-2018-008 | 01 - North | 588210 | GEN-2016-130 | 345 | 12848.1 | 12906.9 | 58.8
GEN-2018-008 | 01 - North | 608597 | SQBP1DC4 | 230 | 24229.4 | 24231.8 | 2.4
GEN-2018-008 | 01 - North | 608599 | SQBP2DC4 | 230 | 24229.4 | 24231.8 | 2.4
GEN-2018-008 | 01 - North | 608600 | BISONMP4 | 230 | 8187.2 | 8187.3 | 0.1
GEN-2018-008 | 01 - North | 608602 | SQBEAST4 | 230 | 24229.4 | 24231.8 | 2.4
GEN-2018-008 | 01 - North | 608603 | TRICNTY4 | 230 | 5911.4 | 5911.4 | 0
GEN-2018-008 | 01 - North | 615600 | GRE-COAL CR4 | 230 | 19334 | 19335.7 | 1.7
GEN-2018-008 | 01 - North | 615601 | GRE-COAL FM8 | 69 | 9051.3 | 9051.5 | 0.2
GEN-2018-008 | 01 - North | 615604 | GRE-COALFB14 | 230 | 19334 | 19335.7 | 1.7
GEN-2018-008 | 01 - North | 615605 | GRE-COALFB24 | 230 | 19334 | 19335.7 | 1.7
GEN-2018-008 | 01 - North | 615606 | GRE-COALFB34 | 230 | 19334 | 19335.7 | 1.7
GEN-2018-008 | 01 - North | 615900 | GRE-COAL TP4 | 230 | 16266.5 | 16268.1 | 1.6
GEN-2018-008 | 01 - North | 615901 | GRE-STANTON4 | 230 | 18242.9 | 18246 | 3.1
GEN-2018-008 | 01 - North | 652250 | GROTON18 | 69 | 4323.9 | 4329.3 | 5.4
GEN-2018-008 | 01 - North | 652253 | GROTON2 8 | 69 | 1947.4 | 1948.5 | 1.1
GEN-2018-008 | 01 - North | 652257 | DEVAUL 8 | 69 | 1104.1 | 1104.2 | 0.1
GEN-2018-008 | 01 - North | 652424 | BELFELD3 | 345 | 6819.8 | 6821.7 | 1.9
GEN-2018-008 | 01 - North | 652426 | BISMARK4 | 230 | 15526.7 | 15531.4 | 4.7
GEN-2018-008 | 01 - North | 652441 | GARRISN4 | 230 | 12617.9 | 12623.4 | 5.5
GEN-2018-008 | 01 - North | 652442 | GARRISN7 | 115 | 15843.7 | 15846.5 | 2.8
GEN-2018-008 | 01 - North | 652444 | JAMESTN4 | 230 | 8881.2 | 8882.2 | 1
GEN-2018-008 | 01 - North | 652456 | WASHBRN4 | 230 | 10814.6 | 10826.8 | 12.2
GEN-2018-008 | 01 - North | 652466 | HILKEN 4 | 230 | 9261.9 | 9263.5 | 1.6
GEN-2018-008 | 01 - North | 652512 | GROTON 7 | 115 | 18921.4 | 19097.7 | 176.3
GEN-2018-008 | 01 - North | 652529 | WATERTN3 | 345 | 10691.8 | 10733.2 | 41.4
GEN-2018-008 | 01 - North | 652530 | WATERTN4 | 230 | 15167.5 | 15197.9 | 30.4
GEN-2018-008 | 01 - North | 652568 | GROTONSOUTH7 | 115 | 18975.4 | 19152.9 | 177.5
GEN-2018-008 | 01 - North | 652630 | WATERTNCAP 4 | 230 | 14987.9 | 15017.6 | 29.7
GEN-2018-008 | 01 - North | 652829 | WATERTN-LNX3 | 345 | 10684.1 | 10724.9 | 40.8
GEN-2018-008 | 01 - North | 655054 | MOS-RDFL-ER8 | 69 | 2143.3 | 2143.7 | 0.4
GEN-2018-008 | 01 - North | 655057 | MOS-LADL-ER8 | 69 | 1634.2 | 1634.4 | 0.2
GEN-2018-008 | 01 - North | 655059 | MOS-ASHT-ER8 | 69 | 1708.4 | 1708.6 | 0.2
GEN-2018-008 | 01 - North | 655061 | MOS-TULR-ER8 | 69 | 1544 | 1544.2 | 0.2
GEN-2018-008 | 01 - North | 655068 | MOS-CRKR-ER8 | 69 | 1530.1 | 1530.2 | 0.1
GEN-2018-008 | 01 - North | 655084 | SW519-ER8 | 69 | 1741 | 1741.9 | 0.9
GEN-2018-008 | 01 - North | 655090 | MOS-STRF-ER8 | 69 | 1827 | 1828 | 1
GEN-2018-008 | 01 - North | 655115 | MOS-CLRK-ER8 | 69 | 1201.9 | 1202 | 0.1
GEN-2018-008 | 01 - North | 655227 | REDFIELD-ER8 | 69 | 2090.3 | 2090.6 | 0.3
GEN-2018-008 | 01 - North | 655230 | LA DELLE-ER8 | 69 | 985.5 | 985.6 | 0.1
GEN-2018-008 | 01 - North | 655232 | ASHTON-ER8 | 69 | 1679 | 1679.2 | 0.2
GEN-2018-008 | 01 - North | 655235 | TULARE-ER8 | 69 | 1150.2 | 1150.4 | 0.2
GEN-2018-008 | 01 - North | 655238 | FRANKFRT-ER8 | 69 | 2184.1 | 2184.5 | 0.4
GEN-2018-008 | 01 - North | 655243 | CROCKER-ER8 | 69 | 1424.7 | 1424.8 | 0.1
GEN-2018-008 | 01 - North | 655256 | FERNEY-ER8 | 69 | 2917.2 | 2919.7 | 2.5
GEN-2018-008 | 01 - North | 655257 | ANDOVER-ER8 | 69 | 1653.7 | 1654.4 | 0.7
GEN-2018-008 | 01 - North | 655261 | MANFIELD-ER8 | 69 | 1299.3 | 1299.8 | 0.5
GEN-2018-008 | 01 - North | 655267 | GROTON-ER8 | 69 | 2777.4 | 2779.7 | 2.3
GEN-2018-008 | 01 - North | 655270 | CRESBARD-ER8 | 69 | 747.7 | 747.9 | 0.2
GEN-2018-008 | 01 - North | 655336 | BURKMERE-ER8 | 69 | 542.9 | 543 | 0.1
GEN-2018-008 | 01 - North | 655350 | WOODLAND-ER8 | 69 | 1273.8 | 1273.9 | 0.1
GEN-2018-008 | 01 - North | 655395 | NWPS509-ER8 | 69 | 4314.4 | 4319.9 | 5.5
GEN-2018-008 | 01 - North | 655399 | NWECLKTI-ER8 | 69 | 1158.7 | 1158.8 | 0.1
GEN-2018-008 | 01 - North | 655411 | CRANDALL-ER7 | 115 | 6878.8 | 6893.5 | 14.7
GEN-2018-008 | 01 - North | 655419 | SW561-ER7 | 115 | 7192.4 | 7208.6 | 16.2
GEN-2018-008 | 01 - North | 655421 | MOS-CRSB-ER8 | 69 | 748.2 | 748.4 | 0.2
GEN-2018-008 | 01 - North | 655422 | MOS-MNFD-ER8 | 69 | 1299.9 | 1300.4 | 0.5
GEN-2018-008 | 01 - North | 655481 | REDFELD-ER7 | 115 | 4312.4 | 4315.2 | 2.8
GEN-2018-008 | 01 - North | 655482 | REDFELD-ER8 | 69 | 2943 | 2943.7 | 0.7
GEN-2018-008 | 01 - North | 655731 | LARK -MG8 | 69 | 975.8 | 975.8 | 0
GEN-2018-008 | 01 - North | 655732 | FLASHER -MG8 | 69 | 902.8 | 902.9 | 0.1
GEN-2018-008 | 01 - North | 655740 | CANNON -MG8 | 69 | 909.6 | 909.7 | 0.1
GEN-2018-008 | 01 - North | 655741 | CEDAR -MG8 | 69 | 689.4 | 689.5 | 0.1
GEN-2018-008 | 01 - North | 655742 | GRANT -MG8 | 69 | 617.7 | 617.7 | 0
GEN-2018-008 | 01 - North | 655744 | DEVALTP -MG8 | 69 | 1110.4 | 1110.4 | 0
GEN-2018-008 | 01 - North | 655746 | DEVAUL -MG8 | 69 | 1116.3 | 1116.3 | 0
GEN-2018-008 | 01 - North | 655747 | DEVAUL -MG7 | 115 | 1107.4 | 1107.4 | 0
GEN-2018-008 | 01 - North | 655748 | NEWSALEM-MG7 | 115 | 1513.9 | 1514 | 0.1
GEN-2018-008 | 01 - North | 655749 | MANSWTCH-MG7 | 115 | 1023.3 | 1023.4 | 0.1
GEN-2018-008 | 01 - North | 655750 | ROUGHRDR-MG7 | 115 | 990.7 | 990.8 | 0.1
GEN-2018-008 | 01 - North | 655751 | NRWSTMDN-MG7 | 115 | 991.1 | 991.2 | 0.1
GEN-2018-008 | 01 - North | 655752 | NWMDNTAP-MG7 | 115 | 1551.6 | 1551.8 | 0.2
GEN-2018-008 | 01 - North | 655830 | MOUNTAIN-MK7 | 115 | 4188.3 | 4188.8 | 0.5
GEN-2018-008 | 01 - North | 655831 | J12_____-MK7 | 115 | 4059 | 4059.3 | 0.3
GEN-2018-008 | 01 - North | 655832 | BLUEBUTE-MK7 | 115 | 7972.1 | 7973.4 | 1.3
GEN-2018-008 | 01 - North | 655833 | GRSYBTTP-MK7 | 115 | 14098.1 | 14101.7 | 3.6
GEN-2018-008 | 01 - North | 655834 | GRASSYBT-MK7 | 115 | 6940.1 | 6941 | 0.9
GEN-2018-008 | 01 - North | 655835 | LITTLKNF-MK7 | 115 | 3126.9 | 3127.2 | 0.3
GEN-2018-008 | 01 - North | 655836 | OAKDALE -MK7 | 115 | 5551.7 | 5552.5 | 0.8
GEN-2018-008 | 01 - North | 655837 | ELMTREE -MK7 | 115 | 3659 | 3659.2 | 0.2
GEN-2018-008 | 01 - North | 655838 | INDIANHL-MK7 | 115 | 4066.9 | 4067.2 | 0.3
GEN-2018-008 | 01 - North | 655842 | HAYBUTTE-MK7 | 115 | 3269 | 3269.1 | 0.1
GEN-2018-008 | 01 - North | 655844 | TIMBERCK-MK7 | 115 | 5244.4 | 5244.8 | 0.4
GEN-2018-008 | 01 - North | 655846 | F9______-MK7 | 115 | 4169.2 | 4169.4 | 0.2
GEN-2018-008 | 01 - North | 655847 | SWENSON -MK7 | 115 | 4317.7 | 4318 | 0.3
GEN-2018-008 | 01 - North | 655848 | BERG -MK7 | 115 | 5732.9 | 5733.5 | 0.6
GEN-2018-008 | 01 - North | 655849 | VEEDER -MK7 | 115 | 9808.7 | 9810.7 | 2
GEN-2018-008 | 01 - North | 655850 | NRTINDHL-MK7 | 115 | 3470.9 | 3471 | 0.1
GEN-2018-008 | 01 - North | 655851 | BIGGULCH-MK7 | 115 | 2917.5 | 2917.7 | 0.2
GEN-2018-008 | 01 - North | 655852 | L11_____-MK7 | 115 | 3570.5 | 3570.8 | 0.3
GEN-2018-008 | 01 - North | 655853 | BEARCREK-MK7 | 115 | 8387.5 | 8389.2 | 1.7
GEN-2018-008 | 01 - North | 655854 | SANDCREK-MK7 | 115 | 3525.9 | 3526.2 | 0.3
GEN-2018-008 | 01 - North | 655856 | STNJOHNY-MK7 | 115 | 6502.5 | 6503.1 | 0.6
GEN-2018-008 | 01 - North | 655857 | MOCCASIN-MK7 | 115 | 2589.5 | 2589.6 | 0.1
GEN-2018-008 | 01 - North | 655858 | TABLEBUT-MK7 | 115 | 4349.6 | 4350 | 0.4
GEN-2018-008 | 01 - North | 655859 | CHARLSON-MK7 | 115 | 3736.6 | 3736.9 | 0.3
GEN-2018-008 | 01 - North | 655861 | HORSECRK-MK7 | 115 | 2319.8 | 2319.9 | 0.1
GEN-2018-008 | 01 - North | 655863 | CARTWRIT-MK7 | 115 | 3130.8 | 3131 | 0.2
GEN-2018-008 | 01 - North | 655864 | GRAIL -MK7 | 115 | 5746.6 | 5747.3 | 0.7
GEN-2018-008 | 01 - North | 655865 | STATION8-MK7 | 115 | 5893.5 | 5894.2 | 0.7
GEN-2018-008 | 01 - North | 655866 | SNDCRKTP-MK7 | 115 | 4066.9 | 4067.2 | 0.3
GEN-2018-008 | 01 - North | 655867 | TWNVLYTP-MK7 | 115 | 2990.1 | 2990.2 | 0.1
GEN-2018-008 | 01 - North | 655869 | TWINVLLY-MK7 | 115 | 2756.6 | 2756.7 | 0.1
GEN-2018-008 | 01 - North | 655870 | TBGARDEN-MK7 | 115 | 2656.3 | 2656.4 | 0.1
GEN-2018-008 | 01 - North | 655871 | G9______-MK7 | 115 | 3920.2 | 3920.4 | 0.2
GEN-2018-008 | 01 - North | 655872 | G9TAP___-MK7 | 115 | 4534.5 | 4534.8 | 0.3
GEN-2018-008 | 01 - North | 655873 | BBCOMPTP-MK7 | 115 | 6952.4 | 6953.4 | 1
GEN-2018-008 | 01 - North | 655874 | BBCMPRSS-MK7 | 115 | 6349.9 | 6350.7 | 0.8
GEN-2018-008 | 01 - North | 655880 | SCHAFR_T-MK7 | 115 | 5765.6 | 5766.2 | 0.6
GEN-2018-008 | 01 - North | 655881 | DAP_____-MK7 | 115 | 13057.3 | 13060.7 | 3.4
GEN-2018-008 | 01 - North | 655882 | GALAXYTP-MK7 | 115 | 9858 | 9860 | 2
GEN-2018-008 | 01 - North | 655883 | GALAXY -MK7 | 115 | 7771.1 | 7772.3 | 1.2
GEN-2018-008 | 01 - North | 655884 | DEMCKSLK-MK7 | 115 | 5432 | 5432.6 | 0.6
GEN-2018-008 | 01 - North | 655885 | NRTHFORK-MK7 | 115 | 4240.4 | 4240.8 | 0.4
GEN-2018-008 | 01 - North | 655886 | KEENE -MK7 | 115 | 5050.5 | 5051 | 0.5
GEN-2018-008 | 01 - North | 655888 | BANKS -MK7 | 115 | 3448.8 | 3449 | 0.2
GEN-2018-008 | 01 - North | 655889 | LC_GAS_P-MK7 | 115 | 6241.3 | 6241.8 | 0.5
GEN-2018-008 | 01 - North | 655892 | ALEXANDR-MK7 | 115 | 4013.5 | 4013.8 | 0.3
GEN-2018-008 | 01 - North | 655893 | DUNNCNTR-MK7 | 115 | 6269.4 | 6270.4 | 1
GEN-2018-008 | 01 - North | 655894 | HALLIDAY-MK7 | 115 | 3551.5 | 3551.8 | 0.3
GEN-2018-008 | 01 - North | 655896 | KEENECRN-MK7 | 115 | 3453.2 | 3453.5 | 0.3
GEN-2018-008 | 01 - North | 655897 | COYOTCHR-MK7 | 115 | 5297.1 | 5297.7 | 0.6
GEN-2018-008 | 01 - North | 655899 | FNCYBTAP-MK7 | 115 | 6391 | 6391.8 | 0.8
GEN-2018-008 | 01 - North | 655905 | RBNSNLAK-MW7 | 115 | 10539.9 | 10542.2 | 2.3
GEN-2018-008 | 01 - North | 655906 | FINSTAD -MW7 | 115 | 20610.9 | 20622 | 11.1
GEN-2018-008 | 01 - North | 655919 | OSBORN -MW7 | 115 | 12206.5 | 12209.8 | 3.3
GEN-2018-008 | 01 - North | 655920 | VANHOOK -MW7 | 115 | 13615 | 13619.3 | 4.3
GEN-2018-008 | 01 - North | 657756 | SQBUTTE4 | 230 | 24229.4 | 24231.8 | 2.4
GEN-2018-008 | 01 - North | 657848 | YNG2 4 | 230 | 19565.4 | 19566.7 | 1.3
GEN-2018-008 | 01 - North | 659060 | FINSTAD345 | 345 | 7376.2 | 7380.7 | 4.5
GEN-2018-008 | 01 - North | 659101 | ANTELOPE-BE3 | 345 | 20272.1 | 20327.2 | 55.1
GEN-2018-008 | 01 - North | 659105 | LELAND_O-BE3 | 345 | 19711.2 | 19853 | 141.8
GEN-2018-008 | 01 - North | 659106 | LELAND_O-BE4 | 230 | 25697.7 | 25799.7 | 102
GEN-2018-008 | 01 - North | 659108 | LOGAN___-BE4 | 230 | 6656.3 | 6658.3 | 2
GEN-2018-008 | 01 - North | 659109 | BASIN___-BE7 | 115 | 5426.4 | 5428.6 | 2.2
GEN-2018-008 | 01 - North | 659130 | CHAPELLE-BE3 | 345 | 7044.7 | 7046.1 | 1.4
GEN-2018-008 | 01 - North | 659143 | BLAISDEL-BE4 | 230 | 6301.2 | 6302.4 | 1.2
GEN-2018-008 | 01 - North | 659155 | LOGAN___-BE7 | 115 | 11297.7 | 11299.4 | 1.7
GEN-2018-008 | 01 - North | 659160 | GROTON__-BE3 | 345 | 6462.9 | 6614.9 | 152
GEN-2018-008 | 01 - North | 659165 | G09_001IST | 345 | 6581.1 | 6668 | 86.9
GEN-2018-008 | 01 - North | 659182 | CHARL_CK-BE7 | 115 | 14220.5 | 14224.2 | 3.7
GEN-2018-008 | 01 - North | 659183 | CHARL_CK-BE3 | 345 | 10964.2 | 10971.5 | 7.3
GEN-2018-008 | 01 - North | 659185 | FOUREYES-RR7 | 115 | 3740.5 | 3740.8 | 0.3
GEN-2018-008 | 01 - North | 659187 | GROTON__-BE7 | 115 | 18932.9 | 19111.7 | 178.8
GEN-2018-008 | 01 - North | 659198 | GROTON__-BE8 | 115 | 9890.5 | 10007.6 | 117.1
GEN-2018-008 | 01 - North | 659199 | BASIN___-BE4 | 230 | 23275.1 | 23358.3 | 83.2
GEN-2018-008 | 01 - North | 659212 | DGC_____-BE3 | 345 | 19163.5 | 19212.6 | 49.1
GEN-2018-008 | 01 - North | 659218 | COTEAU__-RR3 | 345 | 20272.1 | 20327.2 | 55.1
GEN-2018-008 | 01 - North | 659222 | COTEAU_1-RR8 | 69 | 9870.9 | 9873.5 | 2.6
GEN-2018-008 | 01 - North | 659233 | DGC_____-BE4 | 230 | 7687.2 | 7692.5 | 5.3
GEN-2018-008 | 01 - North | 659236 | DGC UREA-BE8 | 69 | 7402.3 | 7403.8 | 1.5
GEN-2018-008 | 01 - North | 659275 | GROTON_G-BE7 | 115 | 18475.5 | 18639 | 163.5
GEN-2018-008 | 01 - North | 659284 | ECKLUND_-PP4 | 230 | 8108.6 | 8109.8 | 1.2
GEN-2018-008 | 01 - North | 659288 | DAY_CNTY-PP7 | 115 | 5760.6 | 5767.1 | 6.5
GEN-2018-008 | 01 - North | 659302 | CHARL_CK-BE4 | 230 | 11781.1 | 11786.4 | 5.3
GEN-2018-008 | 01 - North | 659310 | ORDWAY__-BE7 | 115 | 7906.5 | 7930.9 | 24.4
GEN-2018-008 | 01 - North | 659336 | TANDE___-BE3 | 345 | 8904.8 | 8908.3 | 3.5
GEN-2018-008 | 01 - North | 659337 | TANDE___-BE4 | 230 | 13096.9 | 13100.9 | 4
GEN-2018-008 | 01 - North | 659348 | LC_CT1-3-BE7 | 115 | 12280.7 | 12282.1 | 1.4
GEN-2018-008 | 01 - North | 659349 | LC_SWY.N-BE7 | 115 | 12280.8 | 12282.2 | 1.4
GEN-2018-008 | 01 - North | 659365 | BALDWIN_-PP4 | 230 | 8108.6 | 8109.8 | 1.2
GEN-2018-008 | 01 - North | 659384 | ROUNDUP_-BE3 | 345 | 9956 | 9963.2 | 7.2
GEN-2018-008 | 01 - North | 659385 | ROUNDUP_-MK7 | 115 | 12045 | 12048.6 | 3.6
GEN-2018-008 | 01 - North | 659387 | KUMMERDG-BE3 | 345 | 7524.2 | 7527.7 | 3.5
GEN-2018-008 | 01 - North | 659388 | KUMMERDG-MK7 | 115 | 14479.3 | 14483.6 | 4.3
GEN-2018-008 | 01 - North | 659390 | PATENTGT-BE3 | 345 | 9022.4 | 9026.3 | 3.9
GEN-2018-008 | 01 - North | 659391 | PATENTGT-MK7 | 115 | 18138.2 | 18142.7 | 4.5
GEN-2018-008 | 01 - North | 659404 | BURKE___-PP3 | 345 | 4861.9 | 4862.8 | 0.9
GEN-2018-008 | 01 - North | 659420 | AV.LS-BD-BE3 | 345 | 20272.1 | 20327.2 | 55.1
GEN-2018-008 | 01 - North | 659421 | BD.LS-AV-BE3 | 345 | 4825.4 | 4827.6 | 2.2
GEN-2018-008 | 01 - North | 659422 | LO.LS-GR-BE3 | 345 | 19711.2 | 19853 | 141.8
GEN-2018-008 | 01 - North | 659423 | GR.LS-LO-BE3 | 345 | 6462.9 | 6614.9 | 152
GEN-2018-008 | 01 - North | 659424 | LO.LS-FT-BE3 | 345 | 19711.2 | 19853 | 141.8
GEN-2018-008 | 01 - North | 659427 | TN.LS-JD-BE3 | 345 | 8904.8 | 8908.3 | 3.5
GEN-2018-008 | 01 - North | 659428 | CC.LS-LO-BE3 | 345 | 7006.2 | 7007.6 | 1.4
GEN-2018-008 | 01 - North | 659433 | TRIPLEH__UA3 | 345 | 6971.6 | 6972.9 | 1.3
GEN-2018-008 | 01 - North | 659466 | PG.KU17A-BE7 | 115 | 18040.4 | 18044.8 | 4.4
GEN-2018-008 | 01 - North | 659467 | PG.KU19A-BE7 | 115 | 18052 | 18056.5 | 4.5
GEN-2018-008 | 01 - North | 659472 | CROCKER_-UA3 | 345 | 5664.8 | 5727.5 | 62.7
GEN-2018-008 | 01 - North | 659479 | TRADEWND-UA3 | 345 | 6287.3 | 6288.9 | 1.6
GEN-2018-008 | 01 - North | 659576 | BEPCPRXCC1 3 | 345 | 19420.4 | 19469.5 | 49.1
GEN-2018-008 | 01 - North | 659584 | BEPCPRXCC3 7 | 115 | 14231.7 | 14235.8 | 4.1
GEN-2018-008 | 01 - North | 660430 | GROTON | 69 | 1610.3 | 1611 | 0.7
GEN-2018-008 | 01 - North | 660431 | GROTON CITY | 69 | 1596.9 | 1597.7 | 0.8
GEN-2018-008 | 01 - North | 660432 | ANDOVER | 69 | 1219 | 1219.4 | 0.4
GEN-2018-008 | 01 - North | 660433 | BRISTOL JCT | 69 | 843.3 | 843.5 | 0.2
GEN-2018-008 | 01 - North | 660440 | WEBSTER NW | 69 | 714.8 | 714.9 | 0.1
GEN-2018-008 | 01 - North | 660441 | WEBSTER CITY | 69 | 690 | 690.1 | 0.1
GEN-2018-008 | 01 - North | 760998 | GEN-2017-214 | 230 | 3372.3 | 3372.7 | 0.4
GEN-2018-008 | 01 - North | 762537 | GEN-2018-008 | 345 | Project Bus - Disconnected | 4454.1 | Project Bus - Disconnected
GEN-2018-008 | 01 - North | 762544 | G18-008-TAP | 345 | 3972.9 | 4458.5 | 485.6
GEN-2018-010 | 01 - North | 587030 | GEN-2016-004 | 230 | 7663.1 | 7664 | 0.9
GEN-2018-010 | 01 - North | 588210 | GEN-2016-130 | 345 | 12901.6 | 12906.9 | 5.3
GEN-2018-010 | 01 - North | 588870 | GEN-2017-048 | 230 | 9863.1 | 10082.6 | 219.5
GEN-2018-010 | 01 - North | 603023 | MALLARD7 | 115 | 11460.5 | 11464.9 | 4.4
GEN-2018-010 | 01 - North | 615901 | GRE-STANTON4 | 230 | 18245.3 | 18246 | 0.7
GEN-2018-010 | 01 - North | 652216 | WATFORD4 | 230 | 6833.9 | 6839.1 | 5.2
GEN-2018-010 | 01 - North | 652257 | DEVAUL 8 | 69 | 1104.2 | 1104.2 | 0
GEN-2018-010 | 01 - North | 652391 | WILLISTON27 | 115 | 18714.8 | 18749.8 | 35
GEN-2018-010 | 01 - North | 652400 | WILISTN4 | 230 | 11434.6 | 11468.6 | 34
GEN-2018-010 | 01 - North | 652408 | WATFORD7 | 115 | 8681.3 | 8684.4 | 3.1
GEN-2018-010 | 01 - North | 652421 | WILISTN7 | 115 | 18706.7 | 18741.6 | 34.9
GEN-2018-010 | 01 - North | 652441 | GARRISN4 | 230 | 12622.1 | 12623.4 | 1.3
GEN-2018-010 | 01 - North | 652456 | WASHBRN4 | 230 | 10825.3 | 10826.8 | 1.5
GEN-2018-010 | 01 - North | 652651 | FAIRVIEW 7 | 115 | 5041.2 | 5042.1 | 0.9
GEN-2018-010 | 01 - North | 655641 | BERTHOLD-CP7 | 115 | 6426.6 | 6432.6 | 6
GEN-2018-010 | 01 - North | 655657 | SW.MINOT-CP7 | 115 | 8246.9 | 8250.8 | 3.9
GEN-2018-010 | 01 - North | 655731 | LARK -MG8 | 69 | 975.8 | 975.8 | 0
GEN-2018-010 | 01 - North | 655732 | FLASHER -MG8 | 69 | 902.9 | 902.9 | 0
GEN-2018-010 | 01 - North | 655740 | CANNON -MG8 | 69 | 909.7 | 909.7 | 0
GEN-2018-010 | 01 - North | 655741 | CEDAR -MG8 | 69 | 689.5 | 689.5 | 0
GEN-2018-010 | 01 - North | 655742 | GRANT -MG8 | 69 | 617.7 | 617.7 | 0
GEN-2018-010 | 01 - North | 655744 | DEVALTP -MG8 | 69 | 1110.4 | 1110.4 | 0
GEN-2018-010 | 01 - North | 655746 | DEVAUL -MG8 | 69 | 1116.3 | 1116.3 | 0
GEN-2018-010 | 01 - North | 655747 | DEVAUL -MG7 | 115 | 1107.4 | 1107.4 | 0
GEN-2018-010 | 01 - North | 655748 | NEWSALEM-MG7 | 115 | 1514 | 1514 | 0
GEN-2018-010 | 01 - North | 655749 | MANSWTCH-MG7 | 115 | 1023.3 | 1023.4 | 0.1
GEN-2018-010 | 01 - North | 655750 | ROUGHRDR-MG7 | 115 | 990.8 | 990.8 | 0
GEN-2018-010 | 01 - North | 655751 | NRWSTMDN-MG7 | 115 | 991.2 | 991.2 | 0
GEN-2018-010 | 01 - North | 655752 | NWMDNTAP-MG7 | 115 | 1551.7 | 1551.8 | 0.1
GEN-2018-010 | 01 - North | 655780 | NORMANLK-BD7 | 115 | 3207.3 | 3210.2 | 2.9
GEN-2018-010 | 01 - North | 655781 | LARSON -BD7 | 115 | 2210.2 | 2211.6 | 1.4
GEN-2018-010 | 01 - North | 655782 | LIGNIBRD-BD7 | 115 | 1547.5 | 1548.1 | 0.6
GEN-2018-010 | 01 - North | 655783 | HAWKEYE -BD7 | 115 | 1477.1 | 1477.7 | 0.6
GEN-2018-010 | 01 - North | 655784 | AMBROSE -BD7 | 115 | 1249.6 | 1250.1 | 0.5
GEN-2018-010 | 01 - North | 655791 | SPRINGLK-LY7 | 115 | 1985.9 | 1986 | 0.1
GEN-2018-010 | 01 - North | 655792 | NOHLEY -LY7 | 115 | 3572.7 | 3573.2 | 0.5
GEN-2018-010 | 01 - North | 655793 | MARLEY -LY7 | 115 | 6011.9 | 6015.5 | 3.6
GEN-2018-010 | 01 - North | 655840 | CHRRYCRK-MK7 | 115 | 8681.3 | 8684.4 | 3.1
GEN-2018-010 | 01 - North | 655841 | ARNEGARD-MK7 | 115 | 6723.7 | 6724.8 | 1.1
GEN-2018-010 | 01 - North | 655845 | GRDNCRK2-MK7 | 115 | 4648.9 | 4649.8 | 0.9
GEN-2018-010 | 01 - North | 655855 | ROOSEVLT-MK7 | 115 | 4789.9 | 4790.8 | 0.9
GEN-2018-010 | 01 - North | 655875 | DPLWC___-MK7 | 115 | 7599.5 | 7601.9 | 2.4
GEN-2018-010 | 01 - North | 655876 | DPLWCTAP-MK7 | 115 | 8349 | 8351.9 | 2.9
GEN-2018-010 | 01 - North | 655877 | LITTLMS4-MK7 | 115 | 5249.7 | 5250.8 | 1.1
GEN-2018-010 | 01 - North | 655878 | CRESTWD_-MK7 | 115 | 3914.4 | 3915 | 0.6
GEN-2018-010 | 01 - North | 655879 | OASIS___-MK7 | 115 | 4684.5 | 4685.4 | 0.9
GEN-2018-010 | 01 - North | 655895 | GARDN-FB-MK7 | 115 | 4288.3 | 4289.1 | 0.8
GEN-2018-010 | 01 - North | 655898 | SCHAFER -MK7 | 115 | 3107.5 | 3107.9 | 0.4
GEN-2018-010 | 01 - North | 655900 | MOE -MW7 | 115 | 8641 | 8656.2 | 15.2
GEN-2018-010 | 01 - North | 655901 | BROOKBNK-MW7 | 115 | 11011.1 | 11028.5 | 17.4
GEN-2018-010 | 01 - North | 655902 | PLSNTV_T-MW7 | 115 | 8508.8 | 8527.1 | 18.3
GEN-2018-010 | 01 - North | 655903 | ROSS -MW7 | 115 | 9253.8 | 9265.2 | 11.4
GEN-2018-010 | 01 - North | 655904 | BELDEN -MW7 | 115 | 10093.4 | 10109.6 | 16.2
GEN-2018-010 | 01 - North | 655905 | RBNSNLAK-MW7 | 115 | 10523.7 | 10542.2 | 18.5
GEN-2018-010 | 01 - North | 655906 | FINSTAD -MW7 | 115 | 20548.5 | 20622 | 73.5
GEN-2018-010 | 01 - North | 655907 | E.NEWTWN-MW7 | 115 | 12393.6 | 12418.6 | 25
GEN-2018-010 | 01 - North | 655909 | HESS GAS-MW7 | 115 | 11881.1 | 11928.3 | 47.2
GEN-2018-010 | 01 - North | 655910 | LINDAHLS-MW7 | 115 | 5893.4 | 5903.2 | 9.8
GEN-2018-010 | 01 - North | 655911 | SIMPSON -MW7 | 115 | 3979.4 | 3983.9 | 4.5
GEN-2018-010 | 01 - North | 655912 | AUSTIN -MW7 | 115 | 6716.8 | 6724 | 7.2
GEN-2018-010 | 01 - North | 655913 | PLSNTVAL-MW7 | 115 | 8456.6 | 8474.7 | 18.1
GEN-2018-010 | 01 - North | 655914 | NE.ROSS_-MW7 | 115 | 4325.3 | 4328.5 | 3.2
GEN-2018-010 | 01 - North | 655916 | PALERMO -MW7 | 115 | 7427.3 | 7436.9 | 9.6
GEN-2018-010 | 01 - North | 655917 | STANLEY -MW7 | 115 | 7186.6 | 7195.4 | 8.8
GEN-2018-010 | 01 - North | 655918 | PALGASPL-MW7 | 115 | 6244.3 | 6251.1 | 6.8
GEN-2018-010 | 01 - North | 655919 | OSBORN -MW7 | 115 | 12185.3 | 12209.8 | 24.5
GEN-2018-010 | 01 - North | 655920 | VANHOOK -MW7 | 115 | 13588.9 | 13619.3 | 30.4
GEN-2018-010 | 01 - North | 655921 | LOSTWOOD-MW7 | 115 | 3551 | 3553.1 | 2.1
GEN-2018-010 | 01 - North | 655922 | W.BANK__-MW7 | 115 | 7459.8 | 7476.1 | 16.3
GEN-2018-010 | 01 - North | 655923 | FARMVALE-MW7 | 115 | 4642.3 | 4648.5 | 6.2
GEN-2018-010 | 01 - North | 655925 | JUDSON -MW7 | 115 | 14755.8 | 14775.9 | 20.1
GEN-2018-010 | 01 - North | 655926 | SW.WLSTN-MW7 | 115 | 8506.2 | 8512.8 | 6.6
GEN-2018-010 | 01 - North | 655929 | RATLAKE -MW7 | 115 | 13691.1 | 13718.3 | 27.2
GEN-2018-010 | 01 - North | 655930 | WHTEARTH-MW7 | 115 | 12882.8 | 12938.2 | 55.4
GEN-2018-010 | 01 - North | 655935 | NW.WLSTN-MW7 | 115 | 12023 | 12040.7 | 17.7
GEN-2018-010 | 01 - North | 655940 | MONT -MW7 | 115 | 14070.7 | 14088.4 | 17.7
GEN-2018-010 | 01 - North | 655943 | FARMVL_T-MW7 | 115 | 7343.4 | 7358.7 | 15.3
GEN-2018-010 | 01 - North | 655944 | PLAZA -MW7 | 115 | 7006.9 | 7013.6 | 6.7
GEN-2018-010 | 01 - North | 655945 | WHEELS_T-MW7 | 115 | 9009.8 | 9030.1 | 20.3
GEN-2018-010 | 01 - North | 655946 | POWERSLK-MW7 | 115 | 4916.6 | 4924.1 | 7.5
GEN-2018-010 | 01 - North | 655947 | PWRSLKTP-MW7 | 115 | 7736.7 | 7755 | 18.3
GEN-2018-010 | 01 - North | 655948 | LIBERTY -MW7 | 115 | 6985.4 | 6999.9 | 14.5
GEN-2018-010 | 01 - North | 655949 | BLAISDEL-MW7 | 115 | 9080.4 | 9095.2 | 14.8
GEN-2018-010 | 01 - North | 655950 | LOSTWD_T-MW7 | 115 | 5865.8 | 5871.6 | 5.8
GEN-2018-010 | 01 - North | 655951 | NE.ROS_T-MW7 | 115 | 4861.9 | 4865.9 | 4
GEN-2018-010 | 01 - North | 655952 | TIOGA.N_-MW7 | 115 | 11927.2 | 11974.7 | 47.5
GEN-2018-010 | 01 - North | 655953 | W.BANK_T-MW7 | 115 | 8978.4 | 9004 | 25.6
GEN-2018-010 | 01 - North | 655954 | ELLISVIL-MW7 | 115 | 5902.6 | 5909.9 | 7.3
GEN-2018-010 | 01 - North | 655957 | EASTFORK-MW7 | 115 | 16163.6 | 16202.1 | 38.5
GEN-2018-010 | 01 - North | 655959 | EPPING -MW7 | 115 | 8020.7 | 8036.1 | 15.4
GEN-2018-010 | 01 - North | 655960 | BIGBEND -MW7 | 115 | 5546.6 | 5551.7 | 5.1
GEN-2018-010 | 01 - North | 655961 | HESSRAIL-MW7 | 115 | 6941.2 | 6956.2 | 15
GEN-2018-010 | 01 - North | 655962 | HESSRTAP-MW7 | 115 | 8365.2 | 8387 | 21.8
GEN-2018-010 | 01 - North | 655963 | HOWIE -MW7 | 115 | 4475.7 | 4479 | 3.3
GEN-2018-010 | 01 - North | 655965 | E.NESSON-MW7 | 115 | 6305.9 | 6314.1 | 8.2
GEN-2018-010 | 01 - North | 655966 | OLIVER -MW7 | 115 | 6671 | 6681.4 | 10.4
GEN-2018-010 | 01 - North | 655967 | SATTER -MW7 | 115 | 9639.6 | 9653.7 | 14.1
GEN-2018-010 | 01 - North | 655968 | MUSKRAT -MW7 | 115 | 4624.5 | 4628 | 3.5
GEN-2018-010 | 01 - North | 659060 | FINSTAD345 | 345 | 7352 | 7380.7 | 28.7
GEN-2018-010 | 01 - North | 659101 | ANTELOPE-BE3 | 345 | 20316.4 | 20327.2 | 10.8
GEN-2018-010 | 01 - North | 659105 | LELAND_O-BE3 | 345 | 19840.2 | 19853 | 12.8
GEN-2018-010 | 01 - North | 659106 | LELAND_O-BE4 | 230 | 25787.4 | 25799.7 | 12.3
GEN-2018-010 | 01 - North | 659108 | LOGAN___-BE4 | 230 | 6652 | 6658.3 | 6.3
GEN-2018-010 | 01 - North | 659109 | BASIN___-BE7 | 115 | 5428.4 | 5428.6 | 0.2
GEN-2018-010 | 01 - North | 659138 | NESET___-BE4 | 230 | 13105.5 | 13313 | 207.5
GEN-2018-010 | 01 - North | 659139 | NESET___-BE7 | 115 | 13596.5 | 13659.1 | 62.6
GEN-2018-010 | 01 - North | 659140 | NRTSHORE-BE4 | 230 | 6053 | 6083.1 | 30.1
GEN-2018-010 | 01 - North | 659141 | NRTSHORE-BE7 | 115 | 17546.3 | 17587.3 | 41
GEN-2018-010 | 01 - North | 659143 | BLAISDEL-BE4 | 230 | 6281.5 | 6302.4 | 20.9
GEN-2018-010 | 01 - North | 659144 | BLAISDEL-BE7 | 115 | 9394.3 | 9410.3 | 16
GEN-2018-010 | 01 - North | 659154 | LC_CT4-5-BE7 | 115 | 6523 | 6523.7 | 0.7
GEN-2018-010 | 01 - North | 659155 | LOGAN___-BE7 | 115 | 11293.5 | 11299.4 | 5.9
GEN-2018-010 | 01 - North | 659199 | BASIN___-BE4 | 230 | 23348.3 | 23358.3 | 10
GEN-2018-010 | 01 - North | 659212 | DGC_____-BE3 | 345 | 19203 | 19212.6 | 9.6
GEN-2018-010 | 01 - North | 659218 | COTEAU__-RR3 | 345 | 20316.4 | 20327.2 | 10.8
GEN-2018-010 | 01 - North | 659222 | COTEAU_1-RR8 | 69 | 9873 | 9873.5 | 0.5
GEN-2018-010 | 01 - North | 659233 | DGC_____-BE4 | 230 | 7691.5 | 7692.5 | 1
GEN-2018-010 | 01 - North | 659236 | DGC UREA-BE8 | 69 | 7403.5 | 7403.8 | 0.3
GEN-2018-010 | 01 - North | 659262 | CULBSN.E-BE7 | 115 | 5817.4 | 5818.2 | 0.8
GEN-2018-010 | 01 - North | 659269 | CULB_GEN-BE7 | 115 | 5707.3 | 5708 | 0.7
GEN-2018-010 | 01 - North | 659302 | CHARL_CK-BE4 | 230 | 11777.9 | 11786.4 | 8.5
GEN-2018-010 | 01 - North | 659308 | KENASTON-BE7 | 115 | 3479.8 | 3482.2 | 2.4
GEN-2018-010 | 01 - North | 659333 | JUDSON__-BE3 | 345 | 8610.6 | 8637.1 | 26.5
GEN-2018-010 | 01 - North | 659334 | JUDSON__-BE4 | 230 | 11367.2 | 11400.3 | 33.1
GEN-2018-010 | 01 - North | 659336 | TANDE___-BE3 | 345 | 8833.2 | 8908.3 | 75.1
GEN-2018-010 | 01 - North | 659337 | TANDE___-BE4 | 230 | 12911.1 | 13100.9 | 189.8
GEN-2018-010 | 01 - North | 659346 | LC_SWY.S-BE7 | 115 | 6518 | 6518.7 | 0.7
GEN-2018-010 | 01 - North | 659362 | WHEELOCK-BE4 | 230 | 7837.4 | 7876.9 | 39.5
GEN-2018-010 | 01 - North | 659363 | WHEELOCK-BE7 | 115 | 9221.5 | 9243.2 | 21.7
GEN-2018-010 | 01 - North | 659404 | BURKE___-PP3 | 345 | 4842 | 4862.8 | 20.8
GEN-2018-010 | 01 - North | 659422 | LO.LS-GR-BE3 | 345 | 19840.2 | 19853 | 12.8
GEN-2018-010 | 01 - North | 659424 | LO.LS-FT-BE3 | 345 | 19840.2 | 19853 | 12.8
GEN-2018-010 | 01 - North | 659427 | TN.LS-JD-BE3 | 345 | 8833.2 | 8908.3 | 75.1
GEN-2018-010 | 01 - North | 659454 | LINDAHLWND 7 | 115 | 5423.8 | 5431.8 | 8
GEN-2018-010 | 01 - North | 659479 | TRADEWND-UA3 | 345 | 6253.3 | 6288.9 | 35.6
GEN-2018-010 | 01 - North | 659576 | BEPCPRXCC1 3 | 345 | 19459.9 | 19469.5 | 9.6
GEN-2018-010 | 01 - North | 659580 | BEPCPRXCC2 7 | 115 | 17507.5 | 17547.6 | 40.1
GEN-2018-010 | 01 - North | 659600 | EFORK_-BE334 | 345 | 7870.5 | 7901 | 30.5
GEN-2018-010 | 01 - North | 661003 | WATFRDSOUTH4 | 230 | 6762.4 | 6767.4 | 5
GEN-2018-010 | 01 - North | 661052 | KENMARE7 | 115 | 3400.8 | 3403.2 | 2.4
GEN-2018-010 | 01 - North | 661080 | STANLEY7 | 115 | 3964.3 | 3968.5 | 4.2
GEN-2018-010 | 01 - North | 661084 | TIOGA4 4 | 230 | 13105.5 | 13313 | 207.5
GEN-2018-010 | 01 - North | 661085 | TIOGA4 7 | 115 | 13540.3 | 13602.5 | 62.2
GEN-2018-010 | 01 - North | 661086 | TIOGA7 7 | 115 | 10352 | 10386.6 | 34.6
GEN-2018-010 | 01 - North | 661087 | RAY JCT7 | 115 | 5856.9 | 5865.2 | 8.3
GEN-2018-010 | 01 - North | 661089 | LTLMUDY7 | 115 | 7025.9 | 7033 | 7.1
GEN-2018-010 | 01 - North | 661281 | LIGNITE7 | 115 | 1592.1 | 1592.6 | 0.5
GEN-2018-010 | 01 - North | 672401 | BD 8 | 72 | 6414 | 6414.1 | 0.1
GEN-2018-010 | 01 - North | 672413 | AUBURNTON 8 | 72 | 11464.7 | 11464.9 | 0.2
GEN-2018-010 | 01 - North | 672501 | BD 6 | 138 | 14037.9 | 14039.2 | 1.3
GEN-2018-010 | 01 - North | 672521 | HALBRITE 6 | 138 | 1905.7 | 1905.7 | 0
GEN-2018-010 | 01 - North | 672601 | BD 4 | 230 | 15606.5 | 15609.4 | 2.9
GEN-2018-010 | 01 - North | 672602 | BDX 4 | 230 | 5036.5 | 5045.6 | 9.1
GEN-2018-010 | 01 - North | 672603 | BDV 4 | 230 | 5035.3 | 5044.5 | 9.2
GEN-2018-010 | 01 - North | 672613 | AUBURNTON 4 | 230 | 5767.4 | 5767.6 | 0.2
GEN-2018-010 | 01 - North | 672621 | SHAND 4 | 230 | 10989.9 | 10991 | 1.1
GEN-2018-010 | 01 - North | 672664 | ROWATT | 230 | 10169.3 | 10169.5 | 0.2
GEN-2018-010 | 01 - North | 673601 | KISBEY TAP 4 | 230 | 5692.1 | 5692.3 | 0.2
GEN-2018-010 | 01 - North | 673602 | KISBEY 4 | 230 | 4854.6 | 4854.8 | 0.2
GEN-2018-010 | 01 - North | 760998 | GEN-2017-214 | 230 | 3371.4 | 3372.7 | 1.3
GEN-2018-039 | 01 - North | 587030 | GEN-2016-004 | 230 | 7663.9 | 7664 | 0.1
GEN-2018-039 | 01 - North | 587050 | GEN-2016-007 | 115 | 4124.5 | 4127.7 | 3.2
GEN-2018-039 | 01 - North | 587720 | GEN-2016-087 | 230 | 4069.3 | 4069.4 | 0.1
GEN-2018-039 | 01 - North | 588210 | GEN-2016-130 | 345 | 12906.4 | 12906.9 | 0.5
GEN-2018-039 | 01 - North | 602006 | SHEYNNE4 | 230 | 11696.7 | 11702.9 | 6.2
GEN-2018-039 | 01 - North | 603018 | SHEYNNE7 | 115 | 13610.9 | 13614.5 | 3.6
GEN-2018-039 | 01 - North | 615901 | GRE-STANTON4 | 230 | 18245.4 | 18246 | 0.6
GEN-2018-039 | 01 - North | 620267 | DEVIL J7 | 115 | 5687.6 | 5688.5 | 0.9
GEN-2018-039 | 01 - North | 620268 | DEVIL S7 | 115 | 5544.6 | 5545.5 | 0.9
GEN-2018-039 | 01 - North | 620271 | AVIKO 7 | 115 | 7241.3 | 7241.5 | 0.2
GEN-2018-039 | 01 - North | 620272 | JAMESPK7 | 115 | 7424.7 | 7424.9 | 0.2
GEN-2018-039 | 01 - North | 620273 | JAMETAP7 | 115 | 7532 | 7532.1 | 0.1
GEN-2018-039 | 01 - North | 620274 | JAMSDTN7 | 115 | 7173.6 | 7173.8 | 0.2
GEN-2018-039 | 01 - North | 620337 | LAKE PARK T4 | 230 | 5873.3 | 5874.3 | 1
GEN-2018-039 | 01 - North | 620362 | OAKES 4 | 230 | 5620.8 | 5622.4 | 1.6
GEN-2018-039 | 01 - North | 620363 | FORMAN 4 | 230 | 5673.9 | 5676.5 | 2.6
GEN-2018-039 | 01 - North | 652203 | FARGO 8 | 69 | 12727 | 12729.5 | 2.5
GEN-2018-039 | 01 - North | 652204 | VALLEYC8 | 69 | 2650.4 | 2651.5 | 1.1
GEN-2018-039 | 01 - North | 652205 | LAKOTA 8 | 69 | 2121.2 | 2121.3 | 0.1
GEN-2018-039 | 01 - North | 652209 | SUMMIT-8 | 69 | 2932.4 | 2932.5 | 0.1
GEN-2018-039 | 01 - North | 652250 | GROTON18 | 69 | 4328.5 | 4329.3 | 0.8
GEN-2018-039 | 01 - North | 652253 | GROTON2 8 | 69 | 1948.3 | 1948.5 | 0.2
GEN-2018-039 | 01 - North | 652257 | DEVAUL 8 | 69 | 1104.2 | 1104.2 | 0
GEN-2018-039 | 01 - North | 652284 | HURON 8 | 69 | 4112.6 | 4112.7 | 0.1
GEN-2018-039 | 01 - North | 652296 | WARD 4 | 230 | 15090.3 | 15094.5 | 4.2
GEN-2018-039 | 01 - North | 652426 | BISMARK4 | 230 | 15525.1 | 15531.4 | 6.3
GEN-2018-039 | 01 - North | 652427 | BISMARK7 | 115 | 16620.1 | 16622.8 | 2.7
GEN-2018-039 | 01 - North | 652428 | CARNGTN7 | 115 | 2739.7 | 2742 | 2.3
GEN-2018-039 | 01 - North | 652431 | DEVILSL7 | 115 | 5673.8 | 5674.7 | 0.9
GEN-2018-039 | 01 - North | 652432 | EDGELEY7 | 115 | 4230.9 | 4614.3 | 383.4
GEN-2018-039 | 01 - North | 652433 | EDGELEY8 | 69 | 2862.2 | 2930.4 | 68.2
GEN-2018-039 | 01 - North | 652435 | FARGO 4 | 230 | 10721.1 | 10728 | 6.9
GEN-2018-039 | 01 - North | 652436 | FARGO 7 | 115 | 11547.6 | 11551.2 | 3.6
GEN-2018-039 | 01 - North | 652437 | GRNDFKS4 | 230 | 7814.3 | 7816.6 | 2.3
GEN-2018-039 | 01 - North | 652438 | FORMAN 7 | 115 | 6880 | 6886 | 6
GEN-2018-039 | 01 - North | 652441 | GARRISN4 | 230 | 12621.6 | 12623.4 | 1.8
GEN-2018-039 | 01 - North | 652442 | GARRISN7 | 115 | 15845.7 | 15846.5 | 0.8
GEN-2018-039 | 01 - North | 652443 | GRNDFKS7 | 115 | 12010.4 | 12012.9 | 2.5
GEN-2018-039 | 01 - North | 652444 | JAMESTN4 | 230 | 8849.6 | 8882.2 | 32.6
GEN-2018-039 | 01 - North | 652445 | JAMESTN7 | 115 | 10552.9 | 10645.3 | 92.4
GEN-2018-039 | 01 - North | 652448 | LAKOTA 7 | 115 | 2096.5 | 2096.6 | 0.1
GEN-2018-039 | 01 - North | 652454 | VALLEYC7 | 115 | 4565.6 | 4570.8 | 5.2
GEN-2018-039 | 01 - North | 652456 | WASHBRN4 | 230 | 10826 | 10826.8 | 0.8
GEN-2018-039 | 01 - North | 652462 | ELLIOTT7 | 115 | 3889 | 3891.4 | 2.4
GEN-2018-039 | 01 - North | 652465 | PENN 7 | 115 | 4246.8 | 4247.2 | 0.4
GEN-2018-039 | 01 - North | 652466 | HILKEN 4 | 230 | 9262.1 | 9263.5 | 1.4
GEN-2018-039 | 01 - North | 652496 | WINCHESTER4 | 230 | 4607.2 | 4607.5 | 0.3
GEN-2018-039 | 01 - North | 652499 | CAMPBELL 4 | 230 | 4069.3 | 4069.4 | 0.1
GEN-2018-039 | 01 - North | 652512 | GROTON 7 | 115 | 19071 | 19097.7 | 26.7
GEN-2018-039 | 01 - North | 652514 | HURON 4 | 230 | 11605.9 | 11606.5 | 0.6
GEN-2018-039 | 01 - North | 652515 | HURON 7 | 115 | 15824.2 | 15824.9 | 0.7
GEN-2018-039 | 01 - North | 652522 | SUMMIT-7 | 115 | 5565.9 | 5566.9 | 1
GEN-2018-039 | 01 - North | 652528 | WOONSKT7 | 115 | 5483.1 | 5483.2 | 0.1
GEN-2018-039 | 01 - North | 652568 | GROTONSOUTH7 | 115 | 19126.1 | 19152.9 | 26.8
GEN-2018-039 | 01 - North | 652590 | SNAKECR7 | 115 | 5851.5 | 5851.6 | 0.1
GEN-2018-039 | 01 - North | 652638 | ENDERLIN 7 | 115 | 3440.3 | 3442.6 | 2.3
GEN-2018-039 | 01 - North | 655053 | MOS-MILR-ER8 | 69 | 2602.7 | 2602.7 | 0
GEN-2018-039 | 01 - North | 655054 | MOS-RDFL-ER8 | 69 | 2143.7 | 2143.7 | 0
GEN-2018-039 | 01 - North | 655055 | SW-YALE-ER8 | 69 | 1258 | 1258 | 0
GEN-2018-039 | 01 - North | 655057 | MOS-LADL-ER8 | 69 | 1634.4 | 1634.4 | 0
GEN-2018-039 | 01 - North | 655058 | MOS-HRON-ER8 | 69 | 3053.1 | 3053.1 | 0
GEN-2018-039 | 01 - North | 655059 | MOS-ASHT-ER8 | 69 | 1708.6 | 1708.6 | 0
GEN-2018-039 | 01 - North | 655060 | MOS-POLO-ER8 | 69 | 1036.9 | 1036.9 | 0
GEN-2018-039 | 01 - North | 655061 | MOS-TULR-ER8 | 69 | 1544.2 | 1544.2 | 0
GEN-2018-039 | 01 - North | 655062 | MOS-YALE-ER8 | 69 | 1502.7 | 1502.7 | 0
GEN-2018-039 | 01 - North | 655063 | SW-HURN1-ER8 | 69 | 4057.7 | 4057.7 | 0
GEN-2018-039 | 01 - North | 655064 | SW-HURN4-ER8 | 69 | 4019.1 | 4019.2 | 0.1
GEN-2018-039 | 01 - North | 655065 | MOS-YLTI-ER8 | 69 | 1755.8 | 1755.8 | 0
GEN-2018-039 | 01 - North | 655066 | SW-HURN2-ER8 | 69 | 4093.9 | 4093.9 | 0
GEN-2018-039 | 01 - North | 655067 | SW-HURN3-ER8 | 69 | 4098.6 | 4098.7 | 0.1
GEN-2018-039 | 01 - North | 655068 | MOS-CRKR-ER8 | 69 | 1530.2 | 1530.2 | 0
GEN-2018-039 | 01 - North | 655069 | MOS-WOLS-ER8 | 69 | 2571.3 | 2571.3 | 0
GEN-2018-039 | 01 - North | 655070 | MOS-VRCV-ER8 | 69 | 1339.3 | 1339.3 | 0
GEN-2018-039 | 01 - North | 655071 | MOS-DAK-ER8 | 69 | 1131.4 | 1131.4 | 0
GEN-2018-039 | 01 - North | 655072 | SW-SANDC-ER8 | 69 | 2404.4 | 2404.4 | 0
GEN-2018-039 | 01 - North | 655082 | MOS-CLRM-ER8 | 69 | 2968.1 | 2970.2 | 2.1
GEN-2018-039 | 01 - North | 655083 | MOS-BRTO-ER8 | 69 | 2133.7 | 2133.9 | 0.2
GEN-2018-039 | 01 - North | 655084 | SW519-ER8 | 69 | 1741.7 | 1741.9 | 0.2
GEN-2018-039 | 01 - North | 655085 | MOS-SWAB-ER8 | 69 | 2449.7 | 2451.2 | 1.5
GEN-2018-039 | 01 - North | 655086 | MOS-IPAB-ER8 | 69 | 3843.6 | 3846.5 | 2.9
GEN-2018-039 | 01 - North | 655087 | MOS-ABDN-ER8 | 69 | 4573.1 | 4577.2 | 4.1
GEN-2018-039 | 01 - North | 655089 | SW-IPABD-ER8 | 69 | 2780.1 | 2782 | 1.9
GEN-2018-039 | 01 - North | 655090 | MOS-STRF-ER8 | 69 | 1827.8 | 1828 | 0.2
GEN-2018-039 | 01 - North | 655109 | MOS-PEEV-ER8 | 69 | 1187 | 1187.1 | 0.1
GEN-2018-039 | 01 - North | 655110 | MOS-BGST-ER8 | 69 | 1339.8 | 1339.8 | 0
GEN-2018-039 | 01 - North | 655113 | MOS-WLMT-ER8 | 69 | 2026.7 | 2026.8 | 0.1
GEN-2018-039 | 01 - North | 655114 | SW-BIGST-ER8 | 69 | 1844.3 | 1844.3 | 0
GEN-2018-039 | 01 - North | 655115 | MOS-CLRK-ER8 | 69 | 1202 | 1202 | 0
GEN-2018-039 | 01 - North | 655118 | MOS-MARV-ER8 | 69 | 1910.4 | 1910.4 | 0
GEN-2018-039 | 01 - North | 655125 | MOS-ORTY-ER8 | 69 | 1930.7 | 1930.8 | 0.1
GEN-2018-039 | 01 - North | 655164 | MOS-LMIS-ER8 | 69 | 1255.5 | 1255.5 | 0
GEN-2018-039 | 01 - North | 655227 | REDFIELD-ER8 | 69 | 2090.6 | 2090.6 | 0
GEN-2018-039 | 01 - North | 655228 | YALE-ER8 | 69 | 1238.4 | 1238.4 | 0
GEN-2018-039 | 01 - North | 655230 | LA DELLE-ER8 | 69 | 985.6 | 985.6 | 0
GEN-2018-039 | 01 - North | 655231 | HURON-ER8 | 69 | 3049.3 | 3049.3 | 0
GEN-2018-039 | 01 - North | 655232 | ASHTON-ER8 | 69 | 1679.2 | 1679.2 | 0
GEN-2018-039 | 01 - North | 655233 | POLO-ER8 | 69 | 655.5 | 655.5 | 0
GEN-2018-039 | 01 - North | 655234 | MILLER-ER8 | 69 | 1045.2 | 1045.2 | 0
GEN-2018-039 | 01 - North | 655235 | TULARE-ER8 | 69 | 1150.3 | 1150.4 | 0.1
GEN-2018-039 | 01 - North | 655236 | MORNINGS-ER8 | 69 | 2018.4 | 2018.4 | 0
GEN-2018-039 | 01 - North | 655237 | BONILLA-ER8 | 69 | 1728.6 | 1728.6 | 0
GEN-2018-039 | 01 - North | 655238 | FRANKFRT-ER8 | 69 | 2184.5 | 2184.5 | 0
GEN-2018-039 | 01 - North | 655239 | WOLSEY-ER8 | 69 | 1652.8 | 1652.8 | 0
GEN-2018-039 | 01 - North | 655241 | VIRGIL-ER8 | 69 | 2084.4 | 2084.4 | 0
GEN-2018-039 | 01 - North | 655242 | CAVOUR-ER8 | 69 | 1284 | 1284 | 0
GEN-2018-039 | 01 - North | 655243 | CROCKER-ER8 | 69 | 1424.8 | 1424.8 | 0
GEN-2018-039 | 01 - North | 655244 | DAKOTA-ER8 | 69 | 1047.5 | 1047.5 | 0
GEN-2018-039 | 01 - North | 655245 | SANDCRK-ER8 | 69 | 2115 | 2115 | 0
GEN-2018-039 | 01 - North | 655246 | LETCHER-ER8 | 69 | 1426.1 | 1426.1 | 0
GEN-2018-039 | 01 - North | 655256 | FERNEY-ER8 | 69 | 2919.3 | 2919.7 | 0.4
GEN-2018-039 | 01 - North | 655257 | ANDOVER-ER8 | 69 | 1654.3 | 1654.4 | 0.1
GEN-2018-039 | 01 - North | 655258 | LANGFORD-ER8 | 69 | 1127.7 | 1127.7 | 0
GEN-2018-039 | 01 - North | 655260 | WEBSTER-ER8 | 69 | 1729.1 | 1729.2 | 0.1
GEN-2018-039 | 01 - North | 655261 | MANFIELD-ER8 | 69 | 1299.7 | 1299.8 | 0.1
GEN-2018-039 | 01 - North | 655262 | ABERDEEN-ER8 | 69 | 4663.1 | 4667.4 | 4.3
GEN-2018-039 | 01 - North | 655263 | IPWEBSTR-ER8 | 69 | 1521.7 | 1521.7 | 0
GEN-2018-039 | 01 - North | 655264 | IPABRDEN-ER8 | 69 | 2468.7 | 2470.2 | 1.5
GEN-2018-039 | 01 - North | 655266 | CLAREMNT-ER8 | 69 | 1458.6 | 1459.1 | 0.5
GEN-2018-039 | 01 - North | 655267 | GROTON-ER8 | 69 | 2779.4 | 2779.7 | 0.3
GEN-2018-039 | 01 - North | 655268 | SWABRDN-ER8 | 69 | 1634.1 | 1634.7 | 0.6
GEN-2018-039 | 01 - North | 655269 | BATH-ER8 | 69 | 2880.6 | 2882.6 | 2
GEN-2018-039 | 01 - North | 655270 | CRESBARD-ER8 | 69 | 747.8 | 747.9 | 0.1
GEN-2018-039 | 01 - North | 655286 | GRENVILE-ER8 | 69 | 825.7 | 825.8 | 0.1
GEN-2018-039 | 01 - North | 655287 | BIGSTONE-ER8 | 69 | 1339.3 | 1339.4 | 0.1
GEN-2018-039 | 01 - North | 655292 | MARVIN-ER8 | 69 | 1605 | 1605.1 | 0.1
GEN-2018-039 | 01 - North | 655302 | WILMOT-ER8 | 69 | 1344.6 | 1344.7 | 0.1
GEN-2018-039 | 01 - North | 655306 | ORTLEY-ER8 | 69 | 1849.7 | 1849.8 | 0.1
GEN-2018-039 | 01 - North | 655336 | BURKMERE-ER8 | 69 | 543 | 543 | 0
GEN-2018-039 | 01 - North | 655344 | LOOMIS-ER8 | 69 | 1171.6 | 1171.6 | 0
GEN-2018-039 | 01 - North | 655350 | WOODLAND-ER8 | 69 | 1273.9 | 1273.9 | 0
GEN-2018-039 | 01 - North | 655351 | HECLA-ER8 | 69 | 1126.7 | 1127 | 0.3
GEN-2018-039 | 01 - North | 655355 | WOONSKT-ER8 | 69 | 3734.4 | 3734.5 | 0.1
GEN-2018-039 | 01 - North | 655369 | NWPS6661-ER8 | 69 | 1513.4 | 1513.5 | 0.1
GEN-2018-039 | 01 - North | 655378 | NWPS3680-ER8 | 69 | 1063.2 | 1063.2 | 0
GEN-2018-039 | 01 - North | 655392 | MOS-GRNV-ER8 | 69 | 1175 | 1175 | 0
GEN-2018-039 | 01 - North | 655395 | NWPS509-ER8 | 69 | 4319 | 4319.9 | 0.9
GEN-2018-039 | 01 - North | 655399 | NWECLKTI-ER8 | 69 | 1158.8 | 1158.8 | 0
GEN-2018-039 | 01 - North | 655411 | CRANDALL-ER7 | 115 | 6891.4 | 6893.5 | 2.1
GEN-2018-039 | 01 - North | 655419 | SW561-ER7 | 115 | 7206.3 | 7208.6 | 2.3
GEN-2018-039 | 01 - North | 655421 | MOS-CRSB-ER8 | 69 | 748.4 | 748.4 | 0
GEN-2018-039 | 01 - North | 655422 | MOS-MNFD-ER8 | 69 | 1300.3 | 1300.4 | 0.1
GEN-2018-039 | 01 - North | 655432 | MOS-BRSU-ER8 | 69 | 905.8 | 905.8 | 0
GEN-2018-039 | 01 - North | 655433 | SW-LANGF-ER8 | 69 | 1145.4 | 1145.4 | 0
GEN-2018-039 | 01 - North | 655457 | BRISTOL-ER7 | 115 | 5541.9 | 5543.6 | 1.7
GEN-2018-039 | 01 - North | 655458 | BRISTOL-ER8 | 69 | 2872.8 | 2873 | 0.2
GEN-2018-039 | 01 - North | 655481 | REDFELD-ER7 | 115 | 4314.8 | 4315.2 | 0.4
GEN-2018-039 | 01 - North | 655482 | REDFELD-ER8 | 69 | 2943.6 | 2943.7 | 0.1
GEN-2018-039 | 01 - North | 655491 | ORDWAY-ER8 | 69 | 5998.4 | 6007 | 8.6
GEN-2018-039 | 01 - North | 655509 | SW-MILRC-ER8 | 69 | 1075.6 | 1075.6 | 0
GEN-2018-039 | 01 - North | 655516 | MCSINCRK-ER8 | 69 | 4072.5 | 4075.2 | 2.7
GEN-2018-039 | 01 - North | 655610 | BARLOW -CP7 | 115 | 2731.6 | 2733.2 | 1.6
GEN-2018-039 | 01 - North | 655625 | DICKEYTP-CP8 | 69 | 2223.2 | 2254.1 | 30.9
GEN-2018-039 | 01 - North | 655626 | OMEGATAP-CP8 | 69 | 2075.3 | 2097.7 | 22.4
GEN-2018-039 | 01 - North | 655627 | LAMOURTP-CP8 | 69 | 2064.6 | 2086.3 | 21.7
GEN-2018-039 | 01 - North | 655628 | WESTOAKS-CP8 | 69 | 2245.1 | 2254 | 8.9
GEN-2018-039 | 01 - North | 655643 | VOLTAIR -CP7 | 115 | 8618.4 | 8618.5 | 0.1
GEN-2018-039 | 01 - North | 655647 | WARD -CP7 | 115 | 8461.4 | 8462 | 0.6
GEN-2018-039 | 01 - North | 655652 | E.BISMRK-CP7 | 115 | 16131.6 | 16134.1 | 2.5
GEN-2018-039 | 01 - North | 655690 | MAX_____-CP7 | 115 | 6187.8 | 6187.9 | 0.1
GEN-2018-039 | 01 - North | 655693 | WARD_SPR-CP7 | 115 | 3148.8 | 3148.9 | 0.1
GEN-2018-039 | 01 - North | 655731 | LARK -MG8 | 69 | 975.8 | 975.8 | 0
GEN-2018-039 | 01 - North | 655732 | FLASHER -MG8 | 69 | 902.9 | 902.9 | 0
GEN-2018-039 | 01 - North | 655740 | CANNON -MG8 | 69 | 909.7 | 909.7 | 0
GEN-2018-039 | 01 - North | 655741 | CEDAR -MG8 | 69 | 689.5 | 689.5 | 0
GEN-2018-039 | 01 - North | 655742 | GRANT -MG8 | 69 | 617.7 | 617.7 | 0
GEN-2018-039 | 01 - North | 655744 | DEVALTP -MG8 | 69 | 1110.4 | 1110.4 | 0
GEN-2018-039 | 01 - North | 655746 | DEVAUL -MG8 | 69 | 1116.3 | 1116.3 | 0
GEN-2018-039 | 01 - North | 655747 | DEVAUL -MG7 | 115 | 1107.4 | 1107.4 | 0
GEN-2018-039 | 01 - North | 655748 | NEWSALEM-MG7 | 115 | 1514 | 1514 | 0
GEN-2018-039 | 01 - North | 655749 | MANSWTCH-MG7 | 115 | 1023.4 | 1023.4 | 0
GEN-2018-039 | 01 - North | 655750 | ROUGHRDR-MG7 | 115 | 990.8 | 990.8 | 0
GEN-2018-039 | 01 - North | 655751 | NRWSTMDN-MG7 | 115 | 991.2 | 991.2 | 0
GEN-2018-039 | 01 - North | 655752 | NWMDNTAP-MG7 | 115 | 1551.7 | 1551.8 | 0.1
GEN-2018-039 | 01 - North | 657275 | LAKEPK 8 | 69 | 5418.5 | 5418.7 | 0.2
GEN-2018-039 | 01 - North | 657700 | PILSBRY4 | 230 | 3634.4 | 3634.6 | 0.2
GEN-2018-039 | 01 - North | 657701 | BARNES 4 | 230 | 3295.3 | 3295.4 | 0.1
GEN-2018-039 | 01 - North | 657702 | LUVERNE4 | 230 | 3036.7 | 3036.8 | 0.1
GEN-2018-039 | 01 - North | 657707 | CALEDON7 | 115 | 4142 | 4142.4 | 0.4
GEN-2018-039 | 01 - North | 657734 | SIBLEY 4 | 230 | 3288.6 | 3288.8 | 0.2
GEN-2018-039 | 01 - North | 657754 | MAPLE R4 | 230 | 12894.3 | 12899.6 | 5.3
GEN-2018-039 | 01 - North | 657755 | PRAIRIE4 | 230 | 8941 | 8943.3 | 2.3
GEN-2018-039 | 01 - North | 657759 | PICKERT4 | 230 | 4541.3 | 4544.5 | 3.2
GEN-2018-039 | 01 - North | 657804 | MPC-VCY8 | 69 | 2650.4 | 2651.5 | 1.1
GEN-2018-039 | 01 - North | 657923 | PICKERT8 | 69 | 3290.1 | 3290.6 | 0.5
GEN-2018-039 | 01 - North | 658160 | MPSBROOK | 115 | 6729.8 | 6731 | 1.2
GEN-2018-039 | 01 - North | 658172 | MOORHED4 | 230 | 7300.5 | 7303.4 | 2.9
GEN-2018-039 | 01 - North | 658209 | MOORHDW4 | 230 | 7300.5 | 7303.4 | 2.9
GEN-2018-039 | 01 - North | 659105 | LELAND_O-BE3 | 345 | 19851.7 | 19853 | 1.3
GEN-2018-039 | 01 - North | 659106 | LELAND_O-BE4 | 230 | 25797.6 | 25799.7 | 2.1
GEN-2018-039 | 01 - North | 659108 | LOGAN___-BE4 | 230 | 6658.2 | 6658.3 | 0.1
GEN-2018-039 | 01 - North | 659109 | BASIN___-BE7 | 115 | 5428.6 | 5428.6 | 0
GEN-2018-039 | 01 - North | 659128 | HERBERTW-KM4 | 230 | 5154.4 | 5157.8 | 3.4
GEN-2018-039 | 01 - North | 659160 | GROTON__-BE3 | 345 | 6610.9 | 6614.9 | 4
GEN-2018-039 | 01 - North | 659165 | G09_001IST | 345 | 6665.6 | 6668 | 2.4
GEN-2018-039 | 01 - North | 659172 | LUDDEN -CP7 | 115 | 2112 | 2112.5 | 0.5
GEN-2018-039 | 01 - North | 659187 | GROTON__-BE7 | 115 | 19085.2 | 19111.7 | 26.5
GEN-2018-039 | 01 - North | 659198 | GROTON__-BE8 | 115 | 10004.6 | 10007.6 | 3
GEN-2018-039 | 01 - North | 659199 | BASIN___-BE4 | 230 | 23356.7 | 23358.3 | 1.6
GEN-2018-039 | 01 - North | 659275 | GROTON_G-BE7 | 115 | 18614.3 | 18639 | 24.7
GEN-2018-039 | 01 - North | 659280 | POMONA__-PP7 | 115 | 3437.3 | 3635.4 | 198.1
GEN-2018-039 | 01 - North | 659284 | ECKLUND_-PP4 | 230 | 8108.8 | 8109.8 | 1
GEN-2018-039 | 01 - North | 659288 | DAY_CNTY-PP7 | 115 | 5766.2 | 5767.1 | 0.9
GEN-2018-039 | 01 - North | 659310 | ORDWAY__-BE7 | 115 | 7899.4 | 7930.9 | 31.5
GEN-2018-039 | 01 - North | 659365 | BALDWIN_-PP4 | 230 | 8108.8 | 8109.8 | 1
GEN-2018-039 | 01 - North | 659408 | CAMPBL._-PP4 | 230 | 3761.7 | 3761.8 | 0.1
GEN-2018-039 | 01 - North | 659423 | GR.LS-LO-BE3 | 345 | 6610.9 | 6614.9 | 4
GEN-2018-039 | 01 - North | 659472 | CROCKER_-UA3 | 345 | 5725.8 | 5727.5 | 1.7
GEN-2018-039 | 01 - North | 659543 | PICKCITY-RR7 | 115 | 10201.4 | 10201.7 | 0.3
GEN-2018-039 | 01 - North | 660000 | ABERDN JCT 7 | 115 | 6841.3 | 6842.8 | 1.5
GEN-2018-039 | 01 - North | 660001 | ABERDN SIEB7 | 115 | 8024.1 | 8026.1 | 2
GEN-2018-039 | 01 - North | 660002 | REDFIELD 7 | 115 | 4199.8 | 4200 | 0.2
GEN-2018-039 | 01 - North | 660003 | HURON WPARK7 | 115 | 10007.7 | 10007.9 | 0.2
GEN-2018-039 | 01 - North | 660009 | HURON BTAP 7 | 115 | 15356.7 | 15357.3 | 0.6
GEN-2018-039 | 01 - North | 660012 | HURON WPARK8 | 69 | 7048 | 7048.1 | 0.1
GEN-2018-039 | 01 - North | 660015 | REDFIELD 8 | 69 | 1007.9 | 1007.9 | 0
GEN-2018-039 | 01 - North | 660021 | ABERDNINDPK7 | 115 | 6478.4 | 6479.7 | 1.3
GEN-2018-039 | 01 - North | 660309 | HUR 9THST J | 69 | 6046.3 | 6046.3 | 0
GEN-2018-039 | 01 - North | 660310 | HUR SO.WEST | 69 | 5694.7 | 5694.7 | 0
GEN-2018-039 | 01 - North | 660311 | HUR SO.EAST | 69 | 5270.3 | 5270.3 | 0
GEN-2018-039 | 01 - North | 660312 | HUR GT PLANT | 69 | 4626.5 | 4626.5 | 0
GEN-2018-039 | 01 - North | 660313 | HUR 4TH ST | 69 | 5252.5 | 5252.5 | 0
GEN-2018-039 | 01 - North | 660314 | HUR CITY | 69 | 4493.7 | 4493.8 | 0.1
GEN-2018-039 | 01 - North | 660320 | WOLSEY | 69 | 3175.8 | 3175.8 | 0
GEN-2018-039 | 01 - North | 660321 | VAYLAND | 69 | 1937.2 | 1937.2 | 0
GEN-2018-039 | 01 - North | 660322 | ST.LWR OILSD | 69 | 1793.7 | 1793.7 | 0
GEN-2018-039 | 01 - North | 660324 | ST.LAWRENCE | 69 | 1740.6 | 1740.6 | 0
GEN-2018-039 | 01 - North | 660325 | MILLER | 69 | 1703.9 | 1703.9 | 0
GEN-2018-039 | 01 - North | 660327 | HIGHMORE E | 69 | 1084.5 | 1084.5 | 0
GEN-2018-039 | 01 - North | 660328 | HIGHMORE PLT | 69 | 1084.5 | 1084.5 | 0
GEN-2018-039 | 01 - North | 660329 | TITAN | 69 | 1593.2 | 1593.2 | 0
GEN-2018-039 | 01 - North | 660350 | FRANKFORT | 69 | 891.5 | 891.5 | 0
GEN-2018-039 | 01 - North | 660351 | DOLAND | 69 | 806 | 806 | 0
GEN-2018-039 | 01 - North | 660352 | RAYMOND | 69 | 743.1 | 743.1 | 0
GEN-2018-039 | 01 - North | 660353 | OAK TREE W T | 69 | 690.3 | 690.3 | 0
GEN-2018-039 | 01 - North | 660365 | MILLER 69 WY | 69 | 619.8 | 619.8 | 0
GEN-2018-039 | 01 - North | 660367 | HIGHMORE ERC | 69 | 599.7 | 599.7 | 0
GEN-2018-039 | 01 - North | 660430 | GROTON | 69 | 1610.9 | 1611 | 0.1
GEN-2018-039 | 01 - North | 660431 | GROTON CITY | 69 | 1597.6 | 1597.7 | 0.1
GEN-2018-039 | 01 - North | 660432 | ANDOVER | 69 | 1219.3 | 1219.4 | 0.1
GEN-2018-039 | 01 - North | 660433 | BRISTOL JCT | 69 | 843.5 | 843.5 | 0
GEN-2018-039 | 01 - North | 660440 | WEBSTER NW | 69 | 714.9 | 714.9 | 0
GEN-2018-039 | 01 - North | 660441 | WEBSTER CITY | 69 | 690.1 | 690.1 | 0
GEN-2018-039 | 01 - North | 661029 | ESTBMRK7 | 115 | 16590.7 | 16593.3 | 2.6
GEN-2018-039 | 01 - North | 661053 | MANDAN 4 | 230 | 16780.5 | 16784.4 | 3.9
GEN-2018-039 | 01 - North | 661060 | LINTON 7 | 115 | 1401.8 | 1401.8 | 0
GEN-2018-039 | 01 - North | 661098 | ELLENDL345 4 | 230 | 7804.9 | 7806.4 | 1.5
GEN-2018-039 | 01 - North | 760998 | GEN-2017-214 | 230 | 3372.7 | 3372.7 | 0
GEN-2018-039 | 01 - North | 762350 | ASGI-2017-01 | 69 | 1652.8 | 1652.8 | 0
GEN-2018-039 | 01 - North | 762735 | GEN-2018-039 | 115 | Project Bus - Disconnected | 4029.6 | Project Bus - Disconnected
GEN-2018-012 | 02 - Nebraska | 45906 | J1590 SUB | 345 | 14997.4 | 14999.9 | 2.5
GEN-2018-012 | 02 - Nebraska | 87486 | J748GENTIE | 345 | 13961.8 | 13963.8 | 2
GEN-2018-012 | 02 - Nebraska | 87487 | J748POI | 345 | 15847.5 | 15850.2 | 2.7
GEN-2018-012 | 02 - Nebraska | 587150 | GEN-2016-021 | 345 | 9368.2 | 9408.6 | 40.4
GEN-2018-012 | 02 - Nebraska | 601006 | SPLT RK3 | 345 | 14501.7 | 14502.4 | 0.7
GEN-2018-012 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28378.9 | 28396.9 | 18
GEN-2018-012 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28328.6 | 28335.9 | 7.3
GEN-2018-012 | 02 - Nebraska | 635202 | NEAL S 5 | 161 | 23371.5 | 23376.3 | 4.8
GEN-2018-012 | 02 - Nebraska | 635203 | NEAL N 5 | 161 | 26779.5 | 26786 | 6.5
GEN-2018-012 | 02 - Nebraska | 635204 | NEAL N 8 | 69 | 10248.4 | 10248.8 | 0.4
GEN-2018-012 | 02 - Nebraska | 635206 | IDA CO 3 | 345 | 9489.6 | 9490.4 | 0.8
GEN-2018-012 | 02 - Nebraska | 635219 | GARD AVE 3 | 345 | 9071.5 | 9072.1 | 0.6
GEN-2018-012 | 02 - Nebraska | 635220 | INTCHG 5 | 161 | 15192.3 | 15194.4 | 2.1
GEN-2018-012 | 02 - Nebraska | 635221 | KELLOGG5 | 161 | 17876.6 | 17879.4 | 2.8
GEN-2018-012 | 02 - Nebraska | 635229 | AIRPORT 5 | 161 | 17761.9 | 17764.7 | 2.8
GEN-2018-012 | 02 - Nebraska | 635230 | LIBERTY5 | 161 | 26067.4 | 26073.6 | 6.2
GEN-2018-012 | 02 - Nebraska | 635235 | SALIX 5 | 161 | 15283.2 | 15285.2 | 2
GEN-2018-012 | 02 - Nebraska | 635252 | J412 POI 3 | 345 | 9907 | 9908 | 1
GEN-2018-012 | 02 - Nebraska | 635300 | MONONA 5 | 161 | 5719.6 | 5719.8 | 0.2
GEN-2018-012 | 02 - Nebraska | 635398 | REMSEN 3 | 345 | 15233.6 | 15236.2 | 2.6
GEN-2018-012 | 02 - Nebraska | 635399 | CHEROKEE 3 | 345 | 16755.2 | 16758 | 2.8
GEN-2018-012 | 02 - Nebraska | 635400 | HIGHLND 3 | 345 | 15324.7 | 15326.1 | 1.4
GEN-2018-012 | 02 - Nebraska | 637009 | GLACIAL EDGE | 345 | 16465.7 | 16468.4 | 2.7
GEN-2018-012 | 02 - Nebraska | 637024 | RICHLAND W | 345 | 9001.2 | 9001.8 | 0.6
GEN-2018-012 | 02 - Nebraska | 640054 | ALBION 7 | 115 | 5889.8 | 5892.1 | 2.3
GEN-2018-012 | 02 - Nebraska | 640072 | BATTLCR7 | 115 | 7794.8 | 7808.6 | 13.8
GEN-2018-012 | 02 - Nebraska | 640073 | BATTLCR8 | 69 | 4105.6 | 4107.9 | 2.3
GEN-2018-012 | 02 - Nebraska | 640078 | BEEMER 7 | 115 | 4621.3 | 4622.4 | 1.1
GEN-2018-012 | 02 - Nebraska | 640080 | BELDEN 7 | 115 | 6364.1 | 6366.3 | 2.2
GEN-2018-012 | 02 - Nebraska | 640081 | BELDEN 8 | 69 | 3905.4 | 3905.9 | 0.5
GEN-2018-012 | 02 - Nebraska | 640084 | BLMFLD 7 | 115 | 6391.1 | 6393.4 | 2.3
GEN-2018-012 | 02 - Nebraska | 640085 | BLMFLD 8 | 69 | 4194.9 | 4195.5 | 0.6
GEN-2018-012 | 02 - Nebraska | 640113 | CLRWATR7 | 115 | 5557.7 | 5565.2 | 7.5
GEN-2018-012 | 02 - Nebraska | 640115 | CO.LINE7 | 115 | 7838.7 | 7858.1 | 19.4
GEN-2018-012 | 02 - Nebraska | 640119 | COL.COG7 | 115 | 20871.2 | 20884.7 | 13.5
GEN-2018-012 | 02 - Nebraska | 640122 | COL.DRY7 | 115 | 17575.4 | 17585 | 9.6
GEN-2018-012 | 02 - Nebraska | 640125 | COLMB.E3 | 345 | 10700 | 10717.3 | 17.3
GEN-2018-012 | 02 - Nebraska | 640126 | E.COL. 4 | 230 | 10724.5 | 10732 | 7.5
GEN-2018-012 | 02 - Nebraska | 640127 | COLMB.E7 | 115 | 23605.2 | 23623.3 | 18.1
GEN-2018-012 | 02 - Nebraska | 640131 | COLMB.W4 | 230 | 10464.3 | 10470.8 | 6.5
GEN-2018-012 | 02 - Nebraska | 640133 | COLMBUS4 | 230 | 12271.5 | 12281.4 | 9.9
GEN-2018-012 | 02 - Nebraska | 640134 | KELLY 7 | 115 | 18834.9 | 18846.6 | 11.7
GEN-2018-012 | 02 - Nebraska | 640136 | COLMBUS7 | 115 | 20395.8 | 20409.4 | 13.6
GEN-2018-012 | 02 - Nebraska | 640149 | CREITON7 | 115 | 5280.3 | 5285.6 | 5.3
GEN-2018-012 | 02 - Nebraska | 640150 | CREITON8 | 69 | 4742.2 | 4744.7 | 2.5
GEN-2018-012 | 02 - Nebraska | 640151 | CRESTON7 | 115 | 6314.4 | 6317.4 | 3
GEN-2018-012 | 02 - Nebraska | 640157 | DAVIDCY7 | 115 | 5954.1 | 5954.8 | 0.7
GEN-2018-012 | 02 - Nebraska | 640163 | EMERSON7 | 115 | 5721.4 | 5722.1 | 0.7
GEN-2018-012 | 02 - Nebraska | 640164 | EMERSONG | 69 | 3942.2 | 3942.4 | 0.2
GEN-2018-012 | 02 - Nebraska | 640176 | FULERTN7 | 115 | 2775.8 | 2776.3 | 0.5
GEN-2018-012 | 02 - Nebraska | 640212 | HARTGTN7 | 115 | 5602 | 5603.3 | 1.3
GEN-2018-012 | 02 - Nebraska | 640213 | HARTGTN8 | 69 | 3716.3 | 3716.7 | 0.4
GEN-2018-012 | 02 - Nebraska | 640226 | HOSKINS3 | 345 | 13876.7 | 13982 | 105.3
GEN-2018-012 | 02 - Nebraska | 640227 | HOSKINS4 | 230 | 10665.1 | 10694.3 | 29.2
GEN-2018-012 | 02 - Nebraska | 640228 | HOSKINS7 | 115 | 19209.9 | 19262.7 | 52.8
GEN-2018-012 | 02 - Nebraska | 640263 | MADISON7 | 115 | 6499.3 | 6503.4 | 4.1
GEN-2018-012 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23973.9 | 23977.3 | 3.4
GEN-2018-012 | 02 - Nebraska | 640293 | NELIGH 7 | 115 | 11364.6 | 11406.9 | 42.3
GEN-2018-012 | 02 - Nebraska | 640294 | NELIGH 8 | 69 | 6377.1 | 6384.9 | 7.8
GEN-2018-012 | 02 - Nebraska | 640296 | NORFK.N7 | 115 | 13982.6 | 14012.8 | 30.2
GEN-2018-012 | 02 - Nebraska | 640298 | NORFOLK7 | 115 | 13111.4 | 13135.8 | 24.4
GEN-2018-012 | 02 - Nebraska | 640305 | ONEILL 7 | 115 | 4093.5 | 4094.8 | 1.3
GEN-2018-012 | 02 - Nebraska | 640306 | ONEILL 8 | 69 | 4427.3 | 4428.2 | 0.9
GEN-2018-012 | 02 - Nebraska | 640318 | PETRSBG7 | 115 | 6882.2 | 6887.3 | 5.1
GEN-2018-012 | 02 - Nebraska | 640342 | SHELCRK3 | 345 | 10980.2 | 11004.2 | 24
GEN-2018-012 | 02 - Nebraska | 640343 | SHELCRK4 | 230 | 11546 | 11556.4 | 10.4
GEN-2018-012 | 02 - Nebraska | 640349 | SPENCER7 | 115 | 4767.5 | 4768 | 0.5
GEN-2018-012 | 02 - Nebraska | 640357 | STANTON7 | 115 | 5381.3 | 5384 | 2.7
GEN-2018-012 | 02 - Nebraska | 640363 | STNTN.N7 | 115 | 7349.9 | 7356.1 | 6.2
GEN-2018-012 | 02 - Nebraska | 640377 | TEKAMAH5 | 161 | 9313.7 | 9314.4 | 0.7
GEN-2018-012 | 02 - Nebraska | 640386 | TWIN CH4 | 230 | 9337.9 | 9341.9 | 4
GEN-2018-012 | 02 - Nebraska | 640387 | TWIN CH7 | 115 | 11315.5 | 11318.7 | 3.2
GEN-2018-012 | 02 - Nebraska | 640388 | TWIN CH8 | 69 | 8171.7 | 8172.7 | 1
GEN-2018-012 | 02 - Nebraska | 640424 | S.SIOUXCITY7 | 115 | 7736.4 | 7737.9 | 1.5
GEN-2018-012 | 02 - Nebraska | 640425 | S.SIOUXCITY8 | 69 | 4721.2 | 4721.6 | 0.4
GEN-2018-012 | 02 - Nebraska | 640444 | PETERSBRG.N7 | 115 | 6893.1 | 6898.3 | 5.2
GEN-2018-012 | 02 - Nebraska | 640465 | EAGLECREEK 7 | 115 | 3152 | 3152.5 | 0.5
GEN-2018-012 | 02 - Nebraska | 640466 | KXL_PS22 7 | 115 | 2951 | 2951.5 | 0.5
GEN-2018-012 | 02 - Nebraska | 640520 | ANTELOPE 3 | 345 | 7055.8 | 7197.9 | 142.1
GEN-2018-012 | 02 - Nebraska | 640521 | ANTELOPE 7 | 115 | 16608.6 | 16726 | 117.4
GEN-2018-012 | 02 - Nebraska | 640522 | ANTELOPE 8 | 69 | 5504.4 | 5512.1 | 7.7
GEN-2018-012 | 02 - Nebraska | 640540 | MEADOWGROVE4 | 230 | 5873.2 | 5874.1 | 0.9
GEN-2018-012 | 02 - Nebraska | 640560 | WAKEFIELD 4 | 230 | 8366.2 | 8371.9 | 5.7
GEN-2018-012 | 02 - Nebraska | 640561 | RTLSNAKE.W 4 | 230 | 7469.1 | 7473.2 | 4.1
GEN-2018-012 | 02 - Nebraska | 640588 | TURTLE.CRK 3 | 345 | 12246.1 | 12320.3 | 74.2
GEN-2018-012 | 02 - Nebraska | 640589 | SHOLES.W 3 | 345 | 9953.5 | 10000 | 46.5
GEN-2018-012 | 02 - Nebraska | 643254 | UPSTREAM.W 7 | 115 | 15884.8 | 15989.2 | 104.4
GEN-2018-012 | 02 - Nebraska | 643271 | PLUMBCR.W 3 | 345 | 11992.7 | 12063.7 | 71
GEN-2018-012 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30062.8 | 30064.3 | 1.5
GEN-2018-012 | 02 - Nebraska | 645451 | S3451 3 | 345 | 22760.8 | 22762.6 | 1.8
GEN-2018-012 | 02 - Nebraska | 645454 | S3454 3 | 345 | 29538.1 | 29540.1 | 2
GEN-2018-012 | 02 - Nebraska | 645459 | S3459 3 | 345 | 25752.3 | 25753.6 | 1.3
GEN-2018-012 | 02 - Nebraska | 646251 | S1251 5 | 161 | 32698 | 32699.8 | 1.8
GEN-2018-012 | 02 - Nebraska | 648506 | PR BRZ 4 | 230 | 4434.9 | 4435.2 | 0.3
GEN-2018-012 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17850.1 | 17854.7 | 4.6
GEN-2018-012 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21424 | 21427 | 3
GEN-2018-012 | 02 - Nebraska | 650214 | NW68HOLDRG7 | 115 | 25915.1 | 25917.1 | 2
GEN-2018-012 | 02 - Nebraska | 652511 | GAVINS 7 | 115 | 10005 | 10007.2 | 2.2
GEN-2018-012 | 02 - Nebraska | 652552 | SIOUXCY2 | 230 | 20839.1 | 20845.3 | 6.2
GEN-2018-012 | 02 - Nebraska | 652564 | SIOUXCY3 | 345 | 15921.4 | 15926.1 | 4.7
GEN-2018-012 | 02 - Nebraska | 652565 | SIOUXCY4 | 230 | 20839.1 | 20845.3 | 6.2
GEN-2018-012 | 02 - Nebraska | 652864 | SIOUXCY-LNX3 | 345 | 15730.5 | 15735.1 | 4.6
GEN-2018-012 | 02 - Nebraska | 655139 | MOS-USD-ER8 | 69 | 1913.5 | 1913.5 | 0
GEN-2018-012 | 02 - Nebraska | 655144 | SW869-ER8 | 69 | 1681.2 | 1681.2 | 0
GEN-2018-012 | 02 - Nebraska | 655149 | STR810-ER8 | 69 | 1968 | 1968.1 | 0.1
GEN-2018-012 | 02 - Nebraska | 655168 | SW8105-ER8 | 69 | 2469.6 | 2469.6 | 0
GEN-2018-012 | 02 - Nebraska | 655317 | USD-ER8 | 69 | 1889 | 1889 | 0
GEN-2018-012 | 02 - Nebraska | 655323 | GAYVILLE-ER8 | 69 | 1479.7 | 1479.8 | 0.1
GEN-2018-012 | 02 - Nebraska | 655325 | DKTADOME-ER8 | 69 | 1952.6 | 1952.6 | 0
GEN-2018-012 | 02 - Nebraska | 655356 | SPRTMND-ER8 | 69 | 2976.8 | 2976.8 | 0
GEN-2018-012 | 02 - Nebraska | 655357 | MECKLING-ER8 | 69 | 2300.1 | 2300.1 | 0
GEN-2018-012 | 02 - Nebraska | 655502 | SPRTMND-ER7 | 115 | 6390.5 | 6390.7 | 0.2
GEN-2018-012 | 02 - Nebraska | 658100 | VERMLN 7 | 115 | 4542.7 | 4542.8 | 0.1
GEN-2018-012 | 02 - Nebraska | 658101 | VERMLNE 7 | 115 | 4508.4 | 4508.5 | 0.1
GEN-2018-012 | 02 - Nebraska | 659121 | SPIRIT_M-BE7 | 115 | 6390.5 | 6390.7 | 0.2
GEN-2018-012 | 02 - Nebraska | 659900 | EAGLE___-NI4 | 230 | 7513.6 | 7514.1 | 0.5
GEN-2018-012 | 02 - Nebraska | 660006 | YANKTON JCT7 | 115 | 9151.4 | 9152.8 | 1.4
GEN-2018-012 | 02 - Nebraska | 760788 | GEN-2017-201 | 345 | 9017.4 | 9055.2 | 37.8
GEN-2018-012 | 02 - Nebraska | 762069 | G17-105TAP | 161 | 8732.5 | 8733.1 | 0.6
GEN-2018-012 | 02 - Nebraska | 762070 | GEN-2017-105 | 161 | 8732.5 | 8733.1 | 0.6
GEN-2018-012 | 02 - Nebraska | 762504 | GEN-2018-012 | 345 | Project Bus - Disconnected | 5932.5 | Project Bus - Disconnected
GEN-2018-012 | 02 - Nebraska | 762509 | G18-012-DUMY | 345 | Project Bus - Disconnected | 7197.9 | Project Bus - Disconnected
GEN-2018-012 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 21763.8 | 21765.4 | 1.6
GEN-2018-012 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 16528.4 | 16530 | 1.6
GEN-2018-012 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 13436.6 | 13437.6 | 1
GEN-2018-025 | 02 - Nebraska | 45906 | J1590 SUB | 345 | 14996.5 | 14999.9 | 3.4
GEN-2018-025 | 02 - Nebraska | 85831 | J583 | 345 | 6195.6 | 6196.3 | 0.7
GEN-2018-025 | 02 - Nebraska | 87486 | J748GENTIE | 345 | 13961.1 | 13963.8 | 2.7
GEN-2018-025 | 02 - Nebraska | 87487 | J748POI | 345 | 15846.6 | 15850.2 | 3.6
GEN-2018-025 | 02 - Nebraska | 300039 | 7FAIRPT | 345 | 12858.6 | 12859.2 | 0.6
GEN-2018-025 | 02 - Nebraska | 541197 | MULLNCR7 | 345 | 10936.5 | 10937.6 | 1.1
GEN-2018-025 | 02 - Nebraska | 541199 | ST JOE 7 | 345 | 20504.6 | 20505.4 | 0.8
GEN-2018-025 | 02 - Nebraska | 541411 | MC REAC1 | 345 | 10297 | 10297.9 | 0.9
GEN-2018-025 | 02 - Nebraska | 541412 | MC REAC2 | 345 | 10297 | 10297.9 | 0.9
GEN-2018-025 | 02 - Nebraska | 541413 | MC REAC3 | 345 | 10297 | 10297.9 | 0.9
GEN-2018-025 | 02 - Nebraska | 541510 | HOLT 7 | 345 | 14793.2 | 14795.8 | 2.6
GEN-2018-025 | 02 - Nebraska | 541511 | ROCKCK7 | 345 | 15900.4 | 15903.1 | 2.7
GEN-2018-025 | 02 - Nebraska | 541517 | HOLT_REACT7 | 345 | 14669.1 | 14671.7 | 2.6
GEN-2018-025 | 02 - Nebraska | 541543 | OUTLAW | 345 | 20275.5 | 20279.7 | 4.2
GEN-2018-025 | 02 - Nebraska | 585241 | GEN-2015-088 | 345 | 12238.9 | 12240.9 | 2
GEN-2018-025 | 02 - Nebraska | 587150 | GEN-2016-021 | 345 | 9407.7 | 9408.6 | 0.9
GEN-2018-025 | 02 - Nebraska | 601006 | SPLT RK3 | 345 | 14501.8 | 14502.4 | 0.6
GEN-2018-025 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32284.8 | 32362.1 | 77.3
GEN-2018-025 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39907.7 | 39966.4 | 58.7
GEN-2018-025 | 02 - Nebraska | 635002 | CBLUFFS8 | 69 | 25268.9 | 25279.1 | 10.2
GEN-2018-025 | 02 - Nebraska | 635003 | SUB701 5 | 161 | 21629.8 | 21652.1 | 22.3
GEN-2018-025 | 02 - Nebraska | 635011 | INDNCRK5 | 161 | 22093.5 | 22114.2 | 20.7
GEN-2018-025 | 02 - Nebraska | 635013 | PNYCRK 3 | 345 | 29378.8 | 29441.3 | 62.5
GEN-2018-025 | 02 - Nebraska | 635014 | OVRLND 3 | 345 | 27580.4 | 27634.8 | 54.4
GEN-2018-025 | 02 - Nebraska | 635015 | OVRLND 5 | 161 | 31624.8 | 31659.2 | 34.4
GEN-2018-025 | 02 - Nebraska | 635016 | STHLND 3 | 345 | 29343 | 29405.4 | 62.4
GEN-2018-025 | 02 - Nebraska | 635017 | ATCHSN 3 | 345 | 22551.6 | 22556.8 | 5.2
GEN-2018-025 | 02 - Nebraska | 635030 | RIVRBND5 | 161 | 36355.1 | 36403.2 | 48.1
GEN-2018-025 | 02 - Nebraska | 635100 | RLHILLS3 | 345 | 13611 | 13614.7 | 3.7
GEN-2018-025 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28372.6 | 28396.9 | 24.3
GEN-2018-025 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28324.9 | 28335.9 | 11
GEN-2018-025 | 02 - Nebraska | 635202 | NEAL S 5 | 161 | 23369.1 | 23376.3 | 7.2
GEN-2018-025 | 02 - Nebraska | 635203 | NEAL N 5 | 161 | 26776.2 | 26786 | 9.8
GEN-2018-025 | 02 - Nebraska | 635204 | NEAL N 8 | 69 | 10248.3 | 10248.8 | 0.5
GEN-2018-025 | 02 - Nebraska | 635206 | IDA CO 3 | 345 | 9489.1 | 9490.4 | 1.3
GEN-2018-025 | 02 - Nebraska | 635219 | GARD AVE 3 | 345 | 9071.1 | 9072.1 | 1
GEN-2018-025 | 02 - Nebraska | 635220 | INTCHG 5 | 161 | 15191.6 | 15194.4 | 2.8
GEN-2018-025 | 02 - Nebraska | 635221 | KELLOGG5 | 161 | 17875.8 | 17879.4 | 3.6
GEN-2018-025 | 02 - Nebraska | 635229 | AIRPORT 5 | 161 | 17760.8 | 17764.7 | 3.9
GEN-2018-025 | 02 - Nebraska | 635230 | LIBERTY5 | 161 | 26064.3 | 26073.6 | 9.3
GEN-2018-025 | 02 - Nebraska | 635235 | SALIX 5 | 161 | 15282.4 | 15285.2 | 2.8
GEN-2018-025 | 02 - Nebraska | 635252 | J412 POI 3 | 345 | 9906.5 | 9908 | 1.5
GEN-2018-025 | 02 - Nebraska | 635300 | MONONA 5 | 161 | 5719.5 | 5719.8 | 0.3
GEN-2018-025 | 02 - Nebraska | 635398 | REMSEN 3 | 345 | 15232.7 | 15236.2 | 3.5
GEN-2018-025 | 02 - Nebraska | 635399 | CHEROKEE 3 | 345 | 16754.2 | 16758 | 3.8
GEN-2018-025 | 02 - Nebraska | 635400 | HIGHLND 3 | 345 | 15324.2 | 15326.1 | 1.9
GEN-2018-025 | 02 - Nebraska | 635589 | ECLIPSE3 | 345 | 9402.3 | 9403.9 | 1.6
GEN-2018-025 | 02 - Nebraska | 635590 | FALLOW 3 | 345 | 11475.2 | 11477.6 | 2.4
GEN-2018-025 | 02 - Nebraska | 637009 | GLACIAL EDGE | 345 | 16464.8 | 16468.4 | 3.6
GEN-2018-025 | 02 - Nebraska | 637024 | RICHLAND W | 345 | 9000.8 | 9001.8 | 1
GEN-2018-025 | 02 - Nebraska | 640080 | BELDEN 7 | 115 | 6366.2 | 6366.3 | 0.1
GEN-2018-025 | 02 - Nebraska | 640081 | BELDEN 8 | 69 | 3905.9 | 3905.9 | 0
GEN-2018-025 | 02 - Nebraska | 640125 | COLMB.E3 | 345 | 10715.6 | 10717.3 | 1.7
GEN-2018-025 | 02 - Nebraska | 640127 | COLMB.E7 | 115 | 23621.3 | 23623.3 | 2
GEN-2018-025 | 02 - Nebraska | 640139 | COOPER 3 | 345 | 29864.5 | 29874.8 | 10.3
GEN-2018-025 | 02 - Nebraska | 640140 | COOPER 5 | 161 | 18498.1 | 18500.2 | 2.1
GEN-2018-025 | 02 - Nebraska | 640141 | COOPER_ESST8 | 69 | 4692.7 | 4692.7 | 0
GEN-2018-025 | 02 - Nebraska | 640226 | HOSKINS3 | 345 | 13979.8 | 13982 | 2.2
GEN-2018-025 | 02 - Nebraska | 640227 | HOSKINS4 | 230 | 10693.5 | 10694.3 | 0.8
GEN-2018-025 | 02 - Nebraska | 640228 | HOSKINS7 | 115 | 19261.2 | 19262.7 | 1.5
GEN-2018-025 | 02 - Nebraska | 640271 | MCCOOL 3 | 345 | 11469.8 | 11471 | 1.2
GEN-2018-025 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23965.3 | 23977.3 | 12
GEN-2018-025 | 02 - Nebraska | 640278 | SHELDON7 | 115 | 45501.4 | 45511.8 | 10.4
GEN-2018-025 | 02 - Nebraska | 640296 | NORFK.N7 | 115 | 14012 | 14012.8 | 0.8
GEN-2018-025 | 02 - Nebraska | 640298 | NORFOLK7 | 115 | 13135.1 | 13135.8 | 0.7
GEN-2018-025 | 02 - Nebraska | 640316 | PAWNEEL7 | 115 | 11790.4 | 11791.4 | 1
GEN-2018-025 | 02 - Nebraska | 640342 | SHELCRK3 | 345 | 11002.6 | 11004.2 | 1.6
GEN-2018-025 | 02 - Nebraska | 640343 | SHELCRK4 | 230 | 11555.4 | 11556.4 | 1
GEN-2018-025 | 02 - Nebraska | 640363 | STNTN.N7 | 115 | 7355.8 | 7356.1 | 0.3
GEN-2018-025 | 02 - Nebraska | 640377 | TEKAMAH5 | 161 | 9308.6 | 9314.4 | 5.8
GEN-2018-025 | 02 - Nebraska | 640378 | TEKAMAH7 | 115 | 8595.4 | 8598.1 | 2.7
GEN-2018-025 | 02 - Nebraska | 640446 | COOPER 8 | 69 | 4790.7 | 4790.8 | 0.1
GEN-2018-025 | 02 - Nebraska | 640520 | ANTELOPE 3 | 345 | 7197.4 | 7197.9 | 0.5
GEN-2018-025 | 02 - Nebraska | 640521 | ANTELOPE 7 | 115 | 16725.5 | 16726 | 0.5
GEN-2018-025 | 02 - Nebraska | 640522 | ANTELOPE 8 | 69 | 5512 | 5512.1 | 0.1
GEN-2018-025 | 02 - Nebraska | 640525 | TOBIAS 3 | 345 | 12238.9 | 12240.9 | 2
GEN-2018-025 | 02 - Nebraska | 640560 | WAKEFIELD 4 | 230 | 8371.4 | 8371.9 | 0.5
GEN-2018-025 | 02 - Nebraska | 640561 | RTLSNAKE.W 4 | 230 | 7472.9 | 7473.2 | 0.3
GEN-2018-025 | 02 - Nebraska | 640588 | TURTLE.CRK 3 | 345 | 12318.7 | 12320.3 | 1.6
GEN-2018-025 | 02 - Nebraska | 640589 | SHOLES.W 3 | 345 | 9999 | 10000 | 1
GEN-2018-025 | 02 - Nebraska | 640590 | MONOLITH 3 | 345 | 23449.7 | 23461.1 | 11.4
GEN-2018-025 | 02 - Nebraska | 643254 | UPSTREAM.W 7 | 115 | 15988.8 | 15989.2 | 0.4
GEN-2018-025 | 02 - Nebraska | 643271 | PLUMBCR.W 3 | 345 | 12062.2 | 12063.7 | 1.5
GEN-2018-025 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 29856.4 | 30064.3 | 207.9
GEN-2018-025 | 02 - Nebraska | 645451 | S3451 3 | 345 | 22402.2 | 22762.6 | 360.4
GEN-2018-025 | 02 - Nebraska | 645454 | S3454 3 | 345 | 29399.7 | 29540.1 | 140.4
GEN-2018-025 | 02 - Nebraska | 645455 | S3455 3 | 345 | 32560.5 | 32708.3 | 147.8
GEN-2018-025 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35093.5 | 35257.3 | 163.8
GEN-2018-025 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30912.9 | 30944.5 | 31.6
GEN-2018-025 | 02 - Nebraska | 645459 | S3459 3 | 345 | 25582.2 | 25753.6 | 171.4
GEN-2018-025 | 02 - Nebraska | 645740 | S3740 3 | 345 | 23407.7 | 23464.5 | 56.8
GEN-2018-025 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23276.9 | 23351.2 | 74.3
GEN-2018-025 | 02 - Nebraska | 646201 | S1201 5 | 161 | 32207.5 | 32265.4 | 57.9
GEN-2018-025 | 02 - Nebraska | 646206 | S1206 5 | 161 | 45247.9 | 45348.6 | 100.7
GEN-2018-025 | 02 - Nebraska | 646209 | S1209 5 | 161 | 47445.9 | 47646.6 | 200.7
GEN-2018-025 | 02 - Nebraska | 646211 | S1211 5 | 161 | 36796.2 | 36876.8 | 80.6
GEN-2018-025 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12540.6 | 12547.4 | 6.8
GEN-2018-025 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30917.7 | 30972.5 | 54.8
GEN-2018-025 | 02 - Nebraska | 646217 | S1217 5 | 161 | 33637.1 | 33706.1 | 69
GEN-2018-025 | 02 - Nebraska | 646220 | S1220 5 | 161 | 28815.8 | 28862.8 | 47
GEN-2018-025 | 02 - Nebraska | 646221 | S1221 5 | 161 | 35701.7 | 35793.6 | 91.9
GEN-2018-025 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25123 | 25223.7 | 100.7
GEN-2018-025 | 02 - Nebraska | 646227 | S1227 5 | 161 | 32901.4 | 32975.6 | 74.2
GEN-2018-025 | 02 - Nebraska | 646229 | S1229 5 | 161 | 29092 | 29139.9 | 47.9
GEN-2018-025 | 02 - Nebraska | 646231 | S1231 5 | 161 | 43444.3 | 43590.4 | 146.1
GEN-2018-025 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26865.9 | 26903.7 | 37.8
GEN-2018-025 | 02 - Nebraska | 646233 | S1233 5 | 161 | 29547.8 | 29608.2 | 60.4
GEN-2018-025 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27034.8 | 27088.9 | 54.1
GEN-2018-025 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34205.4 | 34298.3 | 92.9
GEN-2018-025 | 02 - Nebraska | 646236 | S1236 5 | 161 | 24633.5 | 24685.8 | 52.3
GEN-2018-025 | 02 - Nebraska | 646237 | S1237 5 | 161 | 22003.7 | 22050.7 | 47
GEN-2018-025 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22346.7 | 22369.8 | 23.1
GEN-2018-025 | 02 - Nebraska | 646249 | S1249 5 | 161 | 25267.6 | 25311.9 | 44.3
GEN-2018-025 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35742.9 | 35840.5 | 97.6
GEN-2018-025 | 02 - Nebraska | 646251 | S1251 5 | 161 | 32454.2 | 32699.8 | 245.6
GEN-2018-025 | 02 - Nebraska | 646252 | S1252 5 | 161 | 29919.8 | 30003 | 83.2
GEN-2018-025 | 02 - Nebraska | 646253 | S1253 5 | 161 | 27712.3 | 27774.5 | 62.2
GEN-2018-025 | 02 - Nebraska | 646254 | S1254 5 | 161 | 32733.2 | 32803.5 | 70.3
GEN-2018-025 | 02 - Nebraska | 646255 | S1255 5 | 161 | 49097.4 | 49252.8 | 155.4
GEN-2018-025 | 02 - Nebraska | 646256 | S1256 5 | 161 | 22883.1 | 22922 | 38.9
GEN-2018-025 | 02 - Nebraska | 646259 | S1259 5 | 161 | 38695 | 38783.6 | 88.6
GEN-2018-025 | 02 - Nebraska | 646260 | S1260 5 | 161 | 38820.8 | 38904.5 | 83.7
GEN-2018-025 | 02 - Nebraska | 646278 | S1278 5 | 161 | 27652.1 | 27695.5 | 43.4
GEN-2018-025 | 02 - Nebraska | 646281 | S1281 5 | 161 | 35327.9 | 35398.1 | 70.2
GEN-2018-025 | 02 - Nebraska | 646286 | S1286 5 | 161 | 26909.6 | 26950.6 | 41
GEN-2018-025 | 02 - Nebraska | 646287 | S1287 5 | 161 | 21904.5 | 21929.8 | 25.3
GEN-2018-025 | 02 - Nebraska | 646291 | S1291 5 | 161 | 7156.6 | 7162.2 | 5.6
GEN-2018-025 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19106.7 | 19161 | 54.3
GEN-2018-025 | 02 - Nebraska | 646298 | S1298 5 | 161 | 29623.9 | 29814.9 | 191
GEN-2018-025 | 02 - Nebraska | 646299 | S1299 5 | 161 | 28053.6 | 28099.7 | 46.1
GEN-2018-025 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28174.2 | 28348.8 | 174.6
GEN-2018-025 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27418.5 | 27585.8 | 167.3
GEN-2018-025 | 02 - Nebraska | 646345 | S1345 5 | 161 | 22697 | 22745.9 | 48.9
GEN-2018-025 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33092.9 | 33188.3 | 95.4
GEN-2018-025 | 02 - Nebraska | 646361 | S1361 5 | 161 | 40672.3 | 40767.7 | 95.4
GEN-2018-025 | 02 - Nebraska | 646362 | S1362 5 | 161 | 34309.1 | 34371.2 | 62.1
GEN-2018-025 | 02 - Nebraska | 646363 | S1363 5 | 161 | 32072.7 | 32122.1 | 49.4
GEN-2018-025 | 02 - Nebraska | 646366 | S1366 5 | 161 | 16454 | 16465.8 | 11.8
GEN-2018-025 | 02 - Nebraska | 646367 | S1367 5 | 161 | 21819.9 | 21862.1 | 42.2
GEN-2018-025 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32691.7 | 32712.7 | 21
GEN-2018-025 | 02 - Nebraska | 647015 | S6815T1&T2 8 | 69 | 12112.3 | 12115.1 | 2.8
GEN-2018-025 | 02 - Nebraska | 647016 | 6815TP38 | 69 | 17629.6 | 17635.2 | 5.6
GEN-2018-025 | 02 - Nebraska | 647017 | 6815TP98 | 69 | 12703.4 | 12706.5 | 3.1
GEN-2018-025 | 02 - Nebraska | 647104 | MUD LNG8 | 69 | 14694.6 | 14700.6 | 6
GEN-2018-025 | 02 - Nebraska | 647291 | S991 E 8 | 69 | 12819.1 | 12823.2 | 4.1
GEN-2018-025 | 02 - Nebraska | 647815 | S6815T3 8 | 69 | 11469.9 | 11472.3 | 2.4
GEN-2018-025 | 02 - Nebraska | 647874 | S6874 8 | 69 | 8642.4 | 8643.8 | 1.4
GEN-2018-025 | 02 - Nebraska | 647901 | S901 8 | 69 | 27119.1 | 27131 | 11.9
GEN-2018-025 | 02 - Nebraska | 647902 | S902 8 | 69 | 9066.4 | 9067.8 | 1.4
GEN-2018-025 | 02 - Nebraska | 647904 | S904 8 | 69 | 8760.5 | 8761.7 | 1.2
GEN-2018-025 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 33198.1 | 33217.4 | 19.3
GEN-2018-025 | 02 - Nebraska | 647909 | S909 8 | 69 | 27160.3 | 27181 | 20.7
GEN-2018-025 | 02 - Nebraska | 647911 | S911 8 | 69 | 21382.7 | 21394.2 | 11.5
GEN-2018-025 | 02 - Nebraska | 647916 | S916 8 | 69 | 23880.7 | 23894.9 | 14.2
GEN-2018-025 | 02 - Nebraska | 647917 | S917 8 | 69 | 26040.1 | 26057.7 | 17.6
GEN-2018-025 | 02 - Nebraska | 647918 | S918 8 | 69 | 23008.1 | 23022.5 | 14.4
GEN-2018-025 | 02 - Nebraska | 647919 | S919 8 | 69 | 21601.2 | 21614.4 | 13.2
GEN-2018-025 | 02 - Nebraska | 647921 | S921 8 | 69 | 26537.8 | 26556.5 | 18.7
GEN-2018-025 | 02 - Nebraska | 647924 | S924 8 | 69 | 24680.5 | 24691.2 | 10.7
GEN-2018-025 | 02 - Nebraska | 647928 | S928 8 | 69 | 17312.1 | 17318.7 | 6.6
GEN-2018-025 | 02 - Nebraska | 647930 | S930 8 | 69 | 21629.7 | 21642.7 | 13
GEN-2018-025 | 02 - Nebraska | 647937 | S937 8 | 69 | 9164.9 | 9166.4 | 1.5
GEN-2018-025 | 02 - Nebraska | 647938 | S938 8 | 69 | 21921.8 | 21930.9 | 9.1
GEN-2018-025 | 02 - Nebraska | 647939 | S939 8 | 69 | 20185.6 | 20197 | 11.4
GEN-2018-025 | 02 - Nebraska | 647940 | S940 8 | 69 | 20968.2 | 20979.5 | 11.3
GEN-2018-025 | 02 - Nebraska | 647942 | S942 8 | 69 | 16241.7 | 16247.9 | 6.2
GEN-2018-025 | 02 - Nebraska | 647950 | S950 8 | 69 | 20418.3 | 20430.5 | 12.2
GEN-2018-025 | 02 - Nebraska | 647995 | S995 8 | 69 | 9525.3 | 9527 | 1.7
GEN-2018-025 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17845.9 | 17854.7 | 8.8
GEN-2018-025 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21406 | 21427 | 21
GEN-2018-025 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21279 | 21295.1 | 16.1
GEN-2018-025 | 02 - Nebraska | 650210 | NW70FAIRFD7 | 115 | 21613.6 | 21617.4 | 3.8
GEN-2018-025 | 02 - Nebraska | 650214 | NW68HOLDRG7 | 115 | 25911.6 | 25917.1 | 5.5
GEN-2018-025 | 02 - Nebraska | 650216 | SW27&F 7 | 115 | 22379.5 | 22383.7 | 4.2
GEN-2018-025 | 02 - Nebraska | 650262 | 57&GARLAND7 | 115 | 25797.4 | 25803.4 | 6
GEN-2018-025 | 02 - Nebraska | 650267 | 84LEIGHTON7 | 115 | 30009.3 | 30017.7 | 8.4
GEN-2018-025 | 02 - Nebraska | 650270 | 70&CALVERT7 | 115 | 27879.5 | 27886.4 | 6.9
GEN-2018-025 | 02 - Nebraska | 650271 | 81&OCHENEY7 | 115 | 25497.1 | 25502.8 | 5.7
GEN-2018-025 | 02 - Nebraska | 650272 | 91&A 7 | 115 | 22181.2 | 22185.7 | 4.5
GEN-2018-025 | 02 - Nebraska | 650273 | 93&O 7 | 115 | 22957.7 | 22962.6 | 4.9
GEN-2018-025 | 02 - Nebraska | 650274 | 91&HWY2 7 | 115 | 22053.6 | 22057.7 | 4.1
GEN-2018-025 | 02 - Nebraska | 650279 | 120&ALVO 7 | 115 | 22005.6 | 22010.4 | 4.8
GEN-2018-025 | 02 - Nebraska | 650283 | WAVERLY 7 | 115 | 21515 | 21519.5 | 4.5
GEN-2018-025 | 02 - Nebraska | 650284 | 84FLETCHER7 | 115 | 25434.2 | 25440.1 | 5.9
GEN-2018-025 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32683.2 | 32694.8 | 11.6
GEN-2018-025 | 02 - Nebraska | 650290 | ROKEBY 7 | 115 | 26074.9 | 26079.9 | 5
GEN-2018-025 | 02 - Nebraska | 652552 | SIOUXCY2 | 230 | 20841.2 | 20845.3 | 4.1
GEN-2018-025 | 02 - Nebraska | 652564 | SIOUXCY3 | 345 | 15921.5 | 15926.1 | 4.6
GEN-2018-025 | 02 - Nebraska | 652565 | SIOUXCY4 | 230 | 20841.2 | 20845.3 | 4.1
GEN-2018-025 | 02 - Nebraska | 652864 | SIOUXCY-LNX3 | 345 | 15730.6 | 15735.1 | 4.5
GEN-2018-025 | 02 - Nebraska | 659900 | EAGLE___-NI4 | 230 | 7513.8 | 7514.1 | 0.3
GEN-2018-025 | 02 - Nebraska | 760746 | GEN-2017-115 | 345 | 12506.3 | 12508.1 | 1.8
GEN-2018-025 | 02 - Nebraska | 760788 | GEN-2017-201 | 345 | 9054.4 | 9055.2 | 0.8
GEN-2018-025 | 02 - Nebraska | 760872 | GEN-2017-198 | 69 | 25679.4 | 25690.1 | 10.7
GEN-2018-025 | 02 - Nebraska | 761208 | GEN-2017-210 | 345 | 10028.2 | 10029.1 | 0.9
GEN-2018-025 | 02 - Nebraska | 761292 | GEN-2017-181 | 345 | 6878.1 | 6878.7 | 0.6
GEN-2018-025 | 02 - Nebraska | 761313 | GEN-2017-182 | 345 | 5749 | 5749.4 | 0.4
GEN-2018-025 | 02 - Nebraska | 762069 | G17-105TAP | 161 | 8728.4 | 8733.1 | 4.7
GEN-2018-025 | 02 - Nebraska | 762070 | GEN-2017-105 | 161 | 8728.4 | 8733.1 | 4.7
GEN-2018-025 | 02 - Nebraska | 762504 | GEN-2018-012 | 345 | 5932.2 | 5932.5 | 0.3
GEN-2018-025 | 02 - Nebraska | 762509 | G18-012-DUMY | 345 | 7197.4 | 7197.9 | 0.5
GEN-2018-025 | 02 - Nebraska | 762581 | GEN-2018-022 | 345 | 8887.6 | 8888.3 | 0.7
GEN-2018-025 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | Project Bus - Disconnected | 21765.4 | Project Bus - Disconnected
GEN-2018-025 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 23406.1 | 23463 | 56.9
GEN-2018-025 | 02 - Nebraska | 762713 | GEN-2018-037 | 161 | 34478 | 34548.7 | 70.7
GEN-2018-025 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 16406.5 | 16530 | 123.5
GEN-2018-025 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 13358.5 | 13437.6 | 79.1
GEN-2018-033 | 02 - Nebraska | 45906 | J1590 SUB | 345 | 14999.2 | 14999.9 | 0.7
GEN-2018-033 | 02 - Nebraska | 85831 | J583 | 345 | 6195.7 | 6196.3 | 0.6
GEN-2018-033 | 02 - Nebraska | 87486 | J748GENTIE | 345 | 13963.3 | 13963.8 | 0.5
GEN-2018-033 | 02 - Nebraska | 87487 | J748POI | 345 | 15849.4 | 15850.2 | 0.8
GEN-2018-033 | 02 - Nebraska | 300039 | 7FAIRPT | 345 | 12858 | 12859.2 | 1.2
GEN-2018-033 | 02 - Nebraska | 300076 | 5FAIRPTB2 | 161 | 16945.9 | 16946.4 | 0.5
GEN-2018-033 | 02 - Nebraska | 301347 | 5WINSLOW | 161 | 8954.6 | 8954.8 | 0.2
GEN-2018-033 | 02 - Nebraska | 301559 | 5FAIRPTXF3 | 161 | 16962.9 | 16963.5 | 0.6
GEN-2018-033 | 02 - Nebraska | 541147 | ST JOE_CAP5 | 161 | 18876.3 | 18876.9 | 0.6
GEN-2018-033 | 02 - Nebraska | 541197 | MULLNCR7 | 345 | 10935 | 10937.6 | 2.6
GEN-2018-033 | 02 - Nebraska | 541199 | ST JOE 7 | 345 | 20503.6 | 20505.4 | 1.8
GEN-2018-033 | 02 - Nebraska | 541201 | SIBLEY 7 | 345 | 21618.3 | 21618.9 | 0.6
GEN-2018-033 | 02 - Nebraska | 541253 | ST JOE 5 | 161 | 21188.9 | 21189.7 | 0.8
GEN-2018-033 | 02 - Nebraska | 541257 | COOK 5 | 161 | 14719.2 | 14719.5 | 0.3
GEN-2018-033 | 02 - Nebraska | 541258 | WOODBIN5 | 161 | 17748.2 | 17748.7 | 0.5
GEN-2018-033 | 02 - Nebraska | 541394 | AVENUECTY 5 | 161 | 7204.6 | 7204.6 | 0
GEN-2018-033 | 02 - Nebraska | 541400 | EASTOWN7 | 345 | 18988.3 | 18989.5 | 1.2
GEN-2018-033 | 02 - Nebraska | 541401 | EASTOWN5 | 161 | 18071.3 | 18071.8 | 0.5
GEN-2018-033 | 02 - Nebraska | 541411 | MC REAC1 | 345 | 10295.7 | 10297.9 | 2.2
GEN-2018-033 | 02 - Nebraska | 541412 | MC REAC2 | 345 | 10295.7 | 10297.9 | 2.2
GEN-2018-033 | 02 - Nebraska | 541413 | MC REAC3 | 345 | 10295.7 | 10297.9 | 2.2
GEN-2018-033 | 02 - Nebraska | 541414 | SIB REA1 | 345 | 19255.6 | 19256 | 0.4
GEN-2018-033 | 02 - Nebraska | 541500 | KETCHEM7 | 345 | 9066.5 | 9067.3 | 0.8
GEN-2018-033 | 02 - Nebraska | 541501 | OSBORN7 | 345 | 7969.3 | 7970 | 0.7
GEN-2018-033 | 02 - Nebraska | 541510 | HOLT 7 | 345 | 14789.3 | 14795.8 | 6.5
GEN-2018-033 | 02 - Nebraska | 541511 | ROCKCK7 | 345 | 15896.8 | 15903.1 | 6.3
GEN-2018-033 | 02 - Nebraska | 541517 | HOLT_REACT7 | 345 | 14665.3 | 14671.7 | 6.4
GEN-2018-033 | 02 - Nebraska | 541543 | OUTLAW | 345 | 20270.5 | 20279.7 | 9.2
GEN-2018-033 | 02 - Nebraska | 542980 | NASHUA 7 | 345 | 23342.6 | 23343.3 | 0.7
GEN-2018-033 | 02 - Nebraska | 542982 | IATAN 7 | 345 | 31199.3 | 31200.1 | 0.8
GEN-2018-033 | 02 - Nebraska | 560746 | GEN-2013-002 | 115 | 44152.2 | 44168.5 | 16.3
GEN-2018-033 | 02 - Nebraska | 583700 | GEN-2013-019 | 115 | 30748.8 | 30756.6 | 7.8
GEN-2018-033 | 02 - Nebraska | 585241 | GEN-2015-088 | 345 | 12237.6 | 12240.9 | 3.3
GEN-2018-033 | 02 - Nebraska | 587150 | GEN-2016-021 | 345 | 9408.2 | 9408.6 | 0.4
GEN-2018-033 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32289.5 | 32362.1 | 72.6
GEN-2018-033 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39916.6 | 39966.4 | 49.8
GEN-2018-033 | 02 - Nebraska | 635002 | CBLUFFS8 | 69 | 25271 | 25279.1 | 8.1
GEN-2018-033 | 02 - Nebraska | 635011 | INDNCRK5 | 161 | 22098.7 | 22114.2 | 15.5
GEN-2018-033 | 02 - Nebraska | 635013 | PNYCRK 3 | 345 | 29382.5 | 29441.3 | 58.8
GEN-2018-033 | 02 - Nebraska | 635014 | OVRLND 3 | 345 | 27584 | 27634.8 | 50.8
GEN-2018-033 | 02 - Nebraska | 635015 | OVRLND 5 | 161 | 31629.5 | 31659.2 | 29.7
GEN-2018-033 | 02 - Nebraska | 635016 | STHLND 3 | 345 | 29346.8 | 29405.4 | 58.6
GEN-2018-033 | 02 - Nebraska | 635017 | ATCHSN 3 | 345 | 22545.5 | 22556.8 | 11.3
GEN-2018-033 | 02 - Nebraska | 635018 | WESTBORO 3 | 345 | 20925.1 | 20934.6 | 9.5
GEN-2018-033 | 02 - Nebraska | 635030 | RIVRBND5 | 161 | 36362.3 | 36403.2 | 40.9
GEN-2018-033 | 02 - Nebraska | 635100 | RLHILLS3 | 345 | 13610.8 | 13614.7 | 3.9
GEN-2018-033 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28392.1 | 28396.9 | 4.8
GEN-2018-033 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28333.5 | 28335.9 | 2.4
GEN-2018-033 | 02 - Nebraska | 635252 | J412 POI 3 | 345 | 9907.7 | 9908 | 0.3
GEN-2018-033 | 02 - Nebraska | 635398 | REMSEN 3 | 345 | 15235.5 | 15236.2 | 0.7
GEN-2018-033 | 02 - Nebraska | 635570 | ORIENT 3 | 345 | 18798.7 | 18802.9 | 4.2
GEN-2018-033 | 02 - Nebraska | 635589 | ECLIPSE3 | 345 | 9402.4 | 9403.9 | 1.5
GEN-2018-033 | 02 - Nebraska | 635590 | FALLOW 3 | 345 | 11475.3 | 11477.6 | 2.3
GEN-2018-033 | 02 - Nebraska | 637084 | J476 SHENHLL | 345 | 20789.2 | 20798.5 | 9.3
GEN-2018-033 | 02 - Nebraska | 640088 | BPS SUB7 | 115 | 16925.5 | 16926.2 | 0.7
GEN-2018-033 | 02 - Nebraska | 640111 | CLATONA7 | 115 | 11116.5 | 11117.1 | 0.6
GEN-2018-033 | 02 - Nebraska | 640125 | COLMB.E3 | 345 | 10715.7 | 10717.3 | 1.6
GEN-2018-033 | 02 - Nebraska | 640127 | COLMB.E7 | 115 | 23621.5 | 23623.3 | 1.8
GEN-2018-033 | 02 - Nebraska | 640139 | COOPER 3 | 345 | 29851.6 | 29874.8 | 23.2
GEN-2018-033 | 02 - Nebraska | 640140 | COOPER 5 | 161 | 18496.1 | 18500.2 | 4.1
GEN-2018-033 | 02 - Nebraska | 640141 | COOPER_ESST8 | 69 | 4692.6 | 4692.7 | 0.1
GEN-2018-033 | 02 - Nebraska | 640143 | COOPER_602 8 | 69 | 2010 | 2010 | 0
GEN-2018-033 | 02 - Nebraska | 640153 | CRETE__7 | 115 | 8464.8 | 8465.3 | 0.5
GEN-2018-033 | 02 - Nebraska | 640171 | FIRTH 7 | 115 | 7029.1 | 7029.6 | 0.5
GEN-2018-033 | 02 - Nebraska | 640226 | HOSKINS3 | 345 | 13981 | 13982 | 1
GEN-2018-033 | 02 - Nebraska | 640234 | HUMBOLT5 | 161 | 7990.6 | 7991.1 | 0.5
GEN-2018-033 | 02 - Nebraska | 640271 | MCCOOL 3 | 345 | 11469.2 | 11471 | 1.8
GEN-2018-033 | 02 - Nebraska | 640272 | MCCOOL 7 | 115 | 14770.7 | 14771.6 | 0.9
GEN-2018-033 | 02 - Nebraska | 640273 | MCCOOL 8 | 69 | 5735.3 | 5735.4 | 0.1
GEN-2018-033 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23957.6 | 23977.3 | 19.7
GEN-2018-033 | 02 - Nebraska | 640278 | SHELDON7 | 115 | 45495.3 | 45511.8 | 16.5
GEN-2018-033 | 02 - Nebraska | 640312 | PAULINE3 | 345 | 8377.5 | 8378.1 | 0.6
GEN-2018-033 | 02 - Nebraska | 640316 | PAWNEEL7 | 115 | 11790 | 11791.4 | 1.4
GEN-2018-033 | 02 - Nebraska | 640342 | SHELCRK3 | 345 | 11002.8 | 11004.2 | 1.4
GEN-2018-033 | 02 - Nebraska | 640446 | COOPER 8 | 69 | 4790.7 | 4790.8 | 0.1
GEN-2018-033 | 02 - Nebraska | 640525 | TOBIAS 3 | 345 | 12237.6 | 12240.9 | 3.3
GEN-2018-033 | 02 - Nebraska | 640588 | TURTLE.CRK 3 | 345 | 12319.5 | 12320.3 | 0.8
GEN-2018-033 | 02 - Nebraska | 640589 | SHOLES.W 3 | 345 | 9999.6 | 10000 | 0.4
GEN-2018-033 | 02 - Nebraska | 640590 | MONOLITH 3 | 345 | 23442.4 | 23461.1 | 18.7
GEN-2018-033 | 02 - Nebraska | 640591 | MONOLITH 7 | 115 | 44152.2 | 44168.5 | 16.3
GEN-2018-033 | 02 - Nebraska | 643271 | PLUMBCR.W 3 | 345 | 12063 | 12063.7 | 0.7
GEN-2018-033 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30023.3 | 30064.3 | 41
GEN-2018-033 | 02 - Nebraska | 645451 | S3451 3 | 345 | 22707.6 | 22762.6 | 55
GEN-2018-033 | 02 - Nebraska | 645454 | S3454 3 | 345 | 29346.9 | 29540.1 | 193.2
GEN-2018-033 | 02 - Nebraska | 645455 | S3455 3 | 345 | 32489.1 | 32708.3 | 219.2
GEN-2018-033 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35098.4 | 35257.3 | 158.9
GEN-2018-033 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30857.3 | 30944.5 | 87.2
GEN-2018-033 | 02 - Nebraska | 645459 | S3459 3 | 345 | 25677.5 | 25753.6 | 76.1
GEN-2018-033 | 02 - Nebraska | 645740 | S3740 3 | 345 | 23093.8 | 23464.5 | 370.7
GEN-2018-033 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23243.9 | 23351.2 | 107.3
GEN-2018-033 | 02 - Nebraska | 646201 | S1201 5 | 161 | 32227.4 | 32265.4 | 38
GEN-2018-033 | 02 - Nebraska | 646206 | S1206 5 | 161 | 45264.7 | 45348.6 | 83.9
GEN-2018-033 | 02 - Nebraska | 646209 | S1209 5 | 161 | 47536.8 | 47646.6 | 109.8
GEN-2018-033 | 02 - Nebraska | 646214 | S1214 5 | 161 | 12539.6 | 12547.4 | 7.8
GEN-2018-033 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30931.7 | 30972.5 | 40.8
GEN-2018-033 | 02 - Nebraska | 646217 | S1217 5 | 161 | 33657 | 33706.1 | 49.1
GEN-2018-033 | 02 - Nebraska | 646220 | S1220 5 | 161 | 28832.9 | 28862.8 | 29.9
GEN-2018-033 | 02 - Nebraska | 646221 | S1221 5 | 161 | 35719.5 | 35793.6 | 74.1
GEN-2018-033 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25197.4 | 25223.7 | 26.3
GEN-2018-033 | 02 - Nebraska | 646227 | S1227 5 | 161 | 32924.2 | 32975.6 | 51.4
GEN-2018-033 | 02 - Nebraska | 646229 | S1229 5 | 161 | 29108 | 29139.9 | 31.9
GEN-2018-033 | 02 - Nebraska | 646231 | S1231 5 | 161 | 43491.8 | 43590.4 | 98.6
GEN-2018-033 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26868.7 | 26903.7 | 35
GEN-2018-033 | 02 - Nebraska | 646233 | S1233 5 | 161 | 29549.9 | 29608.2 | 58.3
GEN-2018-033 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27043.9 | 27088.9 | 45
GEN-2018-033 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34232.3 | 34298.3 | 66
GEN-2018-033 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22350.4 | 22369.8 | 19.4
GEN-2018-033 | 02 - Nebraska | 646249 | S1249 5 | 161 | 25267.5 | 25311.9 | 44.4
GEN-2018-033 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35791 | 35840.5 | 49.5
GEN-2018-033 | 02 - Nebraska | 646251 | S1251 5 | 161 | 32651.3 | 32699.8 | 48.5
GEN-2018-033 | 02 - Nebraska | 646253 | S1253 5 | 161 | 27730.1 | 27774.5 | 44.4
GEN-2018-033 | 02 - Nebraska | 646254 | S1254 5 | 161 | 32724.6 | 32803.5 | 78.9
GEN-2018-033 | 02 - Nebraska | 646255 | S1255 5 | 161 | 49078.9 | 49252.8 | 173.9
GEN-2018-033 | 02 - Nebraska | 646256 | S1256 5 | 161 | 22888.2 | 22922 | 33.8
GEN-2018-033 | 02 - Nebraska | 646259 | S1259 5 | 161 | 38685.4 | 38783.6 | 98.2
GEN-2018-033 | 02 - Nebraska | 646260 | S1260 5 | 161 | 38807.6 | 38904.5 | 96.9
GEN-2018-033 | 02 - Nebraska | 646263 | S1263 5 | 161 | 8114.9 | 8115.8 | 0.9
GEN-2018-033 | 02 - Nebraska | 646278 | S1278 5 | 161 | 27650.2 | 27695.5 | 45.3
GEN-2018-033 | 02 - Nebraska | 646280 | S1280 5 | 161 | 10331.3 | 10332.5 | 1.2
GEN-2018-033 | 02 - Nebraska | 646281 | S1281 5 | 161 | 35317.2 | 35398.1 | 80.9
GEN-2018-033 | 02 - Nebraska | 646286 | S1286 5 | 161 | 26924.5 | 26950.6 | 26.1
GEN-2018-033 | 02 - Nebraska | 646287 | S1287 5 | 161 | 21900.7 | 21929.8 | 29.1
GEN-2018-033 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19145.6 | 19161 | 15.4
GEN-2018-033 | 02 - Nebraska | 646298 | S1298 5 | 161 | 29775.2 | 29814.9 | 39.7
GEN-2018-033 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28312.8 | 28348.8 | 36
GEN-2018-033 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27551.7 | 27585.8 | 34.1
GEN-2018-033 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33137.2 | 33188.3 | 51.1
GEN-2018-033 | 02 - Nebraska | 646361 | S1361 5 | 161 | 40654.8 | 40767.7 | 112.9
GEN-2018-033 | 02 - Nebraska | 646362 | S1362 5 | 161 | 34299.3 | 34371.2 | 71.9
GEN-2018-033 | 02 - Nebraska | 646363 | S1363 5 | 161 | 32065 | 32122.1 | 57.1
GEN-2018-033 | 02 - Nebraska | 646366 | S1366 5 | 161 | 16455.8 | 16465.8 | 10
GEN-2018-033 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32696.2 | 32712.7 | 16.5
GEN-2018-033 | 02 - Nebraska | 647015 | S6815T1&T2 8 | 69 | 12112.8 | 12115.1 | 2.3
GEN-2018-033 | 02 - Nebraska | 647016 | 6815TP38 | 69 | 17630.7 | 17635.2 | 4.5
GEN-2018-033 | 02 - Nebraska | 647017 | 6815TP98 | 69 | 12704.1 | 12706.5 | 2.4
GEN-2018-033 | 02 - Nebraska | 647815 | S6815T3 8 | 69 | 11470.3 | 11472.3 | 2
GEN-2018-033 | 02 - Nebraska | 647874 | S6874 8 | 69 | 8642.7 | 8643.8 | 1.1
GEN-2018-033 | 02 - Nebraska | 647901 | S901 8 | 69 | 27122.8 | 27131 | 8.2
GEN-2018-033 | 02 - Nebraska | 647904 | S904 8 | 69 | 8760.6 | 8761.7 | 1.1
GEN-2018-033 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 33202 | 33217.4 | 15.4
GEN-2018-033 | 02 - Nebraska | 647909 | S909 8 | 69 | 27167.8 | 27181 | 13.2
GEN-2018-033 | 02 - Nebraska | 647916 | S916 8 | 69 | 23884.7 | 23894.9 | 10.2
GEN-2018-033 | 02 - Nebraska | 647921 | S921 8 | 69 | 26542.9 | 26556.5 | 13.6
GEN-2018-033 | 02 - Nebraska | 647924 | S924 8 | 69 | 24682.9 | 24691.2 | 8.3
GEN-2018-033 | 02 - Nebraska | 647928 | S928 8 | 69 | 17313.7 | 17318.7 | 5
GEN-2018-033 | 02 - Nebraska | 647938 | S938 8 | 69 | 21923.7 | 21930.9 | 7.2
GEN-2018-033 | 02 - Nebraska | 647940 | S940 8 | 69 | 20971.4 | 20979.5 | 8.1
GEN-2018-033 | 02 - Nebraska | 647942 | S942 8 | 69 | 16243.2 | 16247.9 | 4.7
GEN-2018-033 | 02 - Nebraska | 647960 | S960 8 | 69 | 7454.9 | 7456.1 | 1.2
GEN-2018-033 | 02 - Nebraska | 647995 | S995 8 | 69 | 9525.7 | 9527 | 1.3
GEN-2018-033 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17841.3 | 17854.7 | 13.4
GEN-2018-033 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21394.3 | 21427 | 32.7
GEN-2018-033 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21267.9 | 21295.1 | 27.2
GEN-2018-033 | 02 - Nebraska | 650210 | NW70FAIRFD7 | 115 | 21611.7 | 21617.4 | 5.7
GEN-2018-033 | 02 - Nebraska | 650214 | NW68HOLDRG7 | 115 | 25909 | 25917.1 | 8.1
GEN-2018-033 | 02 - Nebraska | 650216 | SW27&F 7 | 115 | 22377.5 | 22383.7 | 6.2
GEN-2018-033 | 02 - Nebraska | 650242 | FOLSM&PHIL7 | 115 | 28223.3 | 28232.2 | 8.9
GEN-2018-033 | 02 - Nebraska | 650246 | SW7&BENNET7 | 115 | 23685.9 | 23691.9 | 6
GEN-2018-033 | 02 - Nebraska | 650262 | 57&GARLAND7 | 115 | 25794.4 | 25803.4 | 9
GEN-2018-033 | 02 - Nebraska | 650267 | 84LEIGHTON7 | 115 | 30005.2 | 30017.7 | 12.5
GEN-2018-033 | 02 - Nebraska | 650270 | 70&CALVERT7 | 115 | 27876.2 | 27886.4 | 10.2
GEN-2018-033 | 02 - Nebraska | 650271 | 81&OCHENEY7 | 115 | 25494.3 | 25502.8 | 8.5
GEN-2018-033 | 02 - Nebraska | 650272 | 91&A 7 | 115 | 22179.1 | 22185.7 | 6.6
GEN-2018-033 | 02 - Nebraska | 650273 | 93&O 7 | 115 | 22955.4 | 22962.6 | 7.2
GEN-2018-033 | 02 - Nebraska | 650274 | 91&HWY2 7 | 115 | 22051.6 | 22057.7 | 6.1
GEN-2018-033 | 02 - Nebraska | 650279 | 120&ALVO 7 | 115 | 22003.2 | 22010.4 | 7.2
GEN-2018-033 | 02 - Nebraska | 650283 | WAVERLY 7 | 115 | 21513 | 21519.5 | 6.5
GEN-2018-033 | 02 - Nebraska | 650284 | 84FLETCHER7 | 115 | 25431.5 | 25440.1 | 8.6
GEN-2018-033 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32677.4 | 32694.8 | 17.4
GEN-2018-033 | 02 - Nebraska | 650290 | ROKEBY 7 | 115 | 26072.4 | 26079.9 | 7.5
GEN-2018-033 | 02 - Nebraska | 652564 | SIOUXCY3 | 345 | 15925.1 | 15926.1 | 1
GEN-2018-033 | 02 - Nebraska | 653571 | GR ISLD3 | 345 | 13063.2 | 13064.2 | 1
GEN-2018-033 | 02 - Nebraska | 760746 | GEN-2017-115 | 345 | 12503.5 | 12508.1 | 4.6
GEN-2018-033 | 02 - Nebraska | 760788 | GEN-2017-201 | 345 | 9054.8 | 9055.2 | 0.4
GEN-2018-033 | 02 - Nebraska | 760872 | GEN-2017-198 | 69 | 25682.8 | 25690.1 | 7.3
GEN-2018-033 | 02 - Nebraska | 761208 | GEN-2017-210 | 345 | 10027.7 | 10029.1 | 1.4
GEN-2018-033 | 02 - Nebraska | 761292 | GEN-2017-181 | 345 | 6877.7 | 6878.7 | 1
GEN-2018-033 | 02 - Nebraska | 761313 | GEN-2017-182 | 345 | 5748.8 | 5749.4 | 0.6
GEN-2018-033 | 02 - Nebraska | 761376 | GEN-2017-183 | 345 | 7640.1 | 7640.2 | 0.1
GEN-2018-033 | 02 - Nebraska | 761383 | G17-183-TAP | 345 | 16776.8 | 16777.4 | 0.6
GEN-2018-033 | 02 - Nebraska | 762581 | GEN-2018-022 | 345 | 8886.6 | 8888.3 | 1.7
GEN-2018-033 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 21715.2 | 21765.4 | 50.2
GEN-2018-033 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | Project Bus - Disconnected | 23463 | Project Bus - Disconnected
GEN-2018-033 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 16511 | 16530 | 19
GEN-2018-033 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 13425.5 | 13437.6 | 12.1
GEN-2018-037 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32315.4 | 32362.1 | 46.7
GEN-2018-037 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39899.1 | 39966.4 | 67.3
GEN-2018-037 | 02 - Nebraska | 635002 | CBLUFFS8 | 69 | 25262.8 | 25279.1 | 16.3
GEN-2018-037 | 02 - Nebraska | 635003 | SUB701 5 | 161 | 21583.9 | 21652.1 | 68.2
GEN-2018-037 | 02 - Nebraska | 635004 | SUB701 8 | 69 | 22387.4 | 22408.7 | 21.3
GEN-2018-037 | 02 - Nebraska | 635005 | SUB702 5 | 161 | 20935.9 | 20989.2 | 53.3
GEN-2018-037 | 02 - Nebraska | 635006 | SUB703 8 | 69 | 10751.3 | 10755.3 | 4
GEN-2018-037 | 02 - Nebraska | 635007 | SUB704 8 | 69 | 13123.2 | 13129.6 | 6.4
GEN-2018-037 | 02 - Nebraska | 635008 | SUB705 8 | 69 | 12491.5 | 12497 | 5.5
GEN-2018-037 | 02 - Nebraska | 635009 | SUB706 8 | 69 | 10840.7 | 10844.5 | 3.8
GEN-2018-037 | 02 - Nebraska | 635010 | MANAWA 5 | 161 | 21770.3 | 21814.9 | 44.6
GEN-2018-037 | 02 - Nebraska | 635011 | INDNCRK5 | 161 | 22070.2 | 22114.2 | 44
GEN-2018-037 | 02 - Nebraska | 635015 | OVRLND 5 | 161 | 31623.5 | 31659.2 | 35.7
GEN-2018-037 | 02 - Nebraska | 635030 | RIVRBND5 | 161 | 36348.4 | 36403.2 | 54.8
GEN-2018-037 | 02 - Nebraska | 635075 | GLNWOOD8 | 69 | 6376.9 | 6377.6 | 0.7
GEN-2018-037 | 02 - Nebraska | 635076 | MALVERN8 | 69 | 7289.7 | 7290.2 | 0.5
GEN-2018-037 | 02 - Nebraska | 635080 | HONEYCK8 | 69 | 5849.4 | 5850.4 | 1
GEN-2018-037 | 02 - Nebraska | 635081 | MOVALLY8 | 69 | 4479.8 | 4480.2 | 0.4
GEN-2018-037 | 02 - Nebraska | 635082 | LOGAN 8 | 69 | 4624.7 | 4625 | 0.3
GEN-2018-037 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 30025.3 | 30064.3 | 39
GEN-2018-037 | 02 - Nebraska | 645451 | S3451 3 | 345 | 22728.9 | 22762.6 | 33.7
GEN-2018-037 | 02 - Nebraska | 645454 | S3454 3 | 345 | 29498.3 | 29540.1 | 41.8
GEN-2018-037 | 02 - Nebraska | 645455 | S3455 3 | 345 | 32650.3 | 32708.3 | 58
GEN-2018-037 | 02 - Nebraska | 645456 | S3456 3 | 345 | 35185.1 | 35257.3 | 72.2
GEN-2018-037 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30932.3 | 30944.5 | 12.2
GEN-2018-037 | 02 - Nebraska | 645459 | S3459 3 | 345 | 25698.7 | 25753.6 | 54.9
GEN-2018-037 | 02 - Nebraska | 646201 | S1201 5 | 161 | 32097.2 | 32265.4 | 168.2
GEN-2018-037 | 02 - Nebraska | 646206 | S1206 5 | 161 | 45233.9 | 45348.6 | 114.7
GEN-2018-037 | 02 - Nebraska | 646209 | S1209 5 | 161 | 47487.4 | 47646.6 | 159.2
GEN-2018-037 | 02 - Nebraska | 646210 | S1210 5 | 161 | 28266.5 | 28356.7 | 90.2
GEN-2018-037 | 02 - Nebraska | 646211 | S1211 5 | 161 | 36479.6 | 36876.8 | 397.2
GEN-2018-037 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30901.5 | 30972.5 | 71
GEN-2018-037 | 02 - Nebraska | 646217 | S1217 5 | 161 | 33612.5 | 33706.1 | 93.6
GEN-2018-037 | 02 - Nebraska | 646220 | S1220 5 | 161 | 28707.4 | 28862.8 | 155.4
GEN-2018-037 | 02 - Nebraska | 646221 | S1221 5 | 161 | 35727.4 | 35793.6 | 66.2
GEN-2018-037 | 02 - Nebraska | 646222 | S1222 5 | 161 | 27763.8 | 27862.9 | 99.1
GEN-2018-037 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25198.3 | 25223.7 | 25.4
GEN-2018-037 | 02 - Nebraska | 646227 | S1227 5 | 161 | 32897.1 | 32975.6 | 78.5
GEN-2018-037 | 02 - Nebraska | 646229 | S1229 5 | 161 | 29016.6 | 29139.9 | 123.3
GEN-2018-037 | 02 - Nebraska | 646231 | S1231 5 | 161 | 43473.2 | 43590.4 | 117.2
GEN-2018-037 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26869.2 | 26903.7 | 34.5
GEN-2018-037 | 02 - Nebraska | 646234 | S1234 5 | 161 | 27056.6 | 27088.9 | 32.3
GEN-2018-037 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34239.9 | 34298.3 | 58.4
GEN-2018-037 | 02 - Nebraska | 646236 | S1236 5 | 161 | 24654.5 | 24685.8 | 31.3
GEN-2018-037 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22343.5 | 22369.8 | 26.3
GEN-2018-037 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35598.3 | 35840.5 | 242.2
GEN-2018-037 | 02 - Nebraska | 646251 | S1251 5 | 161 | 32653.7 | 32699.8 | 46.1
GEN-2018-037 | 02 - Nebraska | 646252 | S1252 5 | 161 | 29955.1 | 30003 | 47.9
GEN-2018-037 | 02 - Nebraska | 646253 | S1253 5 | 161 | 27739.8 | 27774.5 | 34.7
GEN-2018-037 | 02 - Nebraska | 646255 | S1255 5 | 161 | 49169.6 | 49252.8 | 83.2
GEN-2018-037 | 02 - Nebraska | 646278 | S1278 5 | 161 | 27666.2 | 27695.5 | 29.3
GEN-2018-037 | 02 - Nebraska | 646286 | S1286 5 | 161 | 26815.2 | 26950.6 | 135.4
GEN-2018-037 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19124.7 | 19161 | 36.3
GEN-2018-037 | 02 - Nebraska | 646298 | S1298 5 | 161 | 29777.1 | 29814.9 | 37.8
GEN-2018-037 | 02 - Nebraska | 646299 | S1299 5 | 161 | 27895.7 | 28099.7 | 204
GEN-2018-037 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28314.5 | 28348.8 | 34.3
GEN-2018-037 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27553.3 | 27585.8 | 32.5
GEN-2018-037 | 02 - Nebraska | 646345 | S1345 5 | 161 | 22719.8 | 22745.9 | 26.1
GEN-2018-037 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33123.6 | 33188.3 | 64.7
GEN-2018-037 | 02 - Nebraska | 646366 | S1366 5 | 161 | 16452.4 | 16465.8 | 13.4
GEN-2018-037 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32688.1 | 32712.7 | 24.6
GEN-2018-037 | 02 - Nebraska | 647015 | S6815T1&T2 8 | 69 | 12111.8 | 12115.1 | 3.3
GEN-2018-037 | 02 - Nebraska | 647016 | 6815TP38 | 69 | 17628.2 | 17635.2 | 7
GEN-2018-037 | 02 - Nebraska | 647017 | 6815TP98 | 69 | 12702.9 | 12706.5 | 3.6
GEN-2018-037 | 02 - Nebraska | 647104 | MUD LNG8 | 69 | 14692.5 | 14700.6 | 8.1
GEN-2018-037 | 02 - Nebraska | 647105 | JCT205 8 | 69 | 22738.9 | 22759.5 | 20.6
GEN-2018-037 | 02 - Nebraska | 647815 | S6815T3 8 | 69 | 11469.3 | 11472.3 | 3
GEN-2018-037 | 02 - Nebraska | 647874 | S6874 8 | 69 | 8642 | 8643.8 | 1.8
GEN-2018-037 | 02 - Nebraska | 647901 | S901 8 | 69 | 27103.2 | 27131 | 27.8
GEN-2018-037 | 02 - Nebraska | 647902 | S902 8 | 69 | 9066.8 | 9067.8 | 1
GEN-2018-037 | 02 - Nebraska | 647904 | S904 8 | 69 | 8760.3 | 8761.7 | 1.4
GEN-2018-037 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 33191.5 | 33217.4 | 25.9
GEN-2018-037 | 02 - Nebraska | 647907 | S907 8 | 69 | 18051.1 | 18075.3 | 24.2
GEN-2018-037 | 02 - Nebraska | 647908 | S908 8 | 69 | 18661.9 | 18680.3 | 18.4
GEN-2018-037 | 02 - Nebraska | 647909 | S909 8 | 69 | 27156.8 | 27181 | 24.2
GEN-2018-037 | 02 - Nebraska | 647910 | S910 8 | 69 | 26104.6 | 26135.7 | 31.1
GEN-2018-037 | 02 - Nebraska | 647911 | S911 8 | 69 | 21357.6 | 21394.2 | 36.6
GEN-2018-037 | 02 - Nebraska | 647912 | S912 8 | 69 | 22895.5 | 22912.9 | 17.4
GEN-2018-037 | 02 - Nebraska | 647913 | S913 8 | 69 | 16251.9 | 16268.9 | 17
GEN-2018-037 | 02 - Nebraska | 647916 | S916 8 | 69 | 23878 | 23894.9 | 16.9
GEN-2018-037 | 02 - Nebraska | 647917 | S917 8 | 69 | 26035.5 | 26057.7 | 22.2
GEN-2018-037 | 02 - Nebraska | 647918 | S918 8 | 69 | 23003.5 | 23022.5 | 19
GEN-2018-037 | 02 - Nebraska | 647919 | S919 8 | 69 | 21585.7 | 21614.4 | 28.7
GEN-2018-037 | 02 - Nebraska | 647921 | S921 8 | 69 | 26537.3 | 26556.5 | 19.2
GEN-2018-037 | 02 - Nebraska | 647923 | S923 8 | 69 | 19270 | 19283.5 | 13.5
GEN-2018-037 | 02 - Nebraska | 647924 | S924 8 | 69 | 24674.5 | 24691.2 | 16.7
GEN-2018-037 | 02 - Nebraska | 647928 | S928 8 | 69 | 17311.4 | 17318.7 | 7.3
GEN-2018-037 | 02 - Nebraska | 647930 | S930 8 | 69 | 21622.5 | 21642.7 | 20.2
GEN-2018-037 | 02 - Nebraska | 647937 | S937 8 | 69 | 9165.1 | 9166.4 | 1.3
GEN-2018-037 | 02 - Nebraska | 647938 | S938 8 | 69 | 21919.8 | 21930.9 | 11.1
GEN-2018-037 | 02 - Nebraska | 647939 | S939 8 | 69 | 20181.7 | 20197 | 15.3
GEN-2018-037 | 02 - Nebraska | 647940 | S940 8 | 69 | 20966.9 | 20979.5 | 12.6
GEN-2018-037 | 02 - Nebraska | 647942 | S942 8 | 69 | 16241.2 | 16247.9 | 6.7
GEN-2018-037 | 02 - Nebraska | 647950 | S950 8 | 69 | 20403.2 | 20430.5 | 27.3
GEN-2018-037 | 02 - Nebraska | 647995 | S995 8 | 69 | 9524.9 | 9527 | 2.1
GEN-2018-037 | 02 - Nebraska | 760872 | GEN-2017-198 | 69 | 25665.1 | 25690.1 | 25
GEN-2018-037 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 21734.6 | 21765.4 | 30.8
GEN-2018-037 | 02 - Nebraska | 762713 | GEN-2018-037 | 161 | Project Bus - Disconnected | 34548.7 | Project Bus - Disconnected
GEN-2018-037 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 16518.4 | 16530 | 11.6
GEN-2018-037 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | 13430.2 | 13437.6 | 7.4
GEN-2018-043 | 02 - Nebraska | 45816 | J1581 SUB | 345 | 12314.6 | 12316 | 1.4
GEN-2018-043 | 02 - Nebraska | 45906 | J1590 SUB | 345 | 14976.4 | 14999.9 | 23.5
GEN-2018-043 | 02 - Nebraska | 87486 | J748GENTIE | 345 | 13944.9 | 13963.8 | 18.9
GEN-2018-043 | 02 - Nebraska | 87487 | J748POI | 345 | 15825.6 | 15850.2 | 24.6
GEN-2018-043 | 02 - Nebraska | 541510 | HOLT 7 | 345 | 14790.9 | 14795.8 | 4.9
GEN-2018-043 | 02 - Nebraska | 541511 | ROCKCK7 | 345 | 15898 | 15903.1 | 5.1
GEN-2018-043 | 02 - Nebraska | 541517 | HOLT_REACT7 | 345 | 14666.9 | 14671.7 | 4.8
GEN-2018-043 | 02 - Nebraska | 541543 | OUTLAW | 345 | 20271.9 | 20279.7 | 7.8
GEN-2018-043 | 02 - Nebraska | 587150 | GEN-2016-021 | 345 | 9404.6 | 9408.6 | 4
GEN-2018-043 | 02 - Nebraska | 601006 | SPLT RK3 | 345 | 14498.9 | 14502.4 | 3.5
GEN-2018-043 | 02 - Nebraska | 601034 | NOBLES 3 | 345 | 12314.6 | 12316 | 1.4
GEN-2018-043 | 02 - Nebraska | 603016 | SPLT RK7 | 115 | 39242.8 | 39248.8 | 6
GEN-2018-043 | 02 - Nebraska | 603149 | ANSON4 | 115 | 37153.6 | 37159 | 5.4
GEN-2018-043 | 02 - Nebraska | 603200 | ANSON 7 | 115 | 35679.1 | 35683.8 | 4.7
GEN-2018-043 | 02 - Nebraska | 603228 | SPLITRK CAP7 | 115 | 38644.9 | 38650.7 | 5.8
GEN-2018-043 | 02 - Nebraska | 603264 | PROSE WIND7 | 115 | 5096.4 | 5096.5 | 0.1
GEN-2018-043 | 02 - Nebraska | 603265 | PROSE CAP7 | 115 | 37213.6 | 37219 | 5.4
GEN-2018-043 | 02 - Nebraska | 635000 | CBLUFFS3 | 345 | 32220.8 | 32362.1 | 141.3
GEN-2018-043 | 02 - Nebraska | 635001 | CBLUFFS5 | 161 | 39858.8 | 39966.4 | 107.6
GEN-2018-043 | 02 - Nebraska | 635013 | PNYCRK 3 | 345 | 29327 | 29441.3 | 114.3
GEN-2018-043 | 02 - Nebraska | 635014 | OVRLND 3 | 345 | 27535.3 | 27634.8 | 99.5
GEN-2018-043 | 02 - Nebraska | 635016 | STHLND 3 | 345 | 29291.3 | 29405.4 | 114.1
GEN-2018-043 | 02 - Nebraska | 635200 | RAUN 3 | 345 | 28229 | 28396.9 | 167.9
GEN-2018-043 | 02 - Nebraska | 635201 | RAUN 5 | 161 | 28271.5 | 28335.9 | 64.4
GEN-2018-043 | 02 - Nebraska | 635202 | NEAL S 5 | 161 | 23334.5 | 23376.3 | 41.8
GEN-2018-043 | 02 - Nebraska | 635203 | NEAL N 5 | 161 | 26728.7 | 26786 | 57.3
GEN-2018-043 | 02 - Nebraska | 635204 | NEAL N 8 | 69 | 10245.4 | 10248.8 | 3.4
GEN-2018-043 | 02 - Nebraska | 635206 | IDA CO 3 | 345 | 9482.4 | 9490.4 | 8
GEN-2018-043 | 02 - Nebraska | 635219 | GARD AVE 3 | 345 | 9065.7 | 9072.1 | 6.4
GEN-2018-043 | 02 - Nebraska | 635220 | INTCHG 5 | 161 | 15178.1 | 15194.4 | 16.3
GEN-2018-043 | 02 - Nebraska | 635221 | KELLOGG5 | 161 | 17858.4 | 17879.4 | 21
GEN-2018-043 | 02 - Nebraska | 635222 | KELLOGG8 | 69 | 18510.5 | 18519.6 | 9.1
GEN-2018-043 | 02 - Nebraska | 635225 | MORNSD 5 | 161 | 11324.1 | 11331.4 | 7.3
GEN-2018-043 | 02 - Nebraska | 635226 | LEEDS 5 | 161 | 16507.1 | 16523.1 | 16
GEN-2018-043 | 02 - Nebraska | 635227 | SBRIDGE T8 | 69 | 8946 | 8948.5 | 2.5
GEN-2018-043 | 02 - Nebraska | 635229 | AIRPORT 5 | 161 | 17741.6 | 17764.7 | 23.1
GEN-2018-043 | 02 - Nebraska | 635230 | LIBERTY5 | 161 | 26019.5 | 26073.6 | 54.1
GEN-2018-043 | 02 - Nebraska | 635235 | SALIX 5 | 161 | 15268.9 | 15285.2 | 16.3
GEN-2018-043 | 02 - Nebraska | 635236 | SALIX 8 | 69 | 13856.3 | 13861.5 | 5.2
GEN-2018-043 | 02 - Nebraska | 635237 | SLOAN 8 | 69 | 4905.3 | 4905.9 | 0.6
GEN-2018-043 | 02 - Nebraska | 635252 | J412 POI 3 | 345 | 9898.1 | 9908 | 9.9
GEN-2018-043 | 02 - Nebraska | 635300 | MONONA 5 | 161 | 5718.5 | 5719.8 | 1.3
GEN-2018-043 | 02 - Nebraska | 635301 | MONONA 8 | 69 | 4714.9 | 4715.2 | 0.3
GEN-2018-043 | 02 - Nebraska | 635302 | MAPLTN 8 | 69 | 3178.6 | 3178.8 | 0.2
GEN-2018-043 | 02 - Nebraska | 635303 | SMITHLD8 | 69 | 2470.4 | 2470.5 | 0.1
GEN-2018-043 | 02 - Nebraska | 635330 | CRWFRD 5 | 161 | 5119.5 | 5120.1 | 0.6
GEN-2018-043 | 02 - Nebraska | 635368 | OBRIEN 3 | 345 | 15859.9 | 15868.2 | 8.3
GEN-2018-043 | 02 - Nebraska | 635398 | REMSEN 3 | 345 | 15211.9 | 15236.2 | 24.3
GEN-2018-043 | 02 - Nebraska | 635399 | CHEROKEE 3 | 345 | 16732.1 | 16758 | 25.9
GEN-2018-043 | 02 - Nebraska | 635400 | HIGHLND 3 | 345 | 15313.8 | 15326.1 | 12.3
GEN-2018-043 | 02 - Nebraska | 636010 | LEHIGH 3 | 345 | 13707.8 | 13711.6 | 3.8
GEN-2018-043 | 02 - Nebraska | 637009 | GLACIAL EDGE | 345 | 16443.4 | 16468.4 | 25
GEN-2018-043 | 02 - Nebraska | 637024 | RICHLAND W | 345 | 8995.5 | 9001.8 | 6.3
GEN-2018-043 | 02 - Nebraska | 640072 | BATTLCR7 | 115 | 7807.7 | 7808.6 | 0.9
GEN-2018-043 | 02 - Nebraska | 640073 | BATTLCR8 | 69 | 4107.7 | 4107.9 | 0.2
GEN-2018-043 | 02 - Nebraska | 640080 | BELDEN 7 | 115 | 6365.8 | 6366.3 | 0.5
GEN-2018-043 | 02 - Nebraska | 640081 | BELDEN 8 | 69 | 3905.8 | 3905.9 | 0.1
GEN-2018-043 | 02 - Nebraska | 640115 | CO.LINE7 | 115 | 7857.4 | 7858.1 | 0.7
GEN-2018-043 | 02 - Nebraska | 640125 | COLMB.E3 | 345 | 10712.3 | 10717.3 | 5
GEN-2018-043 | 02 - Nebraska | 640127 | COLMB.E7 | 115 | 23617.5 | 23623.3 | 5.8
GEN-2018-043 | 02 - Nebraska | 640133 | COLMBUS4 | 230 | 12278.5 | 12281.4 | 2.9
GEN-2018-043 | 02 - Nebraska | 640139 | COOPER 3 | 345 | 29855.5 | 29874.8 | 19.3
GEN-2018-043 | 02 - Nebraska | 640149 | CREITON7 | 115 | 5285.5 | 5285.6 | 0.1
GEN-2018-043 | 02 - Nebraska | 640150 | CREITON8 | 69 | 4744.7 | 4744.7 | 0
GEN-2018-043 | 02 - Nebraska | 640212 | HARTGTN7 | 115 | 5603 | 5603.3 | 0.3
GEN-2018-043 | 02 - Nebraska | 640213 | HARTGTN8 | 69 | 3716.6 | 3716.7 | 0.1
GEN-2018-043 | 02 - Nebraska | 640226 | HOSKINS3 | 345 | 13971.5 | 13982 | 10.5
GEN-2018-043 | 02 - Nebraska | 640227 | HOSKINS4 | 230 | 10690.4 | 10694.3 | 3.9
GEN-2018-043 | 02 - Nebraska | 640228 | HOSKINS7 | 115 | 19256.4 | 19262.7 | 6.3
GEN-2018-043 | 02 - Nebraska | 640263 | MADISON7 | 115 | 6502.8 | 6503.4 | 0.6
GEN-2018-043 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23953.8 | 23977.3 | 23.5
GEN-2018-043 | 02 - Nebraska | 640293 | NELIGH 7 | 115 | 11405.9 | 11406.9 | 1
GEN-2018-043 | 02 - Nebraska | 640294 | NELIGH 8 | 69 | 6384.8 | 6384.9 | 0.1
GEN-2018-043 | 02 - Nebraska | 640296 | NORFK.N7 | 115 | 14009.6 | 14012.8 | 3.2
GEN-2018-043 | 02 - Nebraska | 640298 | NORFOLK7 | 115 | 13133 | 13135.8 | 2.8
GEN-2018-043 | 02 - Nebraska | 640342 | SHELCRK3 | 345 | 10998.9 | 11004.2 | 5.3
GEN-2018-043 | 02 - Nebraska | 640343 | SHELCRK4 | 230 | 11553.5 | 11556.4 | 2.9
GEN-2018-043 | 02 - Nebraska | 640357 | STANTON7 | 115 | 5383.2 | 5384 | 0.8
GEN-2018-043 | 02 - Nebraska | 640363 | STNTN.N7 | 115 | 7354.9 | 7356.1 | 1.2
GEN-2018-043 | 02 - Nebraska | 640377 | TEKAMAH5 | 161 | 9300.8 | 9314.4 | 13.6
GEN-2018-043 | 02 - Nebraska | 640378 | TEKAMAH7 | 115 | 8591.7 | 8598.1 | 6.4
GEN-2018-043 | 02 - Nebraska | 640386 | TWIN CH4 | 230 | 9338.1 | 9341.9 | 3.8
GEN-2018-043 | 02 - Nebraska | 640387 | TWIN CH7 | 115 | 11315.7 | 11318.7 | 3
GEN-2018-043 | 02 - Nebraska | 640388 | TWIN CH8 | 69 | 8171.7 | 8172.7 | 1
GEN-2018-043 | 02 - Nebraska | 640424 | S.SIOUXCITY7 | 115 | 7736.5 | 7737.9 | 1.4
GEN-2018-043 | 02 - Nebraska | 640425 | S.SIOUXCITY8 | 69 | 4721.3 | 4721.6 | 0.3
GEN-2018-043 | 02 - Nebraska | 640520 | ANTELOPE 3 | 345 | 7195.7 | 7197.9 | 2.2
GEN-2018-043 | 02 - Nebraska | 640521 | ANTELOPE 7 | 115 | 16723.6 | 16726 | 2.4
GEN-2018-043 | 02 - Nebraska | 640522 | ANTELOPE 8 | 69 | 5511.9 | 5512.1 | 0.2
GEN-2018-043 | 02 - Nebraska | 640560 | WAKEFIELD 4 | 230 | 8369.7 | 8371.9 | 2.2
GEN-2018-043 | 02 - Nebraska | 640561 | RTLSNAKE.W 4 | 230 | 7471.6 | 7473.2 | 1.6
GEN-2018-043 | 02 - Nebraska | 640588 | TURTLE.CRK 3 | 345 | 12312.9 | 12320.3 | 7.4
GEN-2018-043 | 02 - Nebraska | 640589 | SHOLES.W 3 | 345 | 9995.4 | 10000 | 4.6
GEN-2018-043 | 02 - Nebraska | 643254 | UPSTREAM.W 7 | 115 | 15987.1 | 15989.2 | 2.1
GEN-2018-043 | 02 - Nebraska | 643271 | PLUMBCR.W 3 | 345 | 12056.6 | 12063.7 | 7.1
GEN-2018-043 | 02 - Nebraska | 645100 | FC1A 5 | 161 | 29689.7 | 30064.3 | 374.6
GEN-2018-043 | 02 - Nebraska | 645451 | S3451 3 | 345 | 22124.9 | 22762.6 | 637.7
GEN-2018-043 | 02 - Nebraska | 645454 | S3454 3 | 345 | 29285.9 | 29540.1 | 254.2
GEN-2018-043 | 02 - Nebraska | 645455 | S3455 3 | 345 | 32440.6 | 32708.3 | 267.7
GEN-2018-043 | 02 - Nebraska | 645456 | S3456 3 | 345 | 34960.7 | 35257.3 | 296.6
GEN-2018-043 | 02 - Nebraska | 645458 | S3458 3 | 345 | 30886.2 | 30944.5 | 58.3
GEN-2018-043 | 02 - Nebraska | 645459 | S3459 3 | 345 | 25445.8 | 25753.6 | 307.8
GEN-2018-043 | 02 - Nebraska | 645740 | S3740 3 | 345 | 23361.2 | 23464.5 | 103.3
GEN-2018-043 | 02 - Nebraska | 645761 | S3761 3 | 345 | 23216.5 | 23351.2 | 134.7
GEN-2018-043 | 02 - Nebraska | 646201 | S1201 5 | 161 | 32160.1 | 32265.4 | 105.3
GEN-2018-043 | 02 - Nebraska | 646206 | S1206 5 | 161 | 45165.5 | 45348.6 | 183.1
GEN-2018-043 | 02 - Nebraska | 646209 | S1209 5 | 161 | 47283.4 | 47646.6 | 363.2
GEN-2018-043 | 02 - Nebraska | 646211 | S1211 5 | 161 | 36730.4 | 36876.8 | 146.4
GEN-2018-043 | 02 - Nebraska | 646216 | S1216 5 | 161 | 30872.8 | 30972.5 | 99.7
GEN-2018-043 | 02 - Nebraska | 646221 | S1221 5 | 161 | 35627 | 35793.6 | 166.6
GEN-2018-043 | 02 - Nebraska | 646226 | S1226 5 | 161 | 25037.9 | 25223.7 | 185.8
GEN-2018-043 | 02 - Nebraska | 646227 | S1227 5 | 161 | 32840.9 | 32975.6 | 134.7
GEN-2018-043 | 02 - Nebraska | 646231 | S1231 5 | 161 | 43325.5 | 43590.4 | 264.9
GEN-2018-043 | 02 - Nebraska | 646232 | S1232 5 | 161 | 26835 | 26903.7 | 68.7
GEN-2018-043 | 02 - Nebraska | 646233 | S1233 5 | 161 | 29498.5 | 29608.2 | 109.7
GEN-2018-043 | 02 - Nebraska | 646235 | S1235 5 | 161 | 34129.6 | 34298.3 | 168.7
GEN-2018-043 | 02 - Nebraska | 646237 | S1237 5 | 161 | 21964.8 | 22050.7 | 85.9
GEN-2018-043 | 02 - Nebraska | 646244 | S1244 5 | 161 | 22327.8 | 22369.8 | 42
GEN-2018-043 | 02 - Nebraska | 646249 | S1249 5 | 161 | 25231.5 | 25311.9 | 80.4
GEN-2018-043 | 02 - Nebraska | 646250 | S1250 5 | 161 | 35663.7 | 35840.5 | 176.8
GEN-2018-043 | 02 - Nebraska | 646251 | S1251 5 | 161 | 32257.4 | 32699.8 | 442.4
GEN-2018-043 | 02 - Nebraska | 646252 | S1252 5 | 161 | 29851.6 | 30003 | 151.4
GEN-2018-043 | 02 - Nebraska | 646254 | S1254 5 | 161 | 32675.8 | 32803.5 | 127.7
GEN-2018-043 | 02 - Nebraska | 646255 | S1255 5 | 161 | 48970.7 | 49252.8 | 282.1
GEN-2018-043 | 02 - Nebraska | 646256 | S1256 5 | 161 | 22851.3 | 22922 | 70.7
GEN-2018-043 | 02 - Nebraska | 646259 | S1259 5 | 161 | 38622.7 | 38783.6 | 160.9
GEN-2018-043 | 02 - Nebraska | 646281 | S1281 5 | 161 | 35270.5 | 35398.1 | 127.6
GEN-2018-043 | 02 - Nebraska | 646287 | S1287 5 | 161 | 21883.8 | 21929.8 | 46
GEN-2018-043 | 02 - Nebraska | 646291 | S1291 5 | 161 | 7151.7 | 7162.2 | 10.5
GEN-2018-043 | 02 - Nebraska | 646297 | S1297 5 | 161 | 19062.8 | 19161 | 98.2
GEN-2018-043 | 02 - Nebraska | 646298 | S1298 5 | 161 | 29469.4 | 29814.9 | 345.5
GEN-2018-043 | 02 - Nebraska | 646305 | S1305 5 | 161 | 28033 | 28348.8 | 315.8
GEN-2018-043 | 02 - Nebraska | 646341 | S1341 5 | 161 | 27283.4 | 27585.8 | 302.4
GEN-2018-043 | 02 - Nebraska | 646347 | S1347 5 | 161 | 33015 | 33188.3 | 173.3
GEN-2018-043 | 02 - Nebraska | 646361 | S1361 5 | 161 | 40594.4 | 40767.7 | 173.3
GEN-2018-043 | 02 - Nebraska | 646363 | S1363 5 | 161 | 32032.3 | 32122.1 | 89.8
GEN-2018-043 | 02 - Nebraska | 647006 | S906 N 8 | 69 | 32674.4 | 32712.7 | 38.3
GEN-2018-043 | 02 - Nebraska | 647104 | MUD LNG8 | 69 | 14689.6 | 14700.6 | 11
GEN-2018-043 | 02 - Nebraska | 647906 | S906 S 8 | 69 | 33182.4 | 33217.4 | 35
GEN-2018-043 | 02 - Nebraska | 647909 | S909 8 | 69 | 27143.3 | 27181 | 37.7
GEN-2018-043 | 02 - Nebraska | 647918 | S918 8 | 69 | 22996.4 | 23022.5 | 26.1
GEN-2018-043 | 02 - Nebraska | 647921 | S921 8 | 69 | 26522.5 | 26556.5 | 34
GEN-2018-043 | 02 - Nebraska | 647937 | S937 8 | 69 | 9163.6 | 9166.4 | 2.8
GEN-2018-043 | 02 - Nebraska | 647939 | S939 8 | 69 | 20176.3 | 20197 | 20.7
GEN-2018-043 | 02 - Nebraska | 647950 | S950 8 | 69 | 20408.4 | 20430.5 | 22.1
GEN-2018-043 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17836.8 | 17854.7 | 17.9
GEN-2018-043 | 02 - Nebraska | 650185 | WAGENER 3 | 345 | 21387.1 | 21427 | 39.9
GEN-2018-043 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21264.4 | 21295.1 | 30.7
GEN-2018-043 | 02 - Nebraska | 650214 | NW68HOLDRG7 | 115 | 25906.2 | 25917.1 | 10.9
GEN-2018-043 | 02 - Nebraska | 650267 | 84LEIGHTON7 | 115 | 30001.3 | 30017.7 | 16.4
GEN-2018-043 | 02 - Nebraska | 650271 | 81&OCHENEY7 | 115 | 25491.8 | 25502.8 | 11
GEN-2018-043 | 02 - Nebraska | 650279 | 120&ALVO 7 | 115 | 22001 | 22010.4 | 9.4
GEN-2018-043 | 02 - Nebraska | 650285 | WAGENER 7 | 115 | 32672.6 | 32694.8 | 22.2
GEN-2018-043 | 02 - Nebraska | 652509 | FTRANDL4 | 230 | 11290.3 | 11291.1 | 0.8
GEN-2018-043 | 02 - Nebraska | 652537 | WHITE 3 | 345 | 18765.4 | 18765.8 | 0.4
GEN-2018-043 | 02 - Nebraska | 652552 | SIOUXCY2 | 230 | 20820.8 | 20845.3 | 24.5
GEN-2018-043 | 02 - Nebraska | 652564 | SIOUXCY3 | 345 | 15896.2 | 15926.1 | 29.9
GEN-2018-043 | 02 - Nebraska | 652565 | SIOUXCY4 | 230 | 20820.8 | 20845.3 | 24.5
GEN-2018-043 | 02 - Nebraska | 652566 | SIOUXCY5 | 161 | 21666.3 | 21687.5 | 21.2
GEN-2018-043 | 02 - Nebraska | 652567 | DENISON4 | 230 | 4741.7 | 4742.4 | 0.7
GEN-2018-043 | 02 - Nebraska | 652864 | SIOUXCY-LNX3 | 345 | 15706 | 15735.1 | 29.1
GEN-2018-043 | 02 - Nebraska | 655126 | MOS-VERM-ER8 | 69 | 2021.3 | 2021.3 | 0
GEN-2018-043 | 02 - Nebraska | 655129 | SW806-ER8 | 69 | 878.9 | 878.9 | 0
GEN-2018-043 | 02 - Nebraska | 655130 | SW808-ER8 | 69 | 2540.2 | 2540.3 | 0.1
GEN-2018-043 | 02 - Nebraska | 655133 | SW822-ER8 | 69 | 2195.3 | 2195.3 | 0
GEN-2018-043 | 02 - Nebraska | 655136 | SW832-ER8 | 69 | 2622.6 | 2622.7 | 0.1
GEN-2018-043 | 02 - Nebraska | 655137 | SW833-ER8 | 69 | 2094.1 | 2094.1 | 0
GEN-2018-043 | 02 - Nebraska | 655145 | SW870-ER8 | 69 | 2888.2 | 2888.3 | 0.1
GEN-2018-043 | 02 - Nebraska | 655146 | SW873-ER8 | 69 | 2886.9 | 2887 | 0.1
GEN-2018-043 | 02 - Nebraska | 655147 | MOS-JEFF-ER8 | 69 | 2540.9 | 2541 | 0.1
GEN-2018-043 | 02 - Nebraska | 655151 | MOS-BGSP-ER8 | 69 | 1364.7 | 1364.7 | 0
GEN-2018-043 | 02 - Nebraska | 655152 | SW894-ER8 | 69 | 2067 | 2067.1 | 0.1
GEN-2018-043 | 02 - Nebraska | 655308 | ALCESTER-ER8 | 69 | 1026.4 | 1026.4 | 0
GEN-2018-043 | 02 - Nebraska | 655311 | AKRON-ER8 | 69 | 1531.1 | 1531.1 | 0
GEN-2018-043 | 02 - Nebraska | 655313 | RICHLAND-ER8 | 69 | 2531.9 | 2532 | 0.1
GEN-2018-043 | 02 - Nebraska | 655314 | ELKPNTCY-ER8 | 69 | 1938.3 | 1938.3 | 0
GEN-2018-043 | 02 - Nebraska | 655315 | ELKPOINT-ER8 | 69 | 1937.6 | 1937.6 | 0
GEN-2018-043 | 02 - Nebraska | 655316 | BURBANK-ER8 | 69 | 1880.3 | 1880.3 | 0
GEN-2018-043 | 02 - Nebraska | 655326 | BGSPRING-ER8 | 69 | 1180.9 | 1180.9 | 0
GEN-2018-043 | 02 - Nebraska | 655327 | UNIONCRK-ER8 | 69 | 2001.3 | 2001.3 | 0
GEN-2018-043 | 02 - Nebraska | 655359 | JEFERSON-ER8 | 69 | 1687.8 | 1687.8 | 0
GEN-2018-043 | 02 - Nebraska | 655360 | MCOOKLK-ER8 | 69 | 1360.9 | 1360.9 | 0
GEN-2018-043 | 02 - Nebraska | 655393 | SWR5123-ER8 | 69 | 978.9 | 978.9 | 0
GEN-2018-043 | 02 - Nebraska | 655427 | MOS-ALC2-ER8 | 69 | 1026.4 | 1026.4 | 0
GEN-2018-043 | 02 - Nebraska | 655428 | BIGSPRGS-ER8 | 69 | 1180.9 | 1180.9 | 0
GEN-2018-043 | 02 - Nebraska | 655484 | RASMUSN-ER4 | 230 | 6913.1 | 6914.9 | 1.8
GEN-2018-043 | 02 - Nebraska | 655485 | RASMUSN-ER8 | 69 | 3317.8 | 3317.9 | 0.1
GEN-2018-043 | 02 - Nebraska | 658122 | ROCKRPDMUNI8 | 69 | 2846.6 | 2846.6 | 0
GEN-2018-043 | 02 - Nebraska | 658124 | LUVERNEMUNW8 | 69 | 1825.9 | 1825.9 | 0
GEN-2018-043 | 02 - Nebraska | 658126 | LUVERNEMUNE8 | 69 | 1728.7 | 1728.7 | 0
GEN-2018-043 | 02 - Nebraska | 658128 | LUVERNEMUNS8 | 69 | 1831.6 | 1831.6 | 0
GEN-2018-043 | 02 - Nebraska | 659286 | DEERCREK-BE3 | 345 | 18248.2 | 18248.6 | 0.4
GEN-2018-043 | 02 - Nebraska | 659311 | PAHOJA__-BE4 | 230 | 7660.1 | 7661.2 | 1.1
GEN-2018-043 | 02 - Nebraska | 659708 | LITLRCKT-LO8 | 69 | 1972.9 | 1973 | 0.1
GEN-2018-043 | 02 - Nebraska | 659709 | LITLRCK -LO8 | 69 | 1932 | 1932 | 0
GEN-2018-043 | 02 - Nebraska | 659710 | GEORGETP-LO8 | 69 | 2390.3 | 2390.3 | 0
GEN-2018-043 | 02 - Nebraska | 659711 | GEORGE -LO8 | 69 | 2328.5 | 2328.5 | 0
GEN-2018-043 | 02 - Nebraska | 659712 | RKRMUNTP-LO8 | 69 | 3390.8 | 3390.9 | 0.1
GEN-2018-043 | 02 - Nebraska | 659714 | RKRPDTAP-LO8 | 69 | 3605.5 | 3605.5 | 0
GEN-2018-043 | 02 - Nebraska | 659715 | ROCKRPDS-LO8 | 69 | 3449 | 3449.1 | 0.1
GEN-2018-043 | 02 - Nebraska | 659726 | STEEN -LO8 | 69 | 2348.1 | 2348.1 | 0
GEN-2018-043 | 02 - Nebraska | 659727 | LUVERNE -LO8 | 69 | 1864.9 | 1864.9 | 0
GEN-2018-043 | 02 - Nebraska | 659735 | CLEVELND-LO4 | 230 | 5108.6 | 5109.1 | 0.5
GEN-2018-043 | 02 - Nebraska | 659736 | CLEVELND-LO8 | 69 | 4446.5 | 4446.6 | 0.1
GEN-2018-043 | 02 - Nebraska | 659900 | EAGLE___-NI4 | 230 | 7512.3 | 7514.1 | 1.8
GEN-2018-043 | 02 - Nebraska | 659901 | EAGLE___-NI8 | 69 | 14410.2 | 14412.2 | 2
GEN-2018-043 | 02 - Nebraska | 760515 | GEN-2017-222 | 230 | 3610.9 | 3611.3 | 0.4
GEN-2018-043 | 02 - Nebraska | 760746 | GEN-2017-115 | 345 | 12504.6 | 12508.1 | 3.5
GEN-2018-043 | 02 - Nebraska | 760788 | GEN-2017-201 | 345 | 9051.4 | 9055.2 | 3.8
GEN-2018-043 | 02 - Nebraska | 762069 | G17-105TAP | 161 | 8721.8 | 8733.1 | 11.3
GEN-2018-043 | 02 - Nebraska | 762070 | GEN-2017-105 | 161 | 8721.8 | 8733.1 | 11.3
GEN-2018-043 | 02 - Nebraska | 762504 | GEN-2018-012 | 345 | 5931 | 5932.5 | 1.5
GEN-2018-043 | 02 - Nebraska | 762509 | G18-012-DUMY | 345 | 7195.7 | 7197.9 | 2.2
GEN-2018-043 | 02 - Nebraska | 762603 | GEN-2018-025 | 345 | 21182.2 | 21765.4 | 583.2
GEN-2018-043 | 02 - Nebraska | 762691 | GEN-2018-033 | 345 | 23359.7 | 23463 | 103.3
GEN-2018-043 | 02 - Nebraska | 762713 | GEN-2018-037 | 161 | 34420.4 | 34548.7 | 128.3
GEN-2018-043 | 02 - Nebraska | 762779 | G18-043-TAP | 345 | 15570.8 | 16530 | 959.2
GEN-2018-043 | 02 - Nebraska | 762780 | GEN-2018-043 | 345 | Project Bus - Disconnected | 13437.6 | Project Bus - Disconnected
GEN-2018-056 | 02 - Nebraska | 7777 | GRPR_DMY1 | 345 | 6559 | 6711.7 | 152.7
GEN-2018-056 | 02 - Nebraska | 8888 | GRPR_DMY2 | 345 | 6921.7 | 7096.3 | 174.6
GEN-2018-056 | 02 - Nebraska | 579450 | GEN-2016-075 | 345 | 6559 | 6711.7 | 152.7
GEN-2018-056 | 02 - Nebraska | 584650 | GEN-2015-023 | 345 | 8020.9 | 8125.2 | 104.3
GEN-2018-056 | 02 - Nebraska | 587680 | GEN-2016-074 | 345 | 6707.9 | 6709.8 | 1.9
GEN-2018-056 | 02 - Nebraska | 587760 | GEN-2016-094 | 230 | 8428.4 | 8432.7 | 4.3
GEN-2018-056 | 02 - Nebraska | 587764 | G16-094-TAP | 230 | 8581.7 | 8586.1 | 4.4
GEN-2018-056 | 02 - Nebraska | 589320 | GEN-2017-094 | 230 | 5874.2 | 5875.4 | 1.2
GEN-2018-056 | 02 - Nebraska | 589324 | G17-094-TAP | 230 | 7432.4 | 7434.3 | 1.9
GEN-2018-056 | 02 - Nebraska | 640096 | CALAMS 7 | 115 | 3534.8 | 3535.3 | 0.5
GEN-2018-056 | 02 - Nebraska | 640183 | GENTLMN3 | 345 | 16306.6 | 16314.5 | 7.9
GEN-2018-056 | 02 - Nebraska | 640184 | GENTLMN4 | 230 | 19797.4 | 19802.2 | 4.8
GEN-2018-056 | 02 - Nebraska | 640200 | GR ISLD4 | 230 | 17480 | 17500 | 20
GEN-2018-056 | 02 - Nebraska | 640252 | KEYSTON3 | 345 | 8818.5 | 8820.3 | 1.8
GEN-2018-056 | 02 - Nebraska | 640271 | MCCOOL 3 | 345 | 11464 | 11471 | 7
GEN-2018-056 | 02 - Nebraska | 640325 | REDWILO3 | 345 | 6540.8 | 6541.4 | 0.6
GEN-2018-056 | 02 - Nebraska | 640359 | STAPLETON 7 | 115 | 4240.2 | 4240.9 | 0.7
GEN-2018-056 | 02 - Nebraska | 640360 | STAPLETON 8 | 69 | 3461 | 3461.2 | 0.2
GEN-2018-056 | 02 - Nebraska | 640374 | SWEET W3 | 345 | 11247.3 | 11253.2 | 5.9
GEN-2018-056 | 02 - Nebraska | 640381 | THEDFRD7 | 115 | 9064.9 | 9072.8 | 7.9
GEN-2018-056 | 02 - Nebraska | 640500 | THEDFRD3 | 345 | 5273.1 | 5283.4 | 10.3
GEN-2018-056 | 02 - Nebraska | 640510 | HOLT.CO3 | 345 | 8084.6 | 8190.7 | 106.1
GEN-2018-056 | 02 - Nebraska | 648513 | GRPR1 3 | 345 | 6921.7 | 7096.3 | 174.6
GEN-2018-056 | 02 - Nebraska | 648520 | GRPR2 3 | 345 | 6559 | 6711.7 | 152.7
GEN-2018-056 | 02 - Nebraska | 652276 | FTTHOMP8 | 69 | 4608.5 | 4608.7 | 0.2
GEN-2018-056 | 02 - Nebraska | 652506 | FTTHOMP3 | 345 | 8744.5 | 8770 | 25.5
GEN-2018-056 | 02 - Nebraska | 652507 | FTTHOMP4 | 230 | 19046.1 | 19072.3 | 26.2
GEN-2018-056 | 02 - Nebraska | 652509 | FTRANDL4 | 230 | 11289.6 | 11291.1 | 1.5
GEN-2018-056 | 02 - Nebraska | 652514 | HURON 4 | 230 | 11194.6 | 11196.9 | 2.3
GEN-2018-056 | 02 - Nebraska | 652519 | OAHE 4 | 230 | 12550.8 | 12556.2 | 5.4
GEN-2018-056 | 02 - Nebraska | 652532 | GR PRAIRIE 3 | 345 | 7323.4 | 7532.3 | 208.9
GEN-2018-056 | 02 - Nebraska | 652540 | BIGBND14 | 230 | 11878.5 | 11887.4 | 8.9
GEN-2018-056 | 02 - Nebraska | 652541 | BIGBND24 | 230 | 11802.9 | 11811.6 | 8.7
GEN-2018-056 | 02 - Nebraska | 652606 | LETCHER4 | 230 | 4900.8 | 4901.3 | 0.5
GEN-2018-056 | 02 - Nebraska | 652607 | WESSINGTON 4 | 230 | 5996.8 | 5997.9 | 1.1
GEN-2018-056 | 02 - Nebraska | 652806 | FTTHOM1-LNX3 | 345 | 8655.8 | 8680.8 | 25
GEN-2018-056 | 02 - Nebraska | 652807 | FTTHOM2-LNX3 | 345 | 8744.5 | 8770 | 25.5
GEN-2018-056 | 02 - Nebraska | 652808 | FTTHOM1-LNX5 | 345 | 8677.8 | 8702.9 | 25.1
GEN-2018-056 | 02 - Nebraska | 652832 | GRPRAR1-LNX3 | 345 | 7323.4 | 7532.3 | 208.9
GEN-2018-056 | 02 - Nebraska | 652833 | GRPRAR2-LNX3 | 345 | 7323.4 | 7532.3 | 208.9
GEN-2018-056 | 02 - Nebraska | 653571 | GR ISLD3 | 345 | 13039.5 | 13064.2 | 24.7
GEN-2018-056 | 02 - Nebraska | 653871 | GR ISLD-LNX3 | 345 | 12908 | 12932.9 | 24.9
GEN-2018-056 | 02 - Nebraska | 655076 | MOS-PLAT-ER8 | 69 | 1498.8 | 1498.8 | 0
GEN-2018-056 | 02 - Nebraska | 655079 | MOS-KLKP-ER8 | 69 | 805.9 | 805.9 | 0
GEN-2018-056 | 02 - Nebraska | 655080 | MOS-HLTP-ER8 | 69 | 1369.8 | 1369.9 | 0.1
GEN-2018-056 | 02 - Nebraska | 655081 | MOS-KMBL-ER8 | 69 | 745.8 | 745.8 | 0
GEN-2018-056 | 02 - Nebraska | 655093 | SW-HARSN-ER8 | 69 | 1088.8 | 1088.8 | 0
GEN-2018-056 | 02 - Nebraska | 655098 | SW-GEDES-ER8 | 69 | 1371.1 | 1371.1 | 0
GEN-2018-056 | 02 - Nebraska | 655153 | MOS-AMES-ER8 | 69 | 4546.8 | 4547 | 0.2
GEN-2018-056 | 02 - Nebraska | 655158 | MOS-HYDE-ER8 | 69 | 3614.9 | 3614.9 | 0
GEN-2018-056 | 02 - Nebraska | 655240 | HGHMORE-ER8 | 69 | 2243.2 | 2243.2 | 0
GEN-2018-056 | 02 - Nebraska | 655250 | CHMBRLAN-ER8 | 69 | 1658 | 1658.1 | 0.1
GEN-2018-056 | 02 - Nebraska | 655251 | PLATTE-ER8 | 69 | 2175 | 2175 | 0
GEN-2018-056 | 02 - Nebraska | 655252 | RIVERVW-ER8 | 69 | 1525.2 | 1525.2 | 0
GEN-2018-056 | 02 - Nebraska | 655253 | PUKWANA-ER8 | 69 | 1163.6 | 1163.6 | 0
GEN-2018-056 | 02 - Nebraska | 655254 | HILLTOP-ER8 | 69 | 1166.9 | 1166.9 | 0
GEN-2018-056 | 02 - Nebraska | 655255 | KIMBALL-ER8 | 69 | 698.1 | 698.1 | 0
GEN-2018-056 | 02 - Nebraska | 655274 | HARRISON-ER8 | 69 | 1076.5 | 1076.5 | 0
GEN-2018-056 | 02 - Nebraska | 655277 | GEDDES-ER8 | 69 | 968.1 | 968.1 | 0
GEN-2018-056 | 02 - Nebraska | 655328 | BIGBEND-ER8 | 69 | 3376 | 3376.2 | 0.2
GEN-2018-056 | 02 - Nebraska | 655329 | GANNVALL-ER8 | 69 | 904.9 | 904.9 | 0
GEN-2018-056 | 02 - Nebraska | 655352 | AMES-ER8 | 69 | 1402.6 | 1402.6 | 0
GEN-2018-056 | 02 - Nebraska | 655384 | NWPS8645-ER8 | 69 | 2282.9 | 2282.9 | 0
GEN-2018-056 | 02 - Nebraska | 655385 | MOS-LKPL-ER8 | 69 | 4185.8 | 4186 | 0.2
GEN-2018-056 | 02 - Nebraska | 655386 | MOS-RVR1-ER8 | 69 | 2186.2 | 2186.2 | 0
GEN-2018-056 | 02 - Nebraska | 655387 | MOS-RVR2-ER8 | 69 | 2175.6 | 2175.6 | 0
GEN-2018-056 | 02 - Nebraska | 655388 | NWPS7632-ER8 | 69 | 1571.2 | 1571.2 | 0
GEN-2018-056 | 02 - Nebraska | 655394 | SW425-ER8 | 69 | 1314.3 | 1314.4 | 0.1
GEN-2018-056 | 02 - Nebraska | 655475 | LAKPLAT-ER4 | 230 | 5783.3 | 5784.5 | 1.2
GEN-2018-056 | 02 - Nebraska | 655476 | LAKPLAT-ER8 | 69 | 4200.9 | 4201.1 | 0.2
GEN-2018-056 | 02 - Nebraska | 659130 | CHAPELLE-BE3 | 345 | 6375.2 | 6387 | 11.8
GEN-2018-056 | 02 - Nebraska | 659295 | SD.PW1__-BE4 | 230 | 4642.4 | 4643 | 0.6
GEN-2018-056 | 02 - Nebraska | 659433 | TRIPLEH__UA3 | 345 | 6303.4 | 6315 | 11.6
GEN-2018-056 | 02 - Nebraska | 760767 | GEN-2017-144 | 345 | 7752.5 | 7849.8 | 97.3
GEN-2018-056 | 02 - Nebraska | 761208 | GEN-2017-210 | 345 | 10023.8 | 10029.1 | 5.3
GEN-2018-056 | 02 - Nebraska | 762911 | GEN-2018-056 | 345 | Project Bus - Disconnected | 6968 | Project Bus - Disconnected
GEN-2018-060 | 02 - Nebraska | 515852 | DGRASSE7 | 345 | 14337.7 | 14338 | 0.3
GEN-2018-060 | 02 - Nebraska | 523118 | BUFF_DUNES 7 | 345 | 5818.8 | 5819.1 | 0.3
GEN-2018-060 | 02 - Nebraska | 523853 | FINNEY 7 | 345 | 9766 | 9766.8 | 0.8
GEN-2018-060 | 02 - Nebraska | 530551 | SALINE 3 | 115 | 5080.9 | 5081.5 | 0.6
GEN-2018-060 | 02 - Nebraska | 530552 | GORHAM 3 | 115 | 3264.4 | 3264.7 | 0.3
GEN-2018-060 | 02 - Nebraska | 530553 | S HAYS 3 | 115 | 9058.9 | 9061.2 | 2.3
GEN-2018-060 | 02 - Nebraska | 530558 | KNOLL N 6 | 230 | 11972 | 11983.2 | 11.2
GEN-2018-060 | 02 - Nebraska | 530560 | WKNNY 3 | 115 | 2264.8 | 2265 | 0.2
GEN-2018-060 | 02 - Nebraska | 530561 | KNOLL 3 | 115 | 11200.8 | 11204.3 | 3.5
GEN-2018-060 | 02 - Nebraska | 530562 | HAYS 3 | 115 | 8208.9 | 8210.7 | 1.8
GEN-2018-060 | 02 - Nebraska | 530581 | N HAYS3 | 115 | 10002.3 | 10005 | 2.7
GEN-2018-060 | 02 - Nebraska | 530582 | S HAYS6 | 230 | 9783.1 | 9788.3 | 5.2
GEN-2018-060 | 02 - Nebraska | 530583 | POSTROCK7 | 345 | 8336.5 | 8351.3 | 14.8
GEN-2018-060 | 02 - Nebraska | 530584 | POSTROCK6 | 230 | 12085.5 | 12097 | 11.5
GEN-2018-060 | 02 - Nebraska | 530590 | BEMIS 3 | 115 | 4066.7 | 4067.1 | 0.4
GEN-2018-060 | 02 - Nebraska | 530592 | SMOKYHL6 | 230 | 7022.7 | 7023.3 | 0.6
GEN-2018-060 | 02 - Nebraska | 530593 | SMKYP1 6 | 230 | 6138.7 | 6139.1 | 0.4
GEN-2018-060 | 02 - Nebraska | 530599 | SMKYP2 6 | 230 | 6500.6 | 6501.1 | 0.5
GEN-2018-060 | 02 - Nebraska | 530605 | REDLIN 3 | 115 | 3916.6 | 3916.9 | 0.3
GEN-2018-060 | 02 - Nebraska | 530610 | SHAYS_230 | 230 | 4414 | 4414.6 | 0.6
GEN-2018-060 | 02 - Nebraska | 530676 | GMEC 3 | 115 | 10577.2 | 10580.2 | 3
GEN-2018-060 | 02 - Nebraska | 530677 | OGALATP3 | 115 | 2686.7 | 2686.9 | 0.2
GEN-2018-060 | 02 - Nebraska | 530680 | HEIZER 6 | 230 | 8400.2 | 8402 | 1.8
GEN-2018-060 | 02 - Nebraska | 530684 | RUSLPMP3 | 115 | 2125.4 | 2125.6 | 0.2
GEN-2018-060 | 02 - Nebraska | 530694 | VINE2 3 | 115 | 8305.3 | 8307.2 | 1.9
GEN-2018-060 | 02 - Nebraska | 530695 | CHETOLAH3 | 115 | 8995.5 | 8997.7 | 2.2
GEN-2018-060 | 02 - Nebraska | 530702 | BUCKEYE_230 | 230 | 9067.7 | 9073.5 | 5.8
GEN-2018-060 | 02 - Nebraska | 530714 | ANGUS 3 | 115 | 5531.6 | 5532.4 | 0.8
GEN-2018-060 | 02 - Nebraska | 530720 | KNOLL S 6 | 230 | 11972 | 11983.2 | 11.2
GEN-2018-060 | 02 - Nebraska | 530721 | VINEDE_N | 115 | 8305.3 | 8307.2 | 1.9
GEN-2018-060 | 02 - Nebraska | 530722 | VINEDE_S | 115 | 8305.3 | 8307.2 | 1.9
GEN-2018-060 | 02 - Nebraska | 530725 | PFEIFER 3 | 115 | 3606 | 3606.3 | 0.3
GEN-2018-060 | 02 - Nebraska | 531448 | HOLCOMB3 | 115 | 21217.4 | 21217.9 | 0.5
GEN-2018-060 | 02 - Nebraska | 531449 | HOLCOMB7 | 345 | 9825.1 | 9825.8 | 0.7
GEN-2018-060 | 02 - Nebraska | 531451 | MINGO 7 | 345 | 6402.3 | 6402.7 | 0.4
GEN-2018-060 | 02 - Nebraska | 531465 | SETAB 7 | 345 | 7063.2 | 7063.7 | 0.5
GEN-2018-060 | 02 - Nebraska | 531469 | SPERVIL7 | 345 | 12884.3 | 12888.3 | 4
GEN-2018-060 | 02 - Nebraska | 531492 | OG ONEOK | 115 | 2184.5 | 2184.7 | 0.2
GEN-2018-060 | 02 - Nebraska | 531497 | TURKEYR3 | 115 | 1825.6 | 1825.7 | 0.1
GEN-2018-060 | 02 - Nebraska | 531501 | BUCKNER7 | 345 | 9516.8 | 9518 | 1.2
GEN-2018-060 | 02 - Nebraska | 531502 | CIMRRN 7 | 345 | 7547.8 | 7548.6 | 0.8
GEN-2018-060 | 02 - Nebraska | 531504 | CIMWD2 7 | 345 | 7837.3 | 7838.1 | 0.8
GEN-2018-060 | 02 - Nebraska | 531632 | GEN-2015-065 | 345 | 5729.5 | 5729.8 | 0.3
GEN-2018-060 | 02 - Nebraska | 532782 | BUFFALO7 | 345 | 19961 | 19961.4 | 0.4
GEN-2018-060 | 02 - Nebraska | 532783 | KINGMAN7 | 345 | 7141.3 | 7141.4 | 0.1
GEN-2018-060 | 02 - Nebraska | 532784 | NINN1WF7 | 345 | 5983.5 | 5983.5 | 0
GEN-2018-060 | 02 - Nebraska | 532785 | PRATTWF7 | 345 | 4984.5 | 4984.5 | 0
GEN-2018-060 | 02 - Nebraska | 532871 | CIRCLE 6 | 230 | 8885.9 | 8886.2 | 0.3
GEN-2018-060 | 02 - Nebraska | 532873 | SUMMIT 6 | 230 | 13302.2 | 13302.6 | 0.4
GEN-2018-060 | 02 - Nebraska | 539117 | SPRVILL-EHVB | 230 | 12077.9 | 12080.1 | 2.2
GEN-2018-060 | 02 - Nebraska | 539628 | NW-DGTP3 | 115 | 3526.4 | 3526.4 | 0
GEN-2018-060 | 02 - Nebraska | 539641 | NW-DODG3 | 115 | 3639.4 | 3639.5 | 0.1
GEN-2018-060 | 02 - Nebraska | 539645 | DCBEEF3 | 115 | 6850 | 6850.2 | 0.2
GEN-2018-060 | 02 - Nebraska | 539661 | 24-FREY3 | 115 | 5477.6 | 5477.9 | 0.3
GEN-2018-060 | 02 - Nebraska | 539667 | HAGGARD3 | 115 | 2434.7 | 2434.7 | 0
GEN-2018-060 | 02 - Nebraska | 539671 | FTDODGE3 | 115 | 9342.3 | 9342.8 | 0.5
GEN-2018-060 | 02 - Nebraska | 539678 | GRTBEND3 | 115 | 11517.6 | 11518.9 | 1.3
GEN-2018-060 | 02 - Nebraska | 539679 | GRTBEND6 | 230 | 8452.6 | 8454.3 | 1.7
GEN-2018-060 | 02 - Nebraska | 539680 | N-DODGE3 | 115 | 4659.1 | 4659.2 | 0.1
GEN-2018-060 | 02 - Nebraska | 539681 | N-GBEND3 | 115 | 7859.9 | 7860.6 | 0.7
GEN-2018-060 | 02 - Nebraska | 539684 | OTISSUB3 | 115 | 2984.8 | 2984.9 | 0.1
GEN-2018-060 | 02 - Nebraska | 539688 | S-DODGE3 | 115 | 6676.9 | 6677.1 | 0.2
GEN-2018-060 | 02 - Nebraska | 539689 | 2ND-KS 3 | 115 | 4953.2 | 4953.5 | 0.3
GEN-2018-060 | 02 - Nebraska | 539694 | SPEARVL3 | 115 | 10005.3 | 10005.9 | 0.6
GEN-2018-060 | 02 - Nebraska | 539695 | SPEARVL6 | 230 | 12358.4 | 12360.7 | 2.3
GEN-2018-060 | 02 - Nebraska | 539699 | W-DODGE3 | 115 | 4310.6 | 4310.7 | 0.1
GEN-2018-060 | 02 - Nebraska | 539740 | EDODGE 3 | 115 | 6274.9 | 6275.1 | 0.2
GEN-2018-060 | 02 - Nebraska | 539758 | FORD 3 | 115 | 5260.6 | 5260.7 | 0.1
GEN-2018-060 | 02 - Nebraska | 539759 | SPRVL 3 | 115 | 12909.1 | 12910.2 | 1.1
GEN-2018-060 | 02 - Nebraska | 539771 | NFTDODG3 | 115 | 9395.2 | 9395.6 | 0.4
GEN-2018-060 | 02 - Nebraska | 539778 | GYCOTAP3 | 115 | 2434.7 | 2434.7 | 0
GEN-2018-060 | 02 - Nebraska | 539779 | GRAY CO3 | 115 | 2434.7 | 2434.7 | 0
GEN-2018-060 | 02 - Nebraska | 539800 | CLARKCOUNTY7 | 345 | 12845.6 | 12847.8 | 2.2
GEN-2018-060 | 02 - Nebraska | 539801 | THISTLE7 | 345 | 16386.7 | 16387.5 | 0.8
GEN-2018-060 | 02 - Nebraska | 539803 | IRONWOOD7 | 345 | 12372.5 | 12376.1 | 3.6
GEN-2018-060 | 02 - Nebraska | 539804 | THISTLE4 | 138 | 17924 | 17924.4 | 0.4
GEN-2018-060 | 02 - Nebraska | 539813 | TRANSFORMER | 345 | 10812.4 | 10814 | 1.6
GEN-2018-060 | 02 - Nebraska | 539815 | IRONWOOD WF7 | 345 | 11209.7 | 11212.6 | 2.9
GEN-2018-060 | 02 - Nebraska | 539840 | GEN-2011-008 | 345 | 11018.6 | 11020.1 | 1.5
GEN-2018-060 | 02 - Nebraska | 539841 | G-2011-008-1 | 345 | 11018.6 | 11020.1 | 1.5
GEN-2018-060 | 02 - Nebraska | 539855 | G-2011-008-2 | 345 | 9375.9 | 9377 | 1.1
GEN-2018-060 | 02 - Nebraska | 539857 | G-2011-008-3 | 345 | 8645.1 | 8646 | 0.9
GEN-2018-060 | 02 - Nebraska | 539944 | LOCHS | 115 | 3261.3 | 3261.4 | 0.1
GEN-2018-060 | 02 - Nebraska | 560080 | G16-046-TAP | 345 | 11263.6 | 11265.7 | 2.1
GEN-2018-060 | 02 - Nebraska | 560082 | G16-050-TAP | 345 | 7467.2 | 7553.7 | 86.5
GEN-2018-060 | 02 - Nebraska | 579480 | GEN-2008-124 | 345 | 11966.7 | 11970.1 | 3.4
GEN-2018-060 | 02 - Nebraska | 584650 | GEN-2015-023 | 345 | 8124.4 | 8125.2 | 0.8
GEN-2018-060 | 02 - Nebraska | 585241 | GEN-2015-088 | 345 | 12236.1 | 12240.9 | 4.8
GEN-2018-060 | 02 - Nebraska | 587310 | GEN-2016-046 | 345 | 9939.4 | 9941 | 1.6
GEN-2018-060 | 02 - Nebraska | 587311 | G16-046XFMR1 | 115 | 15182.4 | 15183.4 | 1
GEN-2018-060 | 02 - Nebraska | 587350 | GEN-2016-050 | 345 | 6291.1 | 6381.2 | 90.1
GEN-2018-060 | 02 - Nebraska | 587500 | GEN-2016-073 | 345 | 14796.1 | 14796.3 | 0.2
GEN-2018-060 | 02 - Nebraska | 587680 | GEN-2016-074 | 345 | 6704 | 6709.8 | 5.8
GEN-2018-060 | 02 - Nebraska | 588630 | GEN-2017-018 | 345 | 16386.7 | 16387.5 | 0.8
GEN-2018-060 | 02 - Nebraska | 599950 | LAMAR7 | 345 | 4181.7 | 4181.8 | 0.1
GEN-2018-060 | 02 - Nebraska | 640065 | AXTELL 3 | 345 | 9901.8 | 9956.8 | 55
GEN-2018-060 | 02 - Nebraska | 640066 | AXTELL 7 | 115 | 14905.8 | 14928.4 | 22.6
GEN-2018-060 | 02 - Nebraska | 640103 | CANADAY7 | 115 | 14364.5 | 14367.2 | 2.7
GEN-2018-060 | 02 - Nebraska | 640131 | COLMB.W4 | 230 | 10470.4 | 10470.8 | 0.4
GEN-2018-060 | 02 - Nebraska | 640161 | ELMCRK_7 | 115 | 6225.2 | 6226.4 | 1.2
GEN-2018-060 | 02 - Nebraska | 640162 | ELMCRK 8 | 69 | 3875 | 3875.3 | 0.3
GEN-2018-060 | 02 - Nebraska | 640183 | GENTLMN3 | 345 | 16308.9 | 16314.5 | 5.6
GEN-2018-060 | 02 - Nebraska | 640184 | GENTLMN4 | 230 | 19798.7 | 19802.2 | 3.5
GEN-2018-060 | 02 - Nebraska | 640194 | GOSPER 7 | 115 | 4533.6 | 4533.8 | 0.2
GEN-2018-060 | 02 - Nebraska | 640200 | GR ISLD4 | 230 | 17492.9 | 17500 | 7.1
GEN-2018-060 | 02 - Nebraska | 640201 | GR ISLD7 | 115 | 23980.8 | 23986.7 | 5.9
GEN-2018-060 | 02 - Nebraska | 640206 | GUIDE R7 | 115 | 4382.8 | 4383.3 | 0.5
GEN-2018-060 | 02 - Nebraska | 640207 | GUIDE R8 | 69 | 2246.7 | 2246.7 | 0
GEN-2018-060 | 02 - Nebraska | 640214 | HASTING4 | 230 | 7635.8 | 7637.4 | 1.6
GEN-2018-060 | 02 - Nebraska | 640215 | HASTING7 | 115 | 20014 | 20021.1 | 7.1
GEN-2018-060 | 02 - Nebraska | 640222 | HILDRTH7 | 115 | 4399.7 | 4400.6 | 0.9
GEN-2018-060 | 02 - Nebraska | 640223 | HILDRTH8 | 69 | 3554.9 | 3555.3 | 0.4
GEN-2018-060 | 02 - Nebraska | 640224 | HOLDREG7 | 115 | 6324 | 6326.2 | 2.2
GEN-2018-060 | 02 - Nebraska | 640242 | JOHN.2 7 | 115 | 13112.1 | 13114.4 | 2.3
GEN-2018-060 | 02 - Nebraska | 640244 | JOHN.LK7 | 115 | 9047.7 | 9048.7 | 1
GEN-2018-060 | 02 - Nebraska | 640245 | JOHN.LK8 | 69 | 4301.2 | 4301.3 | 0.1
GEN-2018-060 | 02 - Nebraska | 640248 | KEAR.NE7 | 115 | 9817.2 | 9820.9 | 3.7
GEN-2018-060 | 02 - Nebraska | 640250 | KEARNEY7 | 115 | 12473 | 12480.5 | 7.5
GEN-2018-060 | 02 - Nebraska | 640252 | KEYSTON3 | 345 | 8819.1 | 8820.3 | 1.2
GEN-2018-060 | 02 - Nebraska | 640253 | KEYSTON7 | 115 | 14836.6 | 14837.6 | 1
GEN-2018-060 | 02 - Nebraska | 640255 | KINGSLY7 | 115 | 9262.5 | 9262.8 | 0.3
GEN-2018-060 | 02 - Nebraska | 640261 | LOWELL 7 | 115 | 8470.5 | 8474.3 | 3.8
GEN-2018-060 | 02 - Nebraska | 640262 | LOWELL 8 | 69 | 4219.8 | 4220.3 | 0.5
GEN-2018-060 | 02 - Nebraska | 640271 | MCCOOL 3 | 345 | 11468.3 | 11471 | 2.7
GEN-2018-060 | 02 - Nebraska | 640272 | MCCOOL 7 | 115 | 14770.2 | 14771.6 | 1.4
GEN-2018-060 | 02 - Nebraska | 640273 | MCCOOL 8 | 69 | 5735.3 | 5735.4 | 0.1
GEN-2018-060 | 02 - Nebraska | 640275 | MINDEN 7 | 115 | 7476.3 | 7480.5 | 4.2
GEN-2018-060 | 02 - Nebraska | 640277 | MOORE 3 | 345 | 23972.2 | 23977.3 | 5.1
GEN-2018-060 | 02 - Nebraska | 640278 | SHELDON7 | 115 | 45508.2 | 45511.8 | 3.6
GEN-2018-060 | 02 - Nebraska | 640286 | N.PLATT4 | 230 | 13506.5 | 13508.4 | 1.9
GEN-2018-060 | 02 - Nebraska | 640302 | OGALALA4 | 230 | 7905.2 | 7905.7 | 0.5
GEN-2018-060 | 02 - Nebraska | 640310 | ORLEANS7 | 115 | 2467.7 | 2468 | 0.3
GEN-2018-060 | 02 - Nebraska | 640311 | ORLEANS8 | 69 | 2470 | 2470.2 | 0.2
GEN-2018-060 | 02 - Nebraska | 640312 | PAULINE3 | 345 | 8363.5 | 8378.1 | 14.6
GEN-2018-060 | 02 - Nebraska | 640313 | PAULINE7 | 115 | 16931.3 | 16942.6 | 11.3
GEN-2018-060 | 02 - Nebraska | 640314 | PAULINE8 | 69 | 4942.8 | 4943.4 | 0.6
GEN-2018-060 | 02 - Nebraska | 640321 | PROSSER7 | 115 | 6995.9 | 6997.5 | 1.6
GEN-2018-060 | 02 - Nebraska | 640322 | PROSSER8 | 69 | 3898.2 | 3898.5 | 0.3
GEN-2018-060 | 02 - Nebraska | 640325 | REDWILO3 | 345 | 6540.8 | 6541.4 | 0.6
GEN-2018-060 | 02 - Nebraska | 640326 | REDWILO7 | 115 | 11739.3 | 11739.9 | 0.6
GEN-2018-060 | 02 - Nebraska | 640330 | RIVERDL4 | 230 | 7600.4 | 7602.5 | 2.1
GEN-2018-060 | 02 - Nebraska | 640331 | RIVERDL7 | 115 | 13416.2 | 13420.7 | 4.5
GEN-2018-060 | 02 - Nebraska | 640332 | RIVERDL8 | 69 | 6719.7 | 6720.3 | 0.6
GEN-2018-060 | 02 - Nebraska | 640374 | SWEET W3 | 345 | 11235 | 11253.2 | 18.2
GEN-2018-060 | 02 - Nebraska | 640381 | THEDFRD7 | 115 | 9072.5 | 9072.8 | 0.3
GEN-2018-060 | 02 - Nebraska | 640383 | TOWER 7 | 115 | 9435.9 | 9439.4 | 3.5
GEN-2018-060 | 02 - Nebraska | 640407 | WESTMIN7 | 115 | 8229.5 | 8230.3 | 0.8
GEN-2018-060 | 02 - Nebraska | 640448 | HOLDREGE 8 | 69 | 3837.4 | 3837.9 | 0.5
GEN-2018-060 | 02 - Nebraska | 640500 | THEDFRD3 | 345 | 5282.9 | 5283.4 | 0.5
GEN-2018-060 | 02 - Nebraska | 640510 | HOLT.CO3 | 345 | 8189.9 | 8190.7 | 0.8
GEN-2018-060 | 02 - Nebraska | 640525 | TOBIAS 3 | 345 | 12236.1 | 12240.9 | 4.8
GEN-2018-060 | 02 - Nebraska | 640583 | ROSEMONT 7 | 115 | 6788.2 | 6789.6 | 1.4
GEN-2018-060 | 02 - Nebraska | 640584 | COTTONWD 7 | 115 | 5482 | 5482.8 | 0.8
GEN-2018-060 | 02 - Nebraska | 640590 | MONOLITH 3 | 345 | 23456.3 | 23461.1 | 4.8
GEN-2018-060 | 02 - Nebraska | 641087 | EGYCNTR7 | 115 | 18734 | 18739.2 | 5.2
GEN-2018-060 | 02 - Nebraska | 641088 | HASTCTY7 | 115 | 20014 | 20021.1 | 7.1
GEN-2018-060 | 02 - Nebraska | 650114 | NW68HOLDRG3 | 345 | 17852.9 | 17854.7 | 1.8
GEN-2018-060 | 02 - Nebraska | 650189 | 103&ROKEBY3 | 345 | 21292.9 | 21295.1 | 2.2
GEN-2018-060 | 02 - Nebraska | 653571 | GR ISLD3 | 345 | 13057.8 | 13064.2 | 6.4
GEN-2018-060 | 02 - Nebraska | 653871 | GR ISLD-LNX3 | 345 | 12926.6 | 12932.9 | 6.3
GEN-2018-060 | 02 - Nebraska | 659425 | SD.LS-KS-MB3 | 345 | 5977.6 | 5977.9 | 0.3
GEN-2018-060 | 02 - Nebraska | 760284 | GEN-2017-220 | 345 | 19854.4 | 19854.8 | 0.4
GEN-2018-060 | 02 - Nebraska | 760767 | GEN-2017-144 | 345 | 7849.1 | 7849.8 | 0.7
GEN-2018-060 | 02 - Nebraska | 761208 | GEN-2017-210 | 345 | 10027.1 | 10029.1 | 2
GEN-2018-060 | 02 - Nebraska | 761292 | GEN-2017-181 | 345 | 6877.3 | 6878.7 | 1.4
GEN-2018-060 | 02 - Nebraska | 761313 | GEN-2017-182 | 345 | 5748.5 | 5749.4 | 0.9
GEN-2018-060 | 02 - Nebraska | 762658 | GEN-2018-030 | 345 | 5327.1 | 5327.4 | 0.3
GEN-2018-060 | 02 - Nebraska | 762662 | G18-030-TAP | 345 | 5975.9 | 5976.2 | 0.3
GEN-2018-060 | 02 - Nebraska | 762834 | GEN-2018-049 | 345 | 7110.8 | 7110.9 | 0.1
ASGI-2018-003 | 03 - Central | 300070 | 5CLARK | 161 | 8271.3 | 8292.1 | 20.8
ASGI-2018-003 | 03 - Central | 300071 | 5CLINTN | 161 | 16251.7 | 16312.1 | 60.4
ASGI-2018-003 | 03 - Central | 300118 | 5STKAEC | 161 | 9312.3 | 9320.7 | 8.4
ASGI-2018-003 | 03 - Central | 300645 | 2BRONA | 69 | 2257.7 | 2258 | 0.3
ASGI-2018-003 | 03 - Central | 300651 | 2LAMR | 69 | 10159.4 | 10162.5 | 3.1
ASGI-2018-003 | 03 - Central | 300652 | 2LAMRCTS | 69 | 3949.8 | 3950.3 | 0.5
ASGI-2018-003 | 03 - Central | 300654 | 2MILO | 69 | 5469 | 5470.9 | 1.9
ASGI-2018-003 | 03 - Central | 300685 | 2LAMARPT | 69 | 8574.7 | 8576.9 | 2.2
ASGI-2018-003 | 03 - Central | 300689 | 2BUTLER | 69 | 6071.3 | 6074.7 | 3.4
ASGI-2018-003 | 03 - Central | 300690 | 2BUTLERE | 69 | 4852.1 | 4854.2 | 2.1
ASGI-2018-003 | 03 - Central | 300697 | 2CRESTH | 69 | 3285.5 | 3286.3 | 0.8
ASGI-2018-003 | 03 - Central | 300707 | 2PL GAP | 69 | 4345.7 | 4347.3 | 1.6
ASGI-2018-003 | 03 - Central | 300793 | 5HYDERHL | 161 | 8641.3 | 8650 | 8.7
ASGI-2018-003 | 03 - Central | 300794 | 5LAMAR | 161 | 8965.8 | 8973.2 | 7.4
ASGI-2018-003 | 03 - Central | 300798 | 2HYDERHL | 69 | 8572.7 | 8575.8 | 3.1
ASGI-2018-003 | 03 - Central | 300802 | 2CLARK | 69 | 6726.4 | 6729.9 | 3.5
ASGI-2018-003 | 03 - Central | 300814 | 2WALKER | 69 | 5220.3 | 5222.1 | 1.8
ASGI-2018-003 | 03 - Central | 300950 | 5JASPER | 161 | 13108.5 | 13113.3 | 4.8
ASGI-2018-003 | 03 - Central | 301342 | 5BUTLER | 161 | 7131.1 | 7145 | 13.9
ASGI-2018-003 | 03 - Central | 503507 | 2BUTLEREGEN | 69 | 4849.5 | 4851.6 | 2.1
ASGI-2018-003 | 03 - Central | 541138 | CLNTPLT_CAP2 | 69 | 8721.5 | 8862 | 140.5
ASGI-2018-003 | 03 - Central | 541207 | ARCHIE 5 | 161 | 19647.4 | 19673.9 | 26.5
ASGI-2018-003 | 03 - Central | 541208 | NEVADA 5 | 161 | 6435.9 | 6469.5 | 33.6
ASGI-2018-003 | 03 - Central | 541240 | ADRIAN 5 | 161 | 8992.1 | 9005.2 | 13.1
ASGI-2018-003 | 03 - Central | 541242 | CLINTON5 | 161 | 16177.7 | 16238.1 | 60.4
ASGI-2018-003 | 03 - Central | 541268 | WBURGP 2 | 69 | 7016.9 | 7022.7 | 5.8
ASGI-2018-003 | 03 - Central | 541269 | WBURGE 2 | 69 | 6866.7 | 6870.6 | 3.9
ASGI-2018-003 | 03 - Central | 541300 | POSTOAK2 | 69 | 4417.2 | 4430.5 | 13.3
ASGI-2018-003 | 03 - Central | 541301 | CLNTPLT2 | 69 | 8914.2 | 9061 | 146.8
ASGI-2018-003 | 03 - Central | 541302 | CLNTGRN2 | 69 | 8637.6 | 8758.9 | 121.3
ASGI-2018-003 | 03 - Central | 541303 | CLNTN N2 | 69 | 8423 | 8516.5 | 93.5
ASGI-2018-003 | 03 - Central | 541304 | URICHTP2 | 69 | 3260.4 | 3498 | 237.6
ASGI-2018-003 | 03 - Central | 541305 | URICH 2 | 69 | 2329.9 | 2449.3 | 119.4
ASGI-2018-003 | 03 - Central | 541306 | APCITY 2 | 69 | 2566.5 | 3039.3 | 472.8
ASGI-2018-003 | 03 - Central | 541307 | NEVPLT 2 | 69 | 5571.7 | 5682.5 | 110.8
ASGI-2018-003 | 03 - Central | 541308 | NEVADA 2 | 69 | 6027.7 | 6157.3 | 129.6
ASGI-2018-003 | 03 - Central | 541309 | METZ 2 | 69 | 4553.3 | 4622.8 | 69.5
ASGI-2018-003 | 03 - Central | 541310 | 3M 2 | 69 | 4035.3 | 4089.8 | 54.5
ASGI-2018-003 | 03 - Central | 541311 | NEVJCT 2 | 69 | 4236.4 | 4300.5 | 64.1
ASGI-2018-003 | 03 - Central | 541312 | LAMAR 2 | 69 | 1101.2 | 1105.1 | 3.9
ASGI-2018-003 | 03 - Central | 541320 | CLNTN S2 | 69 | 8696.4 | 8817.4 | 121
ASGI-2018-003 | 03 - Central | 541383 | FAYETVLTP2 | 69 | 5005.2 | 5006.9 | 1.7
ASGI-2018-003 | 03 - Central | 541385 | CNTRVIEW2 | 69 | 5192.1 | 5194.8 | 2.7
ASGI-2018-003 | 03 - Central | 541499 | SHELDON_69 | 69 | 1768.8 | 1779.3 | 10.5
ASGI-2018-003 | 03 - Central | 762361 | ASGI-2018-00 | 69 | Project Bus - Disconnected | 3039.2 | Project Bus - Disconnected
ASGI-2018-003 | 03 - Central | 762372 | ASGI-2018-00 | 69 | 4550.4 | 4619.8 | 69.4
ASGI-2018-006 | 03 - Central | 300070 | 5CLARK | 161 | 8228.4 | 8292.1 | 63.7
ASGI-2018-006 | 03 - Central | 300118 | 5STKAEC | 161 | 9304.3 | 9320.7 | 16.4
ASGI-2018-006 | 03 - Central | 300645 | 2BRONA | 69 | 2257.1 | 2258 | 0.9
ASGI-2018-006 | 03 - Central | 300651 | 2LAMR | 69 | 10153.7 | 10162.5 | 8.8
ASGI-2018-006 | 03 - Central | 300652 | 2LAMRCTS | 69 | 3949 | 3950.3 | 1.3
ASGI-2018-006 | 03 - Central | 300654 | 2MILO | 69 | 5465.6 | 5470.9 | 5.3
ASGI-2018-006 | 03 - Central | 300685 | 2LAMARPT | 69 | 8570.6 | 8576.9 | 6.3
ASGI-2018-006 | 03 - Central | 300689 | 2BUTLER | 69 | 6068.2 | 6074.7 | 6.5
ASGI-2018-006 | 03 - Central | 300690 | 2BUTLERE | 69 | 4850.4 | 4854.2 | 3.8
ASGI-2018-006 | 03 - Central | 300697 | 2CRESTH | 69 | 3284.9 | 3286.3 | 1.4
ASGI-2018-006 | 03 - Central | 300707 | 2PL GAP | 69 | 4344 | 4347.3 | 3.3
ASGI-2018-006 | 03 - Central | 300793 | 5HYDERHL | 161 | 8631.4 | 8650 | 18.6
ASGI-2018-006 | 03 - Central | 300794 | 5LAMAR | 161 | 8951.4 | 8973.2 | 21.8
ASGI-2018-006 | 03 - Central | 300798 | 2HYDERHL | 69 | 8569.9 | 8575.8 | 5.9
ASGI-2018-006 | 03 - Central | 300802 | 2CLARK | 69 | 6720.3 | 6729.9 | 9.6
ASGI-2018-006 | 03 - Central | 300814 | 2WALKER | 69 | 5217.8 | 5222.1 | 4.3
ASGI-2018-006 | 03 - Central | 300950 | 5JASPER | 161 | 13100 | 13113.3 | 13.3
ASGI-2018-006 | 03 - Central | 301342 | 5BUTLER | 161 | 7110.9 | 7145 | 34.1
ASGI-2018-006 | 03 - Central | 503507 | 2BUTLEREGEN | 69 | 4847.8 | 4851.6 | 3.8
ASGI-2018-006 | 03 - Central | 541138 | CLNTPLT_CAP2 | 69 | 8852.7 | 8862 | 9.3
ASGI-2018-006 | 03 - Central | 541207 | ARCHIE 5 | 161 | 19648.6 | 19673.9 | 25.3
ASGI-2018-006 | 03 - Central | 541208 | NEVADA 5 | 161 | 6356.7 | 6469.5 | 112.8
ASGI-2018-006 | 03 - Central | 541240 | ADRIAN 5 | 161 | 8980 | 9005.2 | 25.2
ASGI-2018-006 | 03 - Central | 541300 | POSTOAK2 | 69 | 4429.6 | 4430.5 | 0.9
ASGI-2018-006 | 03 - Central | 541301 | CLNTPLT2 | 69 | 9051.2 | 9061 | 9.8
ASGI-2018-006 | 03 - Central | 541302 | CLNTGRN2 | 69 | 8750.5 | 8758.9 | 8.4
ASGI-2018-006 | 03 - Central | 541304 | URICHTP2 | 69 | 3485.5 | 3498 | 12.5
ASGI-2018-006 | 03 - Central | 541305 | URICH 2 | 69 | 2443.3 | 2449.3 | 6
ASGI-2018-006 | 03 - Central | 541306 | APCITY 2 | 69 | 3011.1 | 3039.3 | 28.2
ASGI-2018-006 | 03 - Central | 541307 | NEVPLT 2 | 69 | 5268.3 | 5682.5 | 414.2
ASGI-2018-006 | 03 - Central | 541308 | NEVADA 2 | 69 | 5674.4 | 6157.3 | 482.9
ASGI-2018-006 | 03 - Central | 541309 | METZ 2 | 69 | 4128.4 | 4622.8 | 494.4
ASGI-2018-006 | 03 - Central | 541310 | 3M 2 | 69 | 3696.5 | 4089.8 | 393.3
ASGI-2018-006 | 03 - Central | 541311 | NEVJCT 2 | 69 | 4059 | 4300.5 | 241.5
ASGI-2018-006 | 03 - Central | 541312 | LAMAR 2 | 69 | 1090.1 | 1105.1 | 15
ASGI-2018-006 | 03 - Central | 541320 | CLNTN S2 | 69 | 8809.1 | 8817.4 | 8.3
ASGI-2018-006 | 03 - Central | 541499 | SHELDON_69 | 69 | 1739.4 | 1779.3 | 39.9
ASGI-2018-006 | 03 - Central | 762361 | ASGI-2018-00 | 69 | 3011 | 3039.2 | 28.2
ASGI-2018-006 | 03 - Central | 762372 | ASGI-2018-00 | 69 | Project Bus - Disconnected | 4619.8 | Project Bus - Disconnected
ASGI-2018-007 | 03 - Central | 41453 | J1145 SUB | 345 | 20562.2 | 20570.2 | 8
ASGI-2018-007 | 03 - Central | 44882 | J1488_INV | 345 | 19528.7 | 19535.8 | 7.1
ASGI-2018-007 | 03 - Central | 44887 | J1490_INV | 345 | 19628.4 | 19635.6 | 7.2
ASGI-2018-007 | 03 - Central | 44888 | J1490_POI | 345 | 20562.2 | 20570.2 | 8
ASGI-2018-007 | 03 - Central | 300043 | 7KINGDM | 345 | 16619.3 | 16626.4 | 7.1
ASGI-2018-007 | 03 - Central | 300044 | 7MCCRED | 345 | 19772.2 | 19782 | 9.8
ASGI-2018-007 | 03 - Central | 300049 | 7THOMHL | 345 | 15049.9 | 15078 | 28.1
ASGI-2018-007 | 03 - Central | 300066 | 5HIGBEEB1 | 161 | 12848.2 | 12874.1 | 25.9
ASGI-2018-007 | 03 - Central | 300082 | 5GEORGE | 161 | 8296.7 | 8305.5 | 8.8
ASGI-2018-007 | 03 - Central | 300098 | 5MOCITYB2 | 161 | 19556.9 | 19561.6 | 4.7
ASGI-2018-007 | 03 - Central | 300105 | 5NORTON | 161 | 6699.7 | 6727.5 | 27.8
ASGI-2018-007 | 03 - Central | 300120 | 5THMHILB1 | 161 | 31518.2 | 31625.8 | 107.6
ASGI-2018-007 | 03 - Central | 300126 | 5MOBTAP | 161 | 15895 | 15957.7 | 62.7
ASGI-2018-007 | 03 - Central | 300132 | 5THMHLB2 | 161 | 31656.6 | 31765.2 | 108.6
ASGI-2018-007 | 03 - Central | 300133 | 5THMHLB3 | 161 | 31561.3 | 31668.7 | 107.4
ASGI-2018-007 | 03 - Central | 300172 | 2TMHILL | 69 | 23540.6 | 23563 | 22.4
ASGI-2018-007 | 03 - Central | 300201 | 2INGROV | 69 | 3004.6 | 3004.9 | 0.3
ASGI-2018-007 | 03 - Central | 300207 | 5MEADVLB1 | 161 | 5131.8 | 5133 | 1.2
ASGI-2018-007 | 03 - Central | 300381 | 5BEVIER | 161 | 7913.8 | 7919.6 | 5.8
ASGI-2018-007 | 03 - Central | 300387 | 2BEVIER | 69 | 10048.9 | 10051.8 | 2.9
ASGI-2018-007 | 03 - Central | 300389 | 2BYNUMV | 69 | 5414.8 | 5415.7 | 0.9
ASGI-2018-007 | 03 - Central | 300405 | 2MCNPLT | 69 | 7118.9 | 7120.2 | 1.3
ASGI-2018-007 | 03 - Central | 300499 | 5HINTON | 161 | 9230.8 | 9236.9 | 6.1
ASGI-2018-007 | 03 - Central | 300500 | 5HUNTSDL | 161 | 10864.3 | 10867.6 | 3.3
ASGI-2018-007 | 03 - Central | 300505 | 2STURGN | 69 | 7381.1 | 7382.4 | 1.3
ASGI-2018-007 | 03 - Central | 300508 | 5STURGN | 161 | 6691.3 | 6697.8 | 6.5
ASGI-2018-007 | 03 - Central | 300531 | 2GEORGE | 69 | 7898.9 | 7902.2 | 3.3
ASGI-2018-007 | 03 - Central | 300535 | 2MALTAB | 69 | 3003.4 | 3004.9 | 1.5
ASGI-2018-007 | 03 - Central | 300536 | 2MALTAJ | 69 | 4965 | 4968.9 | 3.9
ASGI-2018-007 | 03 - Central | 300537 | 2MARSHL | 69 | 3983.5 | 3985.5 | 2
ASGI-2018-007 | 03 - Central | 300538 | 2NAPTON | 69 | 3786.9 | 3788.8 | 1.9
ASGI-2018-007 | 03 - Central | 300540 | 2NORTON | 69 | 6122.3 | 6128.8 | 6.5
ASGI-2018-007 | 03 - Central | 300560 | 2PILOTG | 69 | 3042.9 | 3043.6 | 0.7
ASGI-2018-007 | 03 - Central | 300615 | 2YATES | 69 | 5272.4 | 5273.1 | 0.7
ASGI-2018-007 | 03 - Central | 300953 | 5HARRSBRG | 161 | 9313.9 | 9322.7 | 8.8
ASGI-2018-007 | 03 - Central | 301318 | 2THMINTP | 69 | 18949.1 | 18963.5 | 14.4
ASGI-2018-007 | 03 - Central | 301443 | 5THMHLB4 | 161 | 31281.4 | 31390.5 | 109.1
ASGI-2018-007 | 03 - Central | 301489 | 5MCBAINB2 | 161 | 14084.5 | 14088.9 | 4.4
ASGI-2018-007 | 03 - Central | 301494 | 5HIGBEEB2 | 161 | 12848.4 | 12874.3 | 25.9
ASGI-2018-007 | 03 - Central | 301503 | 7THOMHLGSU3 | 345 | 14937.4 | 14964.7 | 27.3
ASGI-2018-007 | 03 - Central | 301504 | 5THOMHLGSU1 | 161 | 30527.3 | 30626.9 | 99.6
ASGI-2018-007 | 03 - Central | 301505 | 5THOMHLGSU2 | 161 | 30499 | 30598.9 | 99.9
ASGI-2018-007 | 03 - Central | 301506 | 5THOMHLXF3 | 161 | 31044.8 | 31147.4 | 102.6
ASGI-2018-007 | 03 - Central | 301507 | 5THOMHLU3SU | 161 | 30007.4 | 30104.4 | 97
ASGI-2018-007 | 03 - Central | 301508 | 5THOMHLXF1 | 161 | 30227 | 30325.8 | 98.8
ASGI-2018-007 | 03 - Central | 301509 | 2THOMHLXF1 | 69 | 23255.1 | 23277.1 | 22
ASGI-2018-007 | 03 - Central | 301510 | 5THOMHLXF4 | 161 | 30975.7 | 31081.8 | 106.1
ASGI-2018-007 | 03 - Central | 301511 | 5THMHILTFERB | 161 | 31255.3 | 31361.1 | 105.8
ASGI-2018-007 | 03 - Central | 301562 | 5MEADVLB2 | 161 | 5131.5 | 5132.6 | 1.1
ASGI-2018-007 | 03 - Central | 301567 | 5NORTONTP | 161 | 6219.1 | 6238.8 | 19.7
ASGI-2018-007 | 03 - Central | 301623 | 2BEVIERTP | 69 | 10016.6 | 10019.5 | 2.9
ASGI-2018-007 | 03 - Central | 301624 | 2BEVIERLD | 69 | 9904 | 9906.9 | 2.9
ASGI-2018-007 | 03 - Central | 343004 | 5PERCHE | 161 | 9677.7 | 9680.3 | 2.6
ASGI-2018-007 | 03 - Central | 343005 | 2PERCHE | 69 | 15433.2 | 15435.6 | 2.4
ASGI-2018-007 | 03 - Central | 343052 | 2PERCHE2 | 69 | 15433.2 | 15435.6 | 2.4
ASGI-2018-007 | 03 - Central | 344001 | 5ADAIR2 | 161 | 15347 | 15348.5 | 1.5
ASGI-2018-007 | 03 - Central | 344004 | 5ADAIR1 | 161 | 15347 | 15348.5 | 1.5
ASGI-2018-007 | 03 - Central | 344041 | 5LOYMART 2 | 161 | 10833.4 | 10835.2 | 1.8
ASGI-2018-007 | 03 - Central | 344233 | 5CALIF UE 1 | 161 | 10829.1 | 10831 | 1.9
ASGI-2018-007 | 03 - Central | 344234 | 5CALIF UE 2 | 161 | 10829.1 | 10831 | 1.9
ASGI-2018-007 | 03 - Central | 344557 | 5MAURER 1 | 161 | 8265.4 | 8269.4 | 4
ASGI-2018-007 | 03 - Central | 344558 | 5MAURER 2 | 161 | 8265.4 | 8269.4 | 4
ASGI-2018-007 | 03 - Central | 345071 | 5MCBAIN T | 161 | 14664 | 14668.7 | 4.7
ASGI-2018-007 | 03 - Central | 345088 | 7MCCREDIE | 345 | 6977.3 | 6978.8 | 1.5
ASGI-2018-007 | 03 - Central | 345221 | 5MOBERLY | 161 | 15884.8 | 15947.5 | 62.7
ASGI-2018-007 | 03 - Central | 345222 | 2MOBERLY | 69 | 8034.1 | 8039.3 | 5.2
ASGI-2018-007 | 03 - Central | 345408 | 7OVERTON | 345 | 13503.2 | 13508.8 | 5.6
ASGI-2018-007 | 03 - Central | 345409 | 5OVERTON | 161 | 21611.7 | 21625.2 | 13.5
ASGI-2018-007 | 03 - Central | 345411 | 5OVERTON 2 | 161 | 21611.7 | 21625.2 | 13.5
ASGI-2018-007 | 03 - Central | 346005 | 2ADAIR 1 | 69 | 5610.6 | 5610.7 | 0.1
ASGI-2018-007 | 03 - Central | 346025 | 2BRKFLD | 69 | 1854.7 | 1854.8 | 0.1
ASGI-2018-007 | 03 - Central | 346048 | 2MAURER | 69 | 3301.1 | 3301.3 | 0.2
ASGI-2018-007 | 03 - Central | 346065 | 2HARRISON | 69 | 3210 | 3210 | 0
ASGI-2018-007 | 03 - Central | 346067 | 2HORNER | 69 | 6673.4 | 6677 | 3.6
ASGI-2018-007 | 03 - Central | 346096 | 2MACON_AM | 69 | 1618.1 | 1618.4 | 0.3
ASGI-2018-007 | 03 - Central | 346099 | 2MARCELIN | 69 | 1830.8 | 1830.9 | 0.1
ASGI-2018-007 | 03 - Central | 346117 | 2OVERTON | 69 | 3690.4 | 3690.6 | 0.2
ASGI-2018-007 | 03 - Central | 346142 | 2SINNOCK | 69 | 6308.8 | 6311.9 | 3.1
ASGI-2018-007 | 03 - Central | 346168 | 2RTE EE | 69 | 3761.7 | 3762.4 | 0.7
ASGI-2018-007 | 03 - Central | 346169 | 2DUPONT | 69 | 6967.6 | 6971.6 | 4
ASGI-2018-007 | 03 - Central | 346170 | 2ROTH TAP | 69 | 1842.8 | 1842.9 | 0.1
ASGI-2018-007 | 03 - Central | 346171 | 2SPRK TAP | 69 | 7183.5 | 7187.7 | 4.2
ASGI-2018-007 | 03 - Central | 541146 | SEDLIAW_CAP5 | 161 | 9205.2 | 9212.9 | 7.7
ASGI-2018-007 | 03 - Central | 541200 | PHILL 7 | 345 | 19307.2 | 19308.1 | 0.9
ASGI-2018-007 | 03 - Central | 541201 | SIBLEY 7 | 345 | 21898.8 | 21901 | 2.2
ASGI-2018-007 | 03 - Central | 541202 | SIBLEY 5 | 161 | 27672.2 | 27675.6 | 3.4
ASGI-2018-007 | 03 - Central | 541209 | SEDALIA5 | 161 | 9722.2 | 9730.8 | 8.6
ASGI-2018-007 | 03 - Central | 541241 | SEDEAST5 | 161 | 7697.9 | 7702.5 | 4.6
ASGI-2018-007 | 03 - Central | 541395 | NUCOR5 | 161 | 7221.3 | 7225.3 | 4
ASGI-2018-007 | 03 - Central | 541414 | SIB REA1 | 345 | 19477.8 | 19479.5 | 1.7
ASGI-2018-007 | 03 - Central | 541500 | KETCHEM7 | 345 | 9152.7 | 9152.9 | 0.2
ASGI-2018-007 | 03 - Central | 541501 | OSBORN7 | 345 | 8041 | 8041.1 | 0.1
ASGI-2018-007 | 03 - Central | 542972 | HAWTH 7 | 345 | 23867.5 | 23869.1 | 1.6
ASGI-2018-007 | 03 - Central | 543012 | SWAVCAP2 | 69 | 3874.3 | 3876 | 1.7
ASGI-2018-007 | 03 - Central | 543013 | SWAVCAP5 | 161 | 3427.5 | 3433.9 | 6.4
ASGI-2018-007 | 03 - Central | 543059 | MALTABN5 | 161 | 4115.5 | 4125.2 | 9.7
ASGI-2018-007 | 03 - Central | 543060 | CAROLTN5 | 161 | 4562.6 | 4575.9 | 13.3
ASGI-2018-007 | 03 - Central | 543061 | BRUNSWK5 | 161 | 5842.6 | 5877.7 | 35.1
ASGI-2018-007 | 03 - Central | 543062 | SALSBRY5 | 161 | 11974.6 | 12186.9 | 212.3
ASGI-2018-007 | 03 - Central | 543063 | SWAVRLY5 | 161 | 3496.8 | 3503.4 | 6.6
ASGI-2018-007 | 03 - Central | 543064 | NORTON 5 | 161 | 6722 | 6750.3 | 28.3
ASGI-2018-007 | 03 - Central | 543070 | WEST---5 | 161 | 4696.7 | 4710.6 | 13.9
ASGI-2018-007 | 03 - Central | 543071 | S EAST 5 | 161 | 4882.7 | 4897.6 | 14.9
ASGI-2018-007 | 03 - Central | 543072 | MRSHLJT5 | 161 | 5870 | 5891.7 | 21.7
ASGI-2018-007 | 03 - Central | 543073 | MIAMI_ 5 | 161 | 4765.9 | 4780.1 | 14.2
ASGI-2018-007 | 03 - Central | 543094 | SWAVRLY2 | 69 | 3876 | 3877.7 | 1.7
ASGI-2018-007 | 03 - Central | 543101 | DOVER2 | 69 | 3666.7 | 3667.9 | 1.2
ASGI-2018-007 | 03 - Central | 543658 | DOVER_TAP2 | 69 | 3859.1 | 3860.4 | 1.3
ASGI-2018-007 | 03 - Central | 709200 | GI92_POI | 161 | 10841.6 | 10857.6 | 16
ASGI-2018-007 | 03 - Central | 762383 | ASG-2018-007 | 161 | Project Bus - Disconnected | 12175.9 | Project Bus - Disconnected
ASGI-2018-007 | 03 - Central | 992001 | VSC2_1 | 276 | 5877.3 | 5878 | 0.7
ASGI-2018-007 | 03 - Central | 992002 | VSC2_2 | 276 | 5877.3 | 5878 | 0.7
ASGI-2018-007 | 03 - Central | 992003 | VSC2_3 | 345 | 7350.4 | 7351.7 | 1.3
ASGI-2018-007 | 03 - Central | 992005 | VSC2_5 | 276 | 5877.3 | 5878 | 0.7
ASGI-2018-007 | 03 - Central | 992006 | VSC2_6 | 276 | 5877.3 | 5878 | 0.7
ASGI-2018-007 | 03 - Central | 999950 | GI-86_SUB | 69 | 7510 | 7512.3 | 2.3
ASGI-2018-010 | 03 - Central | 532768 | EMPEC 7 | 345 | 20002.1 | 20003.1 | 1
ASGI-2018-010 | 03 - Central | 532769 | LANG 7 | 345 | 19735.1 | 19736.1 | 1
ASGI-2018-010 | 03 - Central | 532770 | MORRIS 7 | 345 | 13778.3 | 13778.6 | 0.3
ASGI-2018-010 | 03 - Central | 532772 | STRANGR7 | 345 | 28512.1 | 28517.3 | 5.2
ASGI-2018-010 | 03 - Central | 532774 | SWISVAL7 | 345 | 18593.6 | 18597.4 | 3.8
ASGI-2018-010 | 03 - Central | 532775 | 87TH 7 | 345 | 22938.8 | 22951.8 | 13
ASGI-2018-010 | 03 - Central | 532776 | READWF 7 | 345 | 16212.8 | 16213.5 | 0.7
ASGI-2018-010 | 03 - Central | 532790 | EXPED WF7 | 345 | 7204.1 | 7204.2 | 0.1
ASGI-2018-010 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18304 | 18304.4 | 0.4
ASGI-2018-010 | 03 - Central | 532797 | WOLFCRK7 | 345 | 18774.6 | 18775 | 0.4
ASGI-2018-010 | 03 - Central | 532799 | WAVERLY7 | 345 | 16614.1 | 16614.5 | 0.4
ASGI-2018-010 | 03 - Central | 532802 | WAVERTX7 | 345 | 13844 | 13844.4 | 0.4
ASGI-2018-010 | 03 - Central | 532803 | EXPEDITION7 | 345 | 10661.1 | 10661.2 | 0.1
ASGI-2018-010 | 03 - Central | 532851 | AUBURN 6 | 230 | 14011.4 | 14011.9 | 0.5
ASGI-2018-010 | 03 - Central | 532853 | LAWHILL6 | 230 | 14196.9 | 14197.5 | 0.6
ASGI-2018-010 | 03 - Central | 532854 | LEC U5 6 | 230 | 14062.2 | 14062.9 | 0.7
ASGI-2018-010 | 03 - Central | 532856 | SWISVAL6 | 230 | 23042.2 | 23044.8 | 2.6
ASGI-2018-010 | 03 - Central | 532857 | TECHILL6 | 230 | 11282.1 | 11282.6 | 0.5
ASGI-2018-010 | 03 - Central | 532863 | MORRIS 6 | 230 | 14609.3 | 14609.6 | 0.3
ASGI-2018-010 | 03 - Central | 532912 | EDWRDVL5 | 161 | 22584.5 | 22589.1 | 4.6
ASGI-2018-010 | 03 - Central | 533283 | 87TH 3 | 115 | 28110.2 | 28115.2 | 5
ASGI-2018-010 | 03 - Central | 541198 | PECULR 7 | 345 | 21273.7 | 21282.2 | 8.5
ASGI-2018-010 | 03 - Central | 541200 | PHILL 7 | 345 | 19303.2 | 19308.1 | 4.9
ASGI-2018-010 | 03 - Central | 541341 | S.HARP 5 | 161 | 21896.2 | 21900.4 | 4.2
ASGI-2018-010 | 03 - Central | 541342 | PECULR 5 | 161 | 23785.3 | 23790.3 | 5
ASGI-2018-010 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2677.1 | 2677.1 | 0
ASGI-2018-010 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35952.2 | 35978.4 | 26.2
ASGI-2018-010 | 03 - Central | 542947 | MERRIAM_CAP5 | 161 | 27738.9 | 27749.2 | 10.3
ASGI-2018-010 | 03 - Central | 542965 | W.GRDNR7 | 345 | 29838.9 | 29873.7 | 34.8
ASGI-2018-010 | 03 - Central | 542966 | WGARDNR5 | 161 | 30722 | 30884.6 | 162.6
ASGI-2018-010 | 03 - Central | 542968 | STILWEL7 | 345 | 26594.8 | 26612 | 17.2
ASGI-2018-010 | 03 - Central | 542969 | STILWEL5 | 161 | 41740.4 | 41769.4 | 29
ASGI-2018-010 | 03 - Central | 542977 | CRAIG 7 | 345 | 24898.5 | 24917.5 | 19
ASGI-2018-010 | 03 - Central | 542978 | CRAIG 5 | 161 | 45396.3 | 45438 | 41.7
ASGI-2018-010 | 03 - Central | 542979 | PFLUMM 5 | 161 | 30584.8 | 30601.8 | 17
ASGI-2018-010 | 03 - Central | 542981 | LACYGNE7 | 345 | 27801.7 | 27808.9 | 7.2
ASGI-2018-010 | 03 - Central | 542994 | HICKMAN5 | 161 | 20202.5 | 20207 | 4.5
ASGI-2018-010 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37837.9 | 37858.3 | 20.4
ASGI-2018-010 | 03 - Central | 543032 | MERRIAM5 | 161 | 33045.2 | 33059.8 | 14.6
ASGI-2018-010 | 03 - Central | 543036 | OLATHE 5 | 161 | 27828.1 | 27851.2 | 23.1
ASGI-2018-010 | 03 - Central | 543037 | QUARRY 5 | 161 | 16382.5 | 16404.1 | 21.6
ASGI-2018-010 | 03 - Central | 543038 | LENEXA 5 | 161 | 39334 | 39362.8 | 28.8
ASGI-2018-010 | 03 - Central | 543040 | ROEPARK5 | 161 | 31086.4 | 31095.5 | 9.1
ASGI-2018-010 | 03 - Central | 543041 | SHAWNEE5 | 161 | 28314 | 28323.6 | 9.6
ASGI-2018-010 | 03 - Central | 543043 | MURLEN 5 | 161 | 18697.6 | 18714.9 | 17.3
ASGI-2018-010 | 03 - Central | 543044 | MOONLT 5 | 161 | 18135.6 | 18172.8 | 37.2
ASGI-2018-010 | 03 - Central | 543047 | OVERLPK5 | 161 | 33323.7 | 33341.8 | 18.1
ASGI-2018-010 | 03 - Central | 543048 | COLLEGE5 | 161 | 31213.9 | 31236.9 | 23
ASGI-2018-010 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31626.6 | 31655.8 | 29.2
ASGI-2018-010 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23489.6 | 23501 | 11.4
ASGI-2018-010 | 03 - Central | 543052 | REEDER 5 | 161 | 21776.7 | 21784.4 | 7.7
ASGI-2018-010 | 03 - Central | 543053 | REDEL 5 | 161 | 25412.6 | 25421.1 | 8.5
ASGI-2018-010 | 03 - Central | 543054 | CEDARNL5 | 161 | 10928.3 | 10948.8 | 20.5
ASGI-2018-010 | 03 - Central | 543055 | SEOTTWA5 | 161 | 7689.8 | 7753.8 | 64
ASGI-2018-010 | 03 - Central | 543056 | GARDNER5 | 161 | 16882.6 | 16914.6 | 32
ASGI-2018-010 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21240 | 21254.1 | 14.1
ASGI-2018-010 | 03 - Central | 543058 | NLOUISB5 | 161 | 9372.6 | 9375.3 | 2.7
ASGI-2018-010 | 03 - Central | 543065 | CNTRVIL5 | 161 | 6461.2 | 6464.1 | 2.9
ASGI-2018-010 | 03 - Central | 543066 | S.OTTWA5 | 161 | 7692.2 | 7747 | 54.8
ASGI-2018-010 | 03 - Central | 543067 | CENTENL5 | 161 | 10922.6 | 10939.6 | 17
ASGI-2018-010 | 03 - Central | 543068 | WAGSTAF5 | 161 | 14612.8 | 14624.5 | 11.7
ASGI-2018-010 | 03 - Central | 543069 | PAOLA 5 | 161 | 11035.6 | 11056.5 | 20.9
ASGI-2018-010 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10337.6 | 10578.2 | 240.6
ASGI-2018-010 | 03 - Central | 543105 | BULLCRK5 | 161 | 29762 | 29911.3 | 149.3
ASGI-2018-010 | 03 - Central | 543112 | OSAWAT 5 | 161 | 10940.8 | 10961.3 | 20.5
ASGI-2018-010 | 03 - Central | 543126 | LACKMAN5 | 161 | 13939.9 | 13942.9 | 3
ASGI-2018-010 | 03 - Central | 543132 | BNSF 5 | 161 | 22536.1 | 22610.4 | 74.3
ASGI-2018-010 | 03 - Central | 543135 | OSAWTM_CAP5 | 161 | 10289.1 | 10307.3 | 18.2
ASGI-2018-010 | 03 - Central | 543166 | NEASTOTTW5 | 161 | 6614.2 | 6661.5 | 47.3
ASGI-2018-010 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27065.7 | 27072.5 | 6.8
ASGI-2018-010 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27065.7 | 27072.5 | 6.8
ASGI-2018-010 | 03 - Central | 543650 | DAKOTA_5 | 161 | 7723.1 | 7724.6 | 1.5
ASGI-2018-010 | 03 - Central | 543651 | PRQN_WIND5 | 161 | 6776 | 6777 | 1
ASGI-2018-010 | 03 - Central | 543659 | LACYGNE2 | 69 | 2816.1 | 2816.1 | 0
ASGI-2018-010 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 673.4 | 673.5 | 0.1
ASGI-2018-010 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 645 | 645 | 0
ASGI-2018-010 | 03 - Central | 546651 | BARBER 5 | 161 | 31165.5 | 31172.8 | 7.3
ASGI-2018-010 | 03 - Central | 546655 | KAW W 5 | 161 | 24587.7 | 24592.3 | 4.6
ASGI-2018-010 | 03 - Central | 546722 | MAYSOTH5 | 161 | 22856.4 | 22860 | 3.6
ASGI-2018-010 | 03 - Central | 546742 | METRO 5 | 161 | 27908.6 | 27915.6 | 7
ASGI-2018-010 | 03 - Central | 562476 | G14-001-TAP | 345 | 11236.1 | 11236.2 | 0.1
ASGI-2018-010 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7668.3 | 7668.3 | 0
ASGI-2018-010 | 03 - Central | 588240 | GEN-2016-149 | 345 | 9126.7 | 9127.1 | 0.4
ASGI-2018-010 | 03 - Central | 588250 | GEN-2016-174 | 345 | 5930 | 5930.1 | 0.1
ASGI-2018-010 | 03 - Central | 588260 | GEN-2016-176 | 345 | 4804.3 | 4804.3 | 0
ASGI-2018-010 | 03 - Central | 588270 | GEN-2016-150 | 345 | 3571.9 | 3572 | 0.1
ASGI-2018-010 | 03 - Central | 588300 | GEN-2016-157 | 345 | 5235.1 | 5235.9 | 0.8
ASGI-2018-010 | 03 - Central | 588310 | GEN-2016-158 | 345 | 4936.4 | 4937.1 | 0.7
ASGI-2018-010 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19309.6 | 19312.6 | 3
ASGI-2018-010 | 03 - Central | 760921 | G17-209-TAP | 345 | 19817.4 | 19820.6 | 3.2
ASGI-2018-010 | 03 - Central | 761733 | GEN-2017-228 | 345 | 26407.7 | 26424.7 | 17
ASGI-2018-010 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5675.3 | 5675.6 | 0.3
ASGI-2018-010 | 03 - Central | 761922 | GEN-2017-128 | 345 | 4756 | 4756.2 | 0.2
ASGI-2018-010 | 03 - Central | 761943 | GEN-2017-191 | 345 | 18542.7 | 18546.4 | 3.7
ASGI-2018-010 | 03 - Central | 762006 | GEN-2017-111 | 161 | 14479.5 | 14480.5 | 1
ASGI-2018-010 | 03 - Central | 762010 | G17-111-TAP | 161 | 14479.5 | 14480.5 | 1
ASGI-2018-010 | 03 - Central | 762279 | GEN-2017-195 | 345 | 29753.8 | 29788.3 | 34.5
ASGI-2018-010 | 03 - Central | 762405 | ASG-2018-010 | 161 | Project Bus - Disconnected | 10570.1 | Project Bus - Disconnected
ASGI-2018-010 | 03 - Central | 762416 | ASG-2018-011 | 161 | 7688 | 7742.7 | 54.7
ASGI-2018-010 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12043.8 | 12044 | 0.2
ASGI-2018-010 | 03 - Central | 762687 | G18-032_DUMY | 345 | 18304 | 18304.4 | 0.4
ASGI-2018-011 | 03 - Central | 532774 | SWISVAL7 | 345 | 18594.8 | 18597.4 | 2.6
ASGI-2018-011 | 03 - Central | 532934 | MARMTNE5 | 161 | 8713.1 | 8716.4 | 3.3
ASGI-2018-011 | 03 - Central | 532935 | MARMTNW5 | 161 | 8708.4 | 8711.7 | 3.3
ASGI-2018-011 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2677.1 | 2677.1 | 0
ASGI-2018-011 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35961.1 | 35978.4 | 17.3
ASGI-2018-011 | 03 - Central | 542965 | W.GRDNR7 | 345 | 29850.7 | 29873.7 | 23
ASGI-2018-011 | 03 - Central | 542966 | WGARDNR5 | 161 | 30807.7 | 30884.6 | 76.9
ASGI-2018-011 | 03 - Central | 542968 | STILWEL7 | 345 | 26595.1 | 26612 | 16.9
ASGI-2018-011 | 03 - Central | 542969 | STILWEL5 | 161 | 41727.3 | 41769.4 | 42.1
ASGI-2018-011 | 03 - Central | 542977 | CRAIG 7 | 345 | 24904.8 | 24917.5 | 12.7
ASGI-2018-011 | 03 - Central | 542978 | CRAIG 5 | 161 | 45410.4 | 45438 | 27.6
ASGI-2018-011 | 03 - Central | 542981 | LACYGNE7 | 345 | 27802.8 | 27808.9 | 6.1
ASGI-2018-011 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37844.3 | 37858.3 | 14
ASGI-2018-011 | 03 - Central | 543044 | MOONLT 5 | 161 | 18154.1 | 18172.8 | 18.7
ASGI-2018-011 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31638.1 | 31655.8 | 17.7
ASGI-2018-011 | 03 - Central | 543054 | CEDARNL5 | 161 | 10939.1 | 10948.8 | 9.7
ASGI-2018-011 | 03 - Central | 543055 | SEOTTWA5 | 161 | 7548.4 | 7753.8 | 205.4
ASGI-2018-011 | 03 - Central | 543056 | GARDNER5 | 161 | 16898.5 | 16914.6 | 16.1
ASGI-2018-011 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21221.3 | 21254.1 | 32.8
ASGI-2018-011 | 03 - Central | 543058 | NLOUISB5 | 161 | 9368.9 | 9375.3 | 6.4
ASGI-2018-011 | 03 - Central | 543065 | CNTRVIL5 | 161 | 6452.4 | 6464.1 | 11.7
ASGI-2018-011 | 03 - Central | 543066 | S.OTTWA5 | 161 | 7506.8 | 7747 | 240.2
ASGI-2018-011 | 03 - Central | 543067 | CENTENL5 | 161 | 10873.5 | 10939.6 | 66.1
ASGI-2018-011 | 03 - Central | 543068 | WAGSTAF5 | 161 | 14589.3 | 14624.5 | 35.2
ASGI-2018-011 | 03 - Central | 543069 | PAOLA 5 | 161 | 10972.3 | 11056.5 | 84.2
ASGI-2018-011 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10475.7 | 10578.2 | 102.5
ASGI-2018-011 | 03 - Central | 543105 | BULLCRK5 | 161 | 29840.8 | 29911.3 | 70.5
ASGI-2018-011 | 03 - Central | 543112 | OSAWAT 5 | 161 | 10878.8 | 10961.3 | 82.5
ASGI-2018-011 | 03 - Central | 543132 | BNSF 5 | 161 | 22574.4 | 22610.4 | 36
ASGI-2018-011 | 03 - Central | 543135 | OSAWTM_CAP5 | 161 | 10234.3 | 10307.3 | 73
ASGI-2018-011 | 03 - Central | 543166 | NEASTOTTW5 | 161 | 6509.3 | 6661.5 | 152.2
ASGI-2018-011 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27066.8 | 27072.5 | 5.7
ASGI-2018-011 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27066.8 | 27072.5 | 5.7
ASGI-2018-011 | 03 - Central | 543650 | DAKOTA_5 | 161 | 7719 | 7724.6 | 5.6
ASGI-2018-011 | 03 - Central | 543651 | PRQN_WIND5 | 161 | 6773.1 | 6777 | 3.9
ASGI-2018-011 | 03 - Central | 543659 | LACYGNE2 | 69 | 2816.1 | 2816.1 | 0
ASGI-2018-011 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 673.4 | 673.5 | 0.1
ASGI-2018-011 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 645 | 645 | 0
ASGI-2018-011 | 03 - Central | 588300 | GEN-2016-157 | 345 | 5235.4 | 5235.9 | 0.5
ASGI-2018-011 | 03 - Central | 588310 | GEN-2016-158 | 345 | 4936.6 | 4937.1 | 0.5
ASGI-2018-011 | 03 - Central | 588500 | GEN-2017-005 | 161 | 7091 | 7092.2 | 1.2
ASGI-2018-011 | 03 - Central | 588504 | G17-005-TAP | 161 | 7179.6 | 7180.8 | 1.2
ASGI-2018-011 | 03 - Central | 761733 | GEN-2017-228 | 345 | 26408 | 26424.7 | 16.7
ASGI-2018-011 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5675.4 | 5675.6 | 0.2
ASGI-2018-011 | 03 - Central | 761922 | GEN-2017-128 | 345 | 4756 | 4756.2 | 0.2
ASGI-2018-011 | 03 - Central | 761943 | GEN-2017-191 | 345 | 18543.9 | 18546.4 | 2.5
ASGI-2018-011 | 03 - Central | 762279 | GEN-2017-195 | 345 | 29765.5 | 29788.3 | 22.8
ASGI-2018-011 | 03 - Central | 762405 | ASG-2018-010 | 161 | 10467.8 | 10570.1 | 102.3
ASGI-2018-011 | 03 - Central | 762416 | ASG-2018-011 | 161 | Project Bus - Disconnected | 7742.7 | Project Bus - Disconnected
GEN-2018-009 | 03 - Central | 522912 | Y ROAD 3 | 115 | 4509.5 | 4520 | 10.5
GEN-2018-009 | 03 - Central | 522926 | BOURK 2 | 69 | 8143.8 | 8164.1 | 20.3
GEN-2018-009 | 03 - Central | 522930 | RED DEVIL 3 | 115 | 2389.7 | 2392.6 | 2.9
GEN-2018-009 | 03 - Central | 522931 | REED 2 | 69 | 8143.8 | 8164.1 | 20.3
GEN-2018-009 | 03 - Central | 522935 | GOODWELL 3 | 115 | 3457.8 | 3463.9 | 6.1
GEN-2018-009 | 03 - Central | 523089 | TC-TXCOUNTY2 | 69 | 8143.8 | 8164.1 | 20.3
GEN-2018-009 | 03 - Central | 523090 | TEXAS_CNTY 3 | 115 | 7859 | 7891 | 32
GEN-2018-009 | 03 - Central | 523093 | HITCHLAND 3 | 115 | 15850.5 | 15890.4 | 39.9
GEN-2018-009 | 03 - Central | 523097 | HITCHLAND 7 | 345 | 11377.9 | 11410.4 | 32.5
GEN-2018-009 | 03 - Central | 523101 | NOBLE_WND 7 | 345 | 11342.5 | 11374.9 | 32.4
GEN-2018-009 | 03 - Central | 523103 | NOBLE_WND 3 | 115 | 9166.7 | 9173.7 | 7
GEN-2018-009 | 03 - Central | 523106 | TXPHSF 3 | 115 | 4227 | 4263.8 | 36.8
GEN-2018-009 | 03 - Central | 523111 | NOVUS1 3 | 115 | 6534.2 | 6537.8 | 3.6
GEN-2018-009 | 03 - Central | 523112 | NOVUS1 7 | 345 | 11195.8 | 11227.3 | 31.5
GEN-2018-009 | 03 - Central | 523113 | TC-MCMURRY 3 | 115 | 6185.2 | 6203.7 | 18.5
GEN-2018-009 | 03 - Central | 523118 | BUFF_DUNES 7 | 345 | 6933.6 | 6944.9 | 11.3
GEN-2018-009 | 03 - Central | 523130 | GRPLNS-HV4-3 | 115 | 6290.5 | 6293.8 | 3.3
GEN-2018-009 | 03 - Central | 523131 | GRPLNS-HV2-3 | 115 | 8413.1 | 8419 | 5.9
GEN-2018-009 | 03 - Central | 523174 | GOODWELLWND3 | 115 | 6640.6 | 6645.3 | 4.7
GEN-2018-009 | 03 - Central | 523215 | GEN-2011-022 | 345 | 8150.8 | 8167.4 | 16.6
GEN-2018-009 | 03 - Central | 523823 | CARPENTER 7 | 345 | 6493.2 | 6541.3 | 48.1
GEN-2018-009 | 03 - Central | 523853 | FINNEY 7 | 345 | 10820.2 | 10852.2 | 32
GEN-2018-009 | 03 - Central | 531374 | HASKELL3 | 115 | 5056.1 | 5219.5 | 163.4
GEN-2018-009 | 03 - Central | 531375 | PUCKET 3 | 115 | 5060.6 | 5074.8 | 14.2
GEN-2018-009 | 03 - Central | 531377 | HICKOCK2 | 69 | 2882.6 | 2887.2 | 4.6
GEN-2018-009 | 03 - Central | 531378 | HICKOCK3 | 115 | 5640.8 | 5670 | 29.2
GEN-2018-009 | 03 - Central | 531380 | HUGOTON2 | 69 | 2974.3 | 2981.5 | 7.2
GEN-2018-009 | 03 - Central | 531384 | MOSCOW 2 | 69 | 2236.9 | 2241.5 | 4.6
GEN-2018-009 | 03 - Central | 531385 | MOSCOWT2 | 69 | 2352.8 | 2357.9 | 5.1
GEN-2018-009 | 03 - Central | 531388 | NORTH6 2 | 69 | 2646 | 2652.6 | 6.6
GEN-2018-009 | 03 - Central | 531389 | NORTH6T2 | 69 | 3094.8 | 3103.8 | 9
GEN-2018-009 | 03 - Central | 531390 | PIONEER2 | 69 | 4073.8 | 4081.4 | 7.6
GEN-2018-009 | 03 - Central | 531391 | PIONEER3 | 115 | 6111.5 | 6140.1 | 28.6
GEN-2018-009 | 03 - Central | 531392 | PIONTAP3 | 115 | 6885.9 | 6991.5 | 105.6
GEN-2018-009 | 03 - Central | 531394 | PRAXAIR2 | 69 | 2563.6 | 2567.2 | 3.6
GEN-2018-009 | 03 - Central | 531395 | ROLLA 2 | 115 | 2640.4 | 2649.8 | 9.4
GEN-2018-009 | 03 - Central | 531398 | SUBLETE3 | 115 | 6157.1 | 6241.3 | 84.2
GEN-2018-009 | 03 - Central | 531400 | PK_GOAB3 | 115 | 5074.7 | 5088.9 | 14.2
GEN-2018-009 | 03 - Central | 531401 | ULU E 2 | 69 | 3819.9 | 3826.5 | 6.6
GEN-2018-009 | 03 - Central | 531402 | ULU NW 2 | 69 | 3218.8 | 3223.6 | 4.8
GEN-2018-009 | 03 - Central | 531403 | ULU PLT2 | 69 | 3134.1 | 3138.6 | 4.5
GEN-2018-009 | 03 - Central | 531404 | WALKMYR2 | 69 | 8634.5 | 8707.6 | 73.1
GEN-2018-009 | 03 - Central | 531405 | WALKMYR3 | 115 | 10101.4 | 10270.1 | 168.7
GEN-2018-009 | 03 - Central | 531406 | WOODS 2 | 69 | 6355.9 | 6395.5 | 39.6
GEN-2018-009 | 03 - Central | 531442 | SAT-TAP3 | 115 | 5111.4 | 5267.4 | 156
GEN-2018-009 | 03 - Central | 531454 | MOSCCMS2 | 69 | 1948.3 | 1968.4 | 20.1
GEN-2018-009 | 03 - Central | 531463 | SANTCMS2 | 69 | 1329.5 | 1338.6 | 9.1
GEN-2018-009 | 03 - Central | 531466 | CMSSWRD2 | 69 | 3492.7 | 3556.1 | 63.4
GEN-2018-009 | 03 - Central | 531467 | SEWARD-3 | 115 | 4927.7 | 5148.1 | 220.4
GEN-2018-009 | 03 - Central | 531472 | AMOCO 3 | 115 | 5033.5 | 5056.7 | 23.2
GEN-2018-009 | 03 - Central | 531479 | CHUGTON2 | 69 | 2677.8 | 2683.6 | 5.8
GEN-2018-009 | 03 - Central | 531481 | HUGOTON3 | 115 | 5814.9 | 5860.8 | 45.9
GEN-2018-009 | 03 - Central | 531483 | GRANTTP3 | 115 | 5012.7 | 5037.3 | 24.6
GEN-2018-009 | 03 - Central | 531484 | GRANT 3 | 115 | 4723.4 | 4745.2 | 21.8
GEN-2018-009 | 03 - Central | 531490 | ULYSPLT3 | 115 | 4090.6 | 4101.8 | 11.2
GEN-2018-009 | 03 - Central | 531494 | ABBK 2 | 115 | 5235.2 | 5272.4 | 37.2
GEN-2018-009 | 03 - Central | 531510 | HARBNGR3 | 115 | 10724.6 | 10884.2 | 159.6
GEN-2018-009 | 03 - Central | 531512 | HARBNGR7 | 345 | 6474.5 | 6522.5 | 48
GEN-2018-009 | 03 - Central | 539640 | HAYNE3 | 115 | 5187.9 | 5654.8 | 466.9
GEN-2018-009 | 03 - Central | 539641 | NW-DODG3 | 115 | 3645 | 3649.5 | 4.5
GEN-2018-009 | 03 - Central | 539645 | DCBEEF3 | 115 | 6869.8 | 6886.1 | 16.3
GEN-2018-009 | 03 - Central | 539646 | KISMET 3 | 115 | 5058.6 | 5411.9 | 353.3
GEN-2018-009 | 03 - Central | 539652 | CMRIVTP3 | 115 | 5577.9 | 6063.6 | 485.7
GEN-2018-009 | 03 - Central | 539654 | CIM-PLT3 | 115 | 6118.3 | 6819.1 | 700.8
GEN-2018-009 | 03 - Central | 539659 | CUDAHY 3 | 115 | 4184.6 | 4273.7 | 89.1
GEN-2018-009 | 03 - Central | 539671 | FTDODGE3 | 115 | 9379.2 | 9410 | 30.8
GEN-2018-009 | 03 - Central | 539672 | E-LIBER3 | 115 | 4752.7 | 5066.9 | 314.2
GEN-2018-009 | 03 - Central | 539680 | N-DODGE3 | 115 | 4668.2 | 4675.7 | 7.5
GEN-2018-009 | 03 - Central | 539690 | E-PINE 3 | 115 | 4090.9 | 4321.9 | 231
GEN-2018-009 | 03 - Central | 539691 | SATMKEC3 | 115 | 5101.7 | 5257.1 | 155.4
GEN-2018-009 | 03 - Central | 539700 | W-LIBER3 | 115 | 3768.7 | 3983.4 | 214.7
GEN-2018-009 | 03 - Central | 539737 | NLIB 3 | 115 | 4590.3 | 4912.2 | 321.9
GEN-2018-009 | 03 - Central | 539740 | EDODGE 3 | 115 | 6291.5 | 6305.1 | 13.6
GEN-2018-009 | 03 - Central | 539749 | N-CIMRN3 | 115 | 6061.7 | 6740.4 | 678.7
GEN-2018-009 | 03 - Central | 539751 | NATBEEF3 | 115 | 4687 | 4997.5 | 310.5
GEN-2018-009 | 03 - Central | 539783 | CRKCK 3 | 115 | 4694.4 | 4756.8 | 62.4
GEN-2018-009 | 03 - Central | 539784 | ENSNGW 3 | 115 | 3475.6 | 3505.4 | 29.8
GEN-2018-009 | 03 - Central | 560577 | G06-44 | 115 | 6534.2 | 6537.8 | 3.6
GEN-2018-009 | 03 - Central | 576395 | GEN-2010-014 | 345 | 8150.8 | 8167.4 | 16.6
GEN-2018-009 | 03 - Central | 576397 | G10014G11022 | 345 | 8150.8 | 8167.4 | 16.6
GEN-2018-009 | 03 - Central | 589380 | GEN-2017-100 | 115 | 4799.4 | 4811.3 | 11.9
GEN-2018-009 | 03 - Central | 599950 | LAMAR7 | 345 | 4354.4 | 4359.3 | 4.9
GEN-2018-009 | 03 - Central | 762471 | GEN-2018-009 | 115 | Project Bus - Disconnected | 3206 | Project Bus - Disconnected
GEN-2018-009 | 03 - Central | 762658 | GEN-2018-030 | 345 | 5605.6 | 5613.6 | 8
GEN-2018-009 | 03 - Central | 762662 | G18-030-TAP | 345 | 6335 | 6345.4 | 10.4
GEN-2018-013 | 03 - Central | 530592 | SMOKYHL6 | 230 | 7077.3 | 7083.3 | 6
GEN-2018-013 | 03 - Central | 530593 | SMKYP1 6 | 230 | 6178.5 | 6182.9 | 4.4
GEN-2018-013 | 03 - Central | 530599 | SMKYP2 6 | 230 | 6546.1 | 6551.1 | 5
GEN-2018-013 | 03 - Central | 530720 | KNOLL S 6 | 230 | 11993.2 | 11995.3 | 2.1
GEN-2018-013 | 03 - Central | 532767 | GEARY 7 | 345 | 10631 | 10663.9 | 32.9
GEN-2018-013 | 03 - Central | 532773 | SUMMIT 7 | 345 | 11676.4 | 11712 | 35.6
GEN-2018-013 | 03 - Central | 532863 | MORRIS 6 | 230 | 14595.6 | 14609.6 | 14
GEN-2018-013 | 03 - Central | 532871 | CIRCLE 6 | 230 | 9074.2 | 9083.3 | 9.1
GEN-2018-013 | 03 - Central | 532872 | EMCPHER6 | 230 | 8212.4 | 8226.8 | 14.4
GEN-2018-013 | 03 - Central | 532873 | SUMMIT 6 | 230 | 13881.3 | 13953.7 | 72.4
GEN-2018-013 | 03 - Central | 532874 | UNIONRG6 | 230 | 8493.6 | 8506.2 | 12.6
GEN-2018-013 | 03 - Central | 532875 | DVISTA 6 | 230 | 5049.7 | 5053.2 | 3.5
GEN-2018-013 | 03 - Central | 533320 | CLAYCSS3 | 115 | 2437.8 | 2444 | 6.2
GEN-2018-013 | 03 - Central | 533323 | CLAYCTR3 | 115 | 3107.3 | 3117.2 | 9.9
GEN-2018-013 | 03 - Central | 533324 | TCRILEY 3 | 115 | 2138.5 | 2143.3 | 4.8
GEN-2018-013 | 03 - Central | 533325 | CLAYGEN3 | 115 | 2364.9 | 2370.7 | 5.8
GEN-2018-013 | 03 - Central | 533328 | FT JCT 3 | 115 | 15997.5 | 16098.2 | 100.7
GEN-2018-013 | 03 - Central | 533329 | NCFOUND3 | 115 | 12275 | 12347 | 72
GEN-2018-013 | 03 - Central | 533335 | MCDOWEL3 | 115 | 19448.7 | 19510.3 | 61.6
GEN-2018-013 | 03 - Central | 533336 | GEARY 3 | 115 | 20075 | 20188.3 | 113.3
GEN-2018-013 | 03 - Central | 533342 | WJCCTY 3 | 115 | 14399.5 | 14497.3 | 97.8
GEN-2018-013 | 03 - Central | 533344 | WJCCTYW3 | 115 | 14304.4 | 14402.2 | 97.8
GEN-2018-013 | 03 - Central | 533359 | UNIONRG3 | 115 | 3902.5 | 3903.8 | 1.3
GEN-2018-013 | 03 - Central | 533360 | TCHOPE 3 | 115 | 3476.3 | 3477.4 | 1.1
GEN-2018-013 | 03 - Central | 533361 | AEC 3 | 115 | 8787.1 | 9114.7 | 327.6
GEN-2018-013 | 03 - Central | 533362 | CHAPMAN3 | 115 | 11867.5 | 12016 | 148.5
GEN-2018-013 | 03 - Central | 533364 | CRAWFRD3 | 115 | 10593.3 | 10681 | 87.7
GEN-2018-013 | 03 - Central | 533365 | EABILEN3 | 115 | 8857.5 | 9122.3 | 264.8
GEN-2018-013 | 03 - Central | 533367 | BERG 3 | 115 | 11760.2 | 11831.1 | 70.9
GEN-2018-013 | 03 - Central | 533370 | NORTHST3 | 115 | 11549.2 | 11680.7 | 131.5
GEN-2018-013 | 03 - Central | 533371 | NORTHVW3 | 115 | 12594.5 | 12764.4 | 169.9
GEN-2018-013 | 03 - Central | 533374 | MENTOR 3 | 115 | 12997.9 | 13086.3 | 88.4
GEN-2018-013 | 03 - Central | 533376 | SALINA 3 | 115 | 11189 | 11307.2 | 118.2
GEN-2018-013 | 03 - Central | 533377 | SCHILNG3 | 115 | 11174.4 | 11254.1 | 79.7
GEN-2018-013 | 03 - Central | 533378 | SMOKYHLLS3 | 115 | 11245.4 | 11309.4 | 64
GEN-2018-013 | 03 - Central | 533379 | SO GATE3 | 115 | 10743.2 | 10800 | 56.8
GEN-2018-013 | 03 - Central | 533381 | SUMMIT 3 | 115 | 18216.2 | 18361.2 | 145
GEN-2018-013 | 03 - Central | 533394 | CORONAD3 | 115 | 7335.3 | 7351 | 15.7
GEN-2018-013 | 03 - Central | 533417 | EMCPHER3 | 115 | 11817.3 | 11833.3 | 16
GEN-2018-013 | 03 - Central | 533438 | WMCPHER3 | 115 | 11483.9 | 11499.9 | 16
GEN-2018-013 | 03 - Central | 587880 | GEN-2016-111 | 345 | 6877.4 | 6883.6 | 6.2
GEN-2018-013 | 03 - Central | 587884 | G16-111-TAP | 345 | 10393.7 | 10408.9 | 15.2
GEN-2018-013 | 03 - Central | 588490 | GEN-2017-004 | 345 | 8601 | 8618.8 | 17.8
GEN-2018-013 | 03 - Central | 588494 | G17-004-TAP | 345 | 10001 | 10025.4 | 24.4
GEN-2018-013 | 03 - Central | 760000 | GEN-2017-120 | 115 | 9034.6 | 9487.3 | 452.7
GEN-2018-013 | 03 - Central | 760007 | G17-120-TAP | 115 | 9034.6 | 9487.3 | 452.7
GEN-2018-022 | 03 - Central | 41453 | J1145 SUB | 345 | 20569.2 | 20570.2 | 1
GEN-2018-022 | 03 - Central | 44882 | J1488_INV | 345 | 19535 | 19535.8 | 0.8
GEN-2018-022 | 03 - Central | 44887 | J1490_INV | 345 | 19634.8 | 19635.6 | 0.8
GEN-2018-022 | 03 - Central | 44888 | J1490_POI | 345 | 20569.2 | 20570.2 | 1
GEN-2018-022 | 03 - Central | 300039 | 7FAIRPT | 345 | 12953.4 | 12961.2 | 7.8
GEN-2018-022 | 03 - Central | 300043 | 7KINGDM | 345 | 16625.5 | 16626.4 | 0.9
GEN-2018-022 | 03 - Central | 300044 | 7MCCRED | 345 | 19780.8 | 19782 | 1.2
GEN-2018-022 | 03 - Central | 300049 | 7THOMHL | 345 | 15077.7 | 15078 | 0.3
GEN-2018-022 | 03 - Central | 300500 | 5HUNTSDL | 161 | 10867.3 | 10867.6 | 0.3
GEN-2018-022 | 03 - Central | 301503 | 7THOMHLGSU3 | 345 | 14964.4 | 14964.7 | 0.3
GEN-2018-022 | 03 - Central | 301559 | 5FAIRPTXF3 | 161 | 17013 | 17017 | 4
GEN-2018-022 | 03 - Central | 345088 | 7MCCREDIE | 345 | 6978.3 | 6978.8 | 0.5
GEN-2018-022 | 03 - Central | 345221 | 5MOBERLY | 161 | 15947.2 | 15947.5 | 0.3
GEN-2018-022 | 03 - Central | 345408 | 7OVERTON | 345 | 13506.8 | 13508.8 | 2
GEN-2018-022 | 03 - Central | 345409 | 5OVERTON | 161 | 21623.9 | 21625.2 | 1.3
GEN-2018-022 | 03 - Central | 345411 | 5OVERTON 2 | 161 | 21623.9 | 21625.2 | 1.3
GEN-2018-022 | 03 - Central | 346117 | 2OVERTON | 69 | 3690.5 | 3690.6 | 0.1
GEN-2018-022 | 03 - Central | 541147 | ST JOE_CAP5 | 161 | 19029.7 | 19034.6 | 4.9
GEN-2018-022 | 03 - Central | 541197 | MULLNCR7 | 345 | 10539.1 | 11103.7 | 564.6
GEN-2018-022 | 03 - Central | 541198 | PECULR 7 | 345 | 21273.1 | 21282.2 | 9.1
GEN-2018-022 | 03 - Central | 541199 | ST JOE 7 | 345 | 20983.1 | 20998.6 | 15.5
GEN-2018-022 | 03 - Central | 541200 | PHILL 7 | 345 | 19294.7 | 19308.1 | 13.4
GEN-2018-022 | 03 - Central | 541201 | SIBLEY 7 | 345 | 21842.1 | 21901 | 58.9
GEN-2018-022 | 03 - Central | 541202 | SIBLEY 5 | 161 | 27658.6 | 27675.6 | 17
GEN-2018-022 | 03 - Central | 541215 | HLLMRK 5 | 161 | 14254.4 | 14257.3 | 2.9
GEN-2018-022 | 03 - Central | 541225 | PHILL 5 | 161 | 35555.1 | 35562.7 | 7.6
GEN-2018-022 | 03 - Central | 541235 | DUNCAN 5 | 161 | 20008.4 | 20013.4 | 5
GEN-2018-022 | 03 - Central | 541239 | HSNVL 5 | 161 | 17126.5 | 17127.9 | 1.4
GEN-2018-022 | 03 - Central | 541243 | LKWINBG5 | 161 | 25969.3 | 25973.4 | 4.1
GEN-2018-022 | 03 - Central | 541244 | ORRICK 5 | 161 | 14188.4 | 14192.1 | 3.7
GEN-2018-022 | 03 - Central | 541250 | SIBLEYPL | 161 | 29283.2 | 29300 | 16.8
GEN-2018-022 | 03 - Central | 541253 | ST JOE 5 | 161 | 21382.3 | 21388.6 | 6.3
GEN-2018-022 | 03 - Central | 541263 | SIBLEY 2 | 69 | 11897.9 | 11898.9 | 1
GEN-2018-022 | 03 - Central | 541280 | PHILL 2 | 69 | 10433.1 | 10433.4 | 0.3
GEN-2018-022 | 03 - Central | 541313 | HARRIS | 161 | 27087.7 | 27092.1 | 4.4
GEN-2018-022 | 03 - Central | 541342 | PECULR 5 | 161 | 23786.5 | 23790.3 | 3.8
GEN-2018-022 | 03 - Central | 541400 | EASTOWN7 | 345 | 19328.9 | 19339.3 | 10.4
GEN-2018-022 | 03 - Central | 541411 | MC REAC1 | 345 | 9944 | 10445 | 501
GEN-2018-022 | 03 - Central | 541412 | MC REAC2 | 345 | 9944 | 10445 | 501
GEN-2018-022 | 03 - Central | 541413 | MC REAC3 | 345 | 9944 | 10445 | 501
GEN-2018-022 | 03 - Central | 541414 | SIB REA1 | 345 | 19433 | 19479.5 | 46.5
GEN-2018-022 | 03 - Central | 541500 | KETCHEM7 | 345 | 8975 | 9152.9 | 177.9
GEN-2018-022 | 03 - Central | 541501 | OSBORN7 | 345 | 7905.8 | 8041.1 | 135.3
GEN-2018-022 | 03 - Central | 541510 | HOLT 7 | 345 | 14795.1 | 15198.7 | 403.6
GEN-2018-022 | 03 - Central | 541511 | ROCKCK7 | 345 | 15891.1 | 16120.8 | 229.7
GEN-2018-022 | 03 - Central | 541517 | HOLT_REACT7 | 345 | 14671 | 15067.8 | 396.8
GEN-2018-022 | 03 - Central | 541543 | OUTLAW | 345 | 20248.4 | 20415.2 | 166.8
GEN-2018-022 | 03 - Central | 542968 | STILWEL7 | 345 | 26604.1 | 26612 | 7.9
GEN-2018-022 | 03 - Central | 542972 | HAWTH 7 | 345 | 23842.5 | 23869.1 | 26.6
GEN-2018-022 | 03 - Central | 542973 | HAWTHS5 | 161 | 59979.2 | 60011.6 | 32.4
GEN-2018-022 | 03 - Central | 542976 | LEVEE 5 | 161 | 54127.8 | 54153.4 | 25.6
GEN-2018-022 | 03 - Central | 542980 | NASHUA 7 | 345 | 24163.3 | 24179.9 | 16.6
GEN-2018-022 | 03 - Central | 542982 | IATAN 7 | 345 | 31743.4 | 31754.6 | 11.2
GEN-2018-022 | 03 - Central | 543000 | BLUEVLY5 | 161 | 40229.4 | 40243.9 | 14.5
GEN-2018-022 | 03 - Central | 543011 | CHOUTEU5 | 161 | 37615.9 | 37626.7 | 10.8
GEN-2018-022 | 03 - Central | 543027 | RANDLPH5 | 161 | 34377.5 | 34387.8 | 10.3
GEN-2018-022 | 03 - Central | 543028 | NASHUA-5 | 161 | 35090.9 | 35104.6 | 13.7
GEN-2018-022 | 03 - Central | 543129 | HAWTHS_G65 | 161 | 59114.9 | 59146.4 | 31.5
GEN-2018-022 | 03 - Central | 543665 | HAWTHN5 | 161 | 60680.7 | 60714.1 | 33.4
GEN-2018-022 | 03 - Central | 548808 | ECKLES-161 | 161 | 25807.1 | 25817.3 | 10.2
GEN-2018-022 | 03 - Central | 560746 | GEN-2013-002 | 115 | 42305.3 | 42317.8 | 12.5
GEN-2018-022 | 03 - Central | 583700 | GEN-2013-019 | 115 | 29614.7 | 29620.8 | 6.1
GEN-2018-022 | 03 - Central | 585241 | GEN-2015-088 | 345 | 10602.6 | 10605.2 | 2.6
GEN-2018-022 | 03 - Central | 635000 | CBLUFFS3 | 345 | 32240.8 | 32254.9 | 14.1
GEN-2018-022 | 03 - Central | 635001 | CBLUFFS5 | 161 | 39873.1 | 39882.4 | 9.3
GEN-2018-022 | 03 - Central | 635013 | PNYCRK 3 | 345 | 29342.6 | 29354.4 | 11.8
GEN-2018-022 | 03 - Central | 635014 | OVRLND 3 | 345 | 27548.9 | 27558.9 | 10
GEN-2018-022 | 03 - Central | 635016 | STHLND 3 | 345 | 29306.9 | 29318.7 | 11.8
GEN-2018-022 | 03 - Central | 635017 | ATCHSN 3 | 345 | 22513.3 | 22667.7 | 154.4
GEN-2018-022 | 03 - Central | 635018 | WESTBORO 3 | 345 | 20898.3 | 21024.3 | 126
GEN-2018-022 | 03 - Central | 637084 | J476 SHENHLL | 345 | 20762.7 | 20887 | 124.3
GEN-2018-022 | 03 - Central | 640139 | COOPER 3 | 345 | 29754.9 | 29874.7 | 119.8
GEN-2018-022 | 03 - Central | 640140 | COOPER 5 | 161 | 18478.4 | 18495.8 | 17.4
GEN-2018-022 | 03 - Central | 640141 | COOPER_ESST8 | 69 | 4692.1 | 4692.6 | 0.5
GEN-2018-022 | 03 - Central | 640271 | MCCOOL 3 | 345 | 10536.2 | 10537.7 | 1.5
GEN-2018-022 | 03 - Central | 640277 | MOORE 3 | 345 | 22291.1 | 22306.3 | 15.2
GEN-2018-022 | 03 - Central | 640278 | SHELDON7 | 115 | 43746.9 | 43759.4 | 12.5
GEN-2018-022 | 03 - Central | 640446 | COOPER 8 | 69 | 4790.2 | 4790.7 | 0.5
GEN-2018-022 | 03 - Central | 640525 | TOBIAS 3 | 345 | 10602.6 | 10605.2 | 2.6
GEN-2018-022 | 03 - Central | 640590 | MONOLITH 3 | 345 | 21877.1 | 21891.9 | 14.8
GEN-2018-022 | 03 - Central | 640591 | MONOLITH 7 | 115 | 42305.3 | 42317.8 | 12.5
GEN-2018-022 | 03 - Central | 645451 | S3451 3 | 345 | 22597.9 | 22605 | 7.1
GEN-2018-022 | 03 - Central | 645454 | S3454 3 | 345 | 29257.3 | 29276.9 | 19.6
GEN-2018-022 | 03 - Central | 645455 | S3455 3 | 345 | 32443.7 | 32466.9 | 23.2
GEN-2018-022 | 03 - Central | 645456 | S3456 3 | 345 | 35013.1 | 35038.6 | 25.5
GEN-2018-022 | 03 - Central | 645458 | S3458 3 | 345 | 30715.4 | 30830.2 | 114.8
GEN-2018-022 | 03 - Central | 645459 | S3459 3 | 345 | 25600.7 | 25611.9 | 11.2
GEN-2018-022 | 03 - Central | 645740 | S3740 3 | 345 | 23332.3 | 23350.1 | 17.8
GEN-2018-022 | 03 - Central | 645761 | S3761 3 | 345 | 23217.6 | 23229.1 | 11.5
GEN-2018-022 | 03 - Central | 646201 | S1201 5 | 161 | 32165.7 | 32171.5 | 5.8
GEN-2018-022 | 03 - Central | 646206 | S1206 5 | 161 | 45182.4 | 45195.8 | 13.4
GEN-2018-022 | 03 - Central | 646209 | S1209 5 | 161 | 47411.5 | 47426.8 | 15.3
GEN-2018-022 | 03 - Central | 646216 | S1216 5 | 161 | 30885.9 | 30892.1 | 6.2
GEN-2018-022 | 03 - Central | 646232 | S1232 5 | 161 | 26840.7 | 26845.7 | 5
GEN-2018-022 | 03 - Central | 646244 | S1244 5 | 161 | 22329.3 | 22332.8 | 3.5
GEN-2018-022 | 03 - Central | 646254 | S1254 5 | 161 | 32669.6 | 32678.6 | 9
GEN-2018-022 | 03 - Central | 646255 | S1255 5 | 161 | 48992 | 49012.3 | 20.3
GEN-2018-022 | 03 - Central | 646280 | S1280 5 | 161 | 10326 | 10328.9 | 2.9
GEN-2018-022 | 03 - Central | 647006 | S906 N 8 | 69 | 32676.1 | 32678.7 | 2.6
GEN-2018-022 | 03 - Central | 647906 | S906 S 8 | 69 | 33169.1 | 33171.8 | 2.7
GEN-2018-022 | 03 - Central | 650114 | NW68HOLDRG3 | 345 | 17143.1 | 17150.7 | 7.6
GEN-2018-022 | 03 - Central | 650185 | WAGENER 3 | 345 | 20757.8 | 20771.2 | 13.4
GEN-2018-022 | 03 - Central | 650189 | 103&ROKEBY3 | 345 | 20539.3 | 20555.5 | 16.2
GEN-2018-022 | 03 - Central | 650285 | WAGENER 7 | 115 | 32199.8 | 32207.6 | 7.8
GEN-2018-022 | 03 - Central | 760746 | GEN-2017-115 | 345 | 12624.7 | 12914.6 | 289.9
GEN-2018-022 | 03 - Central | 761208 | GEN-2017-210 | 345 | 9165 | 9166.2 | 1.2
GEN-2018-022 | 03 - Central | 761292 | GEN-2017-181 | 345 | 5934.6 | 5935.4 | 0.8
GEN-2018-022 | 03 - Central | 761313 | GEN-2017-182 | 345 | 5027.7 | 5028.3 | 0.6
GEN-2018-022 | 03 - Central | 761376 | GEN-2017-183 | 345 | 8875.5 | 8877.5 | 2
GEN-2018-022 | 03 - Central | 761383 | G17-183-TAP | 345 | 17949.7 | 17959.1 | 9.4
GEN-2018-022 | 03 - Central | 761733 | GEN-2017-228 | 345 | 26416.9 | 26424.7 | 7.8
GEN-2018-022 | 03 - Central | 762581 | GEN-2018-022 | 345 | Project Bus - Disconnected | 8994.7 | Project Bus - Disconnected
GEN-2018-022 | 03 - Central | 762603 | GEN-2018-025 | 345 | 21615.1 | 21621.6 | 6.5
GEN-2018-022 | 03 - Central | 762669 | GEN-2018-031 | 161 | 40219.5 | 40234.1 | 14.6
GEN-2018-022 | 03 - Central | 762691 | GEN-2018-033 | 345 | 23330.8 | 23348.6 | 17.8
GEN-2018-022 | 03 - Central | 992001 | VSC2_1 | 276 | 5877.9 | 5878 | 0.1
GEN-2018-022 | 03 - Central | 992002 | VSC2_2 | 276 | 5877.9 | 5878 | 0.1
GEN-2018-022 | 03 - Central | 992003 | VSC2_3 | 345 | 7351.6 | 7351.7 | 0.1
GEN-2018-022 | 03 - Central | 992005 | VSC2_5 | 276 | 5877.9 | 5878 | 0.1
GEN-2018-022 | 03 - Central | 992006 | VSC2_6 | 276 | 5877.9 | 5878 | 0.1
GEN-2018-030 | 03 - Central | 515554 | BVRCNTY7 | 345 | 12008.9 | 12019.8 | 10.9
GEN-2018-030 | 03 - Central | 515590 | PALDR2W7 | 345 | 10846.5 | 10855 | 8.5
GEN-2018-030 | 03 - Central | 515618 | BALKOW 7 | 345 | 10408.9 | 10416.9 | 8
GEN-2018-030 | 03 - Central | 515634 | PALDR1W7 | 345 | 9836.9 | 9843.6 | 6.7
GEN-2018-030 | 03 - Central | 515677 | BADGER 7 | 345 | 11694.8 | 11703 | 8.2
GEN-2018-030 | 03 - Central | 515686 | BLUWND 7 | 345 | 10654.4 | 10661.2 | 6.8
GEN-2018-030 | 03 - Central | 523093 | HITCHLAND 3 | 115 | 15884 | 15890.4 | 6.4
GEN-2018-030 | 03 - Central | 523095 | HITCHLAND 6 | 230 | 12511.8 | 12521.7 | 9.9
GEN-2018-030 | 03 - Central | 523097 | HITCHLAND 7 | 345 | 11395.5 | 11410.4 | 14.9
GEN-2018-030 | 03 - Central | 523101 | NOBLE_WND 7 | 345 | 11360 | 11374.9 | 14.9
GEN-2018-030 | 03 - Central | 523103 | NOBLE_WND 3 | 115 | 9170.5 | 9173.7 | 3.2
GEN-2018-030 | 03 - Central | 523111 | NOVUS1 3 | 115 | 6536.1 | 6537.8 | 1.7
GEN-2018-030 | 03 - Central | 523112 | NOVUS1 7 | 345 | 11212.8 | 11227.3 | 14.5
GEN-2018-030 | 03 - Central | 523118 | BUFF_DUNES 7 | 345 | 6819.7 | 6944.9 | 125.2
GEN-2018-030 | 03 - Central | 523130 | GRPLNS-HV4-3 | 115 | 6292.3 | 6293.8 | 1.5
GEN-2018-030 | 03 - Central | 523131 | GRPLNS-HV2-3 | 115 | 8416.3 | 8419 | 2.7
GEN-2018-030 | 03 - Central | 523155 | OCHILTREE 6 | 230 | 4144.7 | 4145.7 | 1
GEN-2018-030 | 03 - Central | 523174 | GOODWELLWND3 | 115 | 6644.5 | 6645.3 | 0.8
GEN-2018-030 | 03 - Central | 523215 | GEN-2011-022 | 345 | 8159.8 | 8167.4 | 7.6
GEN-2018-030 | 03 - Central | 523309 | MOORE_CNTY 6 | 230 | 6653.8 | 6654.7 | 0.9
GEN-2018-030 | 03 - Central | 523823 | CARPENTER 7 | 345 | 6506.3 | 6541.3 | 35
GEN-2018-030 | 03 - Central | 523853 | FINNEY 7 | 345 | 10503.1 | 10852.2 | 349.1
GEN-2018-030 | 03 - Central | 523959 | POTTER_CO 6 | 230 | 20016.9 | 20019.1 | 2.2
GEN-2018-030 | 03 - Central | 523961 | POTTER_CO 7 | 345 | 7349.4 | 7350.8 | 1.4
GEN-2018-030 | 03 - Central | 524296 | SPNSPUR_WND7 | 345 | 4159.8 | 4160.2 | 0.4
GEN-2018-030 | 03 - Central | 524299 | SPNSPUR_COL7 | 345 | 4159.8 | 4160.2 | 0.4
GEN-2018-030 | 03 - Central | 530583 | POSTROCK7 | 345 | 8301 | 8308.4 | 7.4
GEN-2018-030 | 03 - Central | 531210 | BLUEJAY3 | 115 | 2213.2 | 2214.6 | 1.4
GEN-2018-030 | 03 - Central | 531211 | CHRLSTN3 | 115 | 2149.4 | 2150.6 | 1.2
GEN-2018-030 | 03 - Central | 531212 | TWNSPRG3 | 115 | 1671.7 | 1672.5 | 0.8
GEN-2018-030 | 03 - Central | 531213 | SANTAFE3 | 115 | 2822.6 | 2824.8 | 2.2
GEN-2018-030 | 03 - Central | 531375 | PUCKET 3 | 115 | 5068.5 | 5074.8 | 6.3
GEN-2018-030 | 03 - Central | 531379 | JONES3 | 115 | 10963.8 | 11003.9 | 40.1
GEN-2018-030 | 03 - Central | 531384 | MOSCOW 2 | 69 | 2240.8 | 2241.5 | 0.7
GEN-2018-030 | 03 - Central | 531385 | MOSCOWT2 | 69 | 2357.2 | 2357.9 | 0.7
GEN-2018-030 | 03 - Central | 531388 | NORTH6 2 | 69 | 2651.6 | 2652.6 | 1
GEN-2018-030 | 03 - Central | 531389 | NORTH6T2 | 69 | 3102.4 | 3103.8 | 1.4
GEN-2018-030 | 03 - Central | 531392 | PIONTAP3 | 115 | 6982.7 | 6991.5 | 8.8
GEN-2018-030 | 03 - Central | 531393 | PLYMELL3 | 115 | 8011.3 | 8028.9 | 17.6
GEN-2018-030 | 03 - Central | 531398 | SUBLETE3 | 115 | 6234.3 | 6241.3 | 7
GEN-2018-030 | 03 - Central | 531400 | PK_GOAB3 | 115 | 5082.6 | 5088.9 | 6.3
GEN-2018-030 | 03 - Central | 531404 | WALKMYR2 | 69 | 8697 | 8707.6 | 10.6
GEN-2018-030 | 03 - Central | 531405 | WALKMYR3 | 115 | 10245.3 | 10270.1 | 24.8
GEN-2018-030 | 03 - Central | 531406 | WOODS 2 | 69 | 6389.8 | 6395.5 | 5.7
GEN-2018-030 | 03 - Central | 531407 | INGALLS3 | 115 | 2821.1 | 2823.3 | 2.2
GEN-2018-030 | 03 - Central | 531408 | PIERCVL3 | 115 | 4046.4 | 4050.9 | 4.5
GEN-2018-030 | 03 - Central | 531420 | FLETCHR3 | 115 | 7043.6 | 7058.7 | 15.1
GEN-2018-030 | 03 - Central | 531423 | GARDNCY2 | 69 | 3745.8 | 3748.1 | 2.3
GEN-2018-030 | 03 - Central | 531426 | JAMESON3 | 115 | 10406.1 | 10441.2 | 35.1
GEN-2018-030 | 03 - Central | 531429 | MINGO 3 | 115 | 12672.3 | 12708.9 | 36.6
GEN-2018-030 | 03 - Central | 531433 | SCOTCTY3 | 115 | 9116.7 | 9151.9 | 35.2
GEN-2018-030 | 03 - Central | 531440 | WILLIAM3 | 115 | 3931.5 | 3935.9 | 4.4
GEN-2018-030 | 03 - Central | 531445 | GRDNCTY3 | 115 | 12947.5 | 12994.1 | 46.6
GEN-2018-030 | 03 - Central | 531448 | HOLCOMB3 | 115 | 21636.9 | 21807.3 | 170.4
GEN-2018-030 | 03 - Central | 531449 | HOLCOMB7 | 345 | 10559.4 | 10906.3 | 346.9
GEN-2018-030 | 03 - Central | 531451 | MINGO 7 | 345 | 6466.7 | 6497.5 | 30.8
GEN-2018-030 | 03 - Central | 531464 | SETAB 3 | 115 | 10699 | 10751.2 | 52.2
GEN-2018-030 | 03 - Central | 531465 | SETAB 7 | 345 | 7279.7 | 7376.1 | 96.4
GEN-2018-030 | 03 - Central | 531469 | SPERVIL7 | 345 | 13480.1 | 13541.5 | 61.4
GEN-2018-030 | 03 - Central | 531476 | SWNDTAP3 | 115 | 7472.6 | 7488 | 15.4
GEN-2018-030 | 03 - Central | 531477 | S. WIND3 | 115 | 6886.6 | 6899.7 | 13.1
GEN-2018-030 | 03 - Central | 531480 | KSAVWTP3 | 115 | 12577.9 | 12622.2 | 44.3
GEN-2018-030 | 03 - Central | 531485 | CNTRLPL3 | 115 | 6185.4 | 6200.3 | 14.9
GEN-2018-030 | 03 - Central | 531501 | BUCKNER7 | 345 | 9896.3 | 10019.9 | 123.6
GEN-2018-030 | 03 - Central | 531502 | CIMRRN 7 | 345 | 7784.6 | 7860.9 | 76.3
GEN-2018-030 | 03 - Central | 531504 | CIMWD2 7 | 345 | 8082 | 8160.9 | 78.9
GEN-2018-030 | 03 - Central | 531510 | HARBNGR3 | 115 | 10855.8 | 10884.2 | 28.4
GEN-2018-030 | 03 - Central | 531512 | HARBNGR7 | 345 | 6487.8 | 6522.5 | 34.7
GEN-2018-030 | 03 - Central | 531623 | EASTFORK3 | 115 | 9856.4 | 9878.6 | 22.2
GEN-2018-030 | 03 - Central | 531632 | GEN-2015-065 | 345 | 5778.5 | 5802 | 23.5
GEN-2018-030 | 03 - Central | 539117 | SPRVILL-EHVB | 230 | 12349.4 | 12376.4 | 27
GEN-2018-030 | 03 - Central | 539695 | SPEARVL6 | 230 | 12644.2 | 12672.7 | 28.5
GEN-2018-030 | 03 - Central | 539759 | SPRVL 3 | 115 | 13079.1 | 13096.4 | 17.3
GEN-2018-030 | 03 - Central | 539800 | CLARKCOUNTY7 | 345 | 13280.4 | 13312.8 | 32.4
GEN-2018-030 | 03 - Central | 539803 | IRONWOOD7 | 345 | 12967 | 13021.6 | 54.6
GEN-2018-030 | 03 - Central | 539813 | TRANSFORMER | 345 | 11115.7 | 11138.1 | 22.4
GEN-2018-030 | 03 - Central | 539815 | IRONWOOD WF7 | 345 | 11695.5 | 11739.9 | 44.4
GEN-2018-030 | 03 - Central | 539840 | GEN-2011-008 | 345 | 11313.9 | 11335.7 | 21.8
GEN-2018-030 | 03 - Central | 539841 | G-2011-008-1 | 345 | 11313.9 | 11335.7 | 21.8
GEN-2018-030 | 03 - Central | 539855 | G-2011-008-2 | 345 | 9582.5 | 9597.7 | 15.2
GEN-2018-030 | 03 - Central | 539857 | G-2011-008-3 | 345 | 8821.7 | 8834.7 | 13
GEN-2018-030 | 03 - Central | 560577 | G06-44 | 115 | 6536.1 | 6537.8 | 1.7
GEN-2018-030 | 03 - Central | 576395 | GEN-2010-014 | 345 | 8159.8 | 8167.4 | 7.6
GEN-2018-030 | 03 - Central | 576397 | G10014G11022 | 345 | 8159.8 | 8167.4 | 7.6
GEN-2018-030 | 03 - Central | 579480 | GEN-2008-124 | 345 | 12549.3 | 12600.3 | 51
GEN-2018-030 | 03 - Central | 585190 | GEN-2015-082 | 345 | 6375 | 6377.4 | 2.4
GEN-2018-030 | 03 - Central | 599950 | LAMAR7 | 345 | 4187.3 | 4359.3 | 172
GEN-2018-030 | 03 - Central | 640325 | REDWILO3 | 345 | 6532.1 | 6540.9 | 8.8
GEN-2018-030 | 03 - Central | 762658 | GEN-2018-030 | 345 | Project Bus - Disconnected | 5613.6 | Project Bus - Disconnected
GEN-2018-030 | 03 - Central | 762662 | G18-030-TAP | 345 | 5987.6 | 6345.4 | 357.8
GEN-2018-031 | 03 - Central | 300044 | 7MCCRED | 345 | 19781.7 | 19782 | 0.3
GEN-2018-031 | 03 - Central | 300098 | 5MOCITYB2 | 161 | 19553.4 | 19561.6 | 8.2
GEN-2018-031 | 03 - Central | 345088 | 7MCCREDIE | 345 | 6978.7 | 6978.8 | 0.1
GEN-2018-031 | 03 - Central | 345408 | 7OVERTON | 345 | 13508.4 | 13508.8 | 0.4
GEN-2018-031 | 03 - Central | 345409 | 5OVERTON | 161 | 21624.9 | 21625.2 | 0.3
GEN-2018-031 | 03 - Central | 532772 | STRANGR7 | 345 | 28512.8 | 28517.3 | 4.5
GEN-2018-031 | 03 - Central | 541144 | NASHUA_CAP5 | 161 | 29022.5 | 29034.4 | 11.9
GEN-2018-031 | 03 - Central | 541145 | RNRIDGE_CAP5 | 161 | 21821.5 | 21828.7 | 7.2
GEN-2018-031 | 03 - Central | 541197 | MULLNCR7 | 345 | 11103.3 | 11103.7 | 0.4
GEN-2018-031 | 03 - Central | 541198 | PECULR 7 | 345 | 21277.5 | 21282.2 | 4.7
GEN-2018-031 | 03 - Central | 541199 | ST JOE 7 | 345 | 20995.5 | 20998.6 | 3.1
GEN-2018-031 | 03 - Central | 541200 | PHILL 7 | 345 | 19303.3 | 19308.1 | 4.8
GEN-2018-031 | 03 - Central | 541201 | SIBLEY 7 | 345 | 21889.3 | 21901 | 11.7
GEN-2018-031 | 03 - Central | 541202 | SIBLEY 5 | 161 | 27664.3 | 27675.6 | 11.3
GEN-2018-031 | 03 - Central | 541203 | NASHUA 5 | 161 | 34879.5 | 34896.8 | 17.3
GEN-2018-031 | 03 - Central | 541224 | LNGVW 5 | 161 | 23559.5 | 23563.4 | 3.9
GEN-2018-031 | 03 - Central | 541225 | PHILL 5 | 161 | 35557.2 | 35562.7 | 5.5
GEN-2018-031 | 03 - Central | 541230 | RNRIDGE5 | 161 | 24976.3 | 24985.8 | 9.5
GEN-2018-031 | 03 - Central | 541248 | LBRTYST5 | 161 | 19590.6 | 19604.6 | 14
GEN-2018-031 | 03 - Central | 541250 | SIBLEYPL | 161 | 29286.9 | 29300 | 13.1
GEN-2018-031 | 03 - Central | 541282 | LNGVW 2 | 69 | 10695.5 | 10696.2 | 0.7
GEN-2018-031 | 03 - Central | 541283 | BRMALL 2 | 69 | 15541.3 | 15545.6 | 4.3
GEN-2018-031 | 03 - Central | 541284 | GRDVWTP2 | 69 | 9503.8 | 9504.2 | 0.4
GEN-2018-031 | 03 - Central | 541350 | IATAN5 | 161 | 15678.9 | 15680.2 | 1.3
GEN-2018-031 | 03 - Central | 541400 | EASTOWN7 | 345 | 19336.7 | 19339.3 | 2.6
GEN-2018-031 | 03 - Central | 541411 | MC REAC1 | 345 | 10444.7 | 10445 | 0.3
GEN-2018-031 | 03 - Central | 541412 | MC REAC2 | 345 | 10444.7 | 10445 | 0.3
GEN-2018-031 | 03 - Central | 541413 | MC REAC3 | 345 | 10444.7 | 10445 | 0.3
GEN-2018-031 | 03 - Central | 541414 | SIB REA1 | 345 | 19470.2 | 19479.5 | 9.3
GEN-2018-031 | 03 - Central | 541500 | KETCHEM7 | 345 | 9152.2 | 9152.9 | 0.7
GEN-2018-031 | 03 - Central | 541501 | OSBORN7 | 345 | 8040.6 | 8041.1 | 0.5
GEN-2018-031 | 03 - Central | 542946 | GLADSTN_CAP5 | 161 | 17343.5 | 17351.8 | 8.3
GEN-2018-031 | 03 - Central | 542948 | NEASTS_CAP5 | 161 | 37835.7 | 37878.1 | 42.4
GEN-2018-031 | 03 - Central | 542950 | STHTOWN_CAP5 | 161 | 31138.7 | 31154.8 | 16.1
GEN-2018-031 | 03 - Central | 542972 | HAWTH 7 | 345 | 23841.9 | 23869.1 | 27.2
GEN-2018-031 | 03 - Central | 542973 | HAWTHS5 | 161 | 59821.8 | 60011.6 | 189.8
GEN-2018-031 | 03 - Central | 542976 | LEVEE 5 | 161 | 54003.8 | 54153.4 | 149.6
GEN-2018-031 | 03 - Central | 542980 | NASHUA 7 | 345 | 24166 | 24179.9 | 13.9
GEN-2018-031 | 03 - Central | 542982 | IATAN 7 | 345 | 31748.1 | 31754.6 | 6.5
GEN-2018-031 | 03 - Central | 542985 | NEASTS5 | 161 | 48442 | 48511.6 | 69.6
GEN-2018-031 | 03 - Central | 542986 | TROOST 5 | 161 | 34620.7 | 34648.1 | 27.4
GEN-2018-031 | 03 - Central | 542987 | GRAND 5 | 161 | 44255.6 | 44307.1 | 51.5
GEN-2018-031 | 03 - Central | 542988 | GRAND W5 | 161 | 44672.4 | 44724.8 | 52.4
GEN-2018-031 | 03 - Central | 542989 | NAVY 5 | 161 | 44610 | 44662.1 | 52.1
GEN-2018-031 | 03 - Central | 542990 | CROSTWN5 | 161 | 40279.5 | 40320.6 | 41.1
GEN-2018-031 | 03 - Central | 542993 | STHTOWN5 | 161 | 37985.7 | 38009.6 | 23.9
GEN-2018-031 | 03 - Central | 542996 | MIDTOWN5 | 161 | 36286.7 | 36312.5 | 25.8
GEN-2018-031 | 03 - Central | 542997 | LEEDS 5 | 161 | 36069.9 | 36115.4 | 45.5
GEN-2018-031 | 03 - Central | 542998 | LVISTA 5 | 161 | 24791.5 | 24804.5 | 13
GEN-2018-031 | 03 - Central | 543000 | BLUEVLY5 | 161 | 40043.2 | 40243.9 | 200.7
GEN-2018-031 | 03 - Central | 543001 | FOREST 5 | 161 | 32444.9 | 32464.4 | 19.5
GEN-2018-031 | 03 - Central | 543004 | BLUMILS5 | 161 | 17499.6 | 17507.5 | 7.9
GEN-2018-031 | 03 - Central | 543006 | SWOPE N5 | 161 | 22350.6 | 22364.5 | 13.9
GEN-2018-031 | 03 - Central | 543007 | SWOPE S5 | 161 | 22388.6 | 22402.2 | 13.6
GEN-2018-031 | 03 - Central | 543009 | WINJT N5 | 161 | 24391.3 | 24407.8 | 16.5
GEN-2018-031 | 03 - Central | 543010 | WINJT S5 | 161 | 23989.9 | 24005.6 | 15.7
GEN-2018-031 | 03 - Central | 543011 | CHOUTEU5 | 161 | 37572 | 37626.7 | 54.7
GEN-2018-031 | 03 - Central | 543015 | AVONDAL5 | 161 | 30907.3 | 30941.2 | 33.9
GEN-2018-031 | 03 - Central | 543016 | GLADSTN5 | 161 | 19279 | 19289.2 | 10.2
GEN-2018-031 | 03 - Central | 543018 | NKANCTY5 | 161 | 35285.2 | 35324.5 | 39.3
GEN-2018-031 | 03 - Central | 543020 | BRMGHAM5 | 161 | 27340 | 27373.9 | 33.9
GEN-2018-031 | 03 - Central | 543021 | RIVRSID5 | 161 | 19588.9 | 19598 | 9.1
GEN-2018-031 | 03 - Central | 543022 | CLAYCM15 | 161 | 11833.4 | 11836.5 | 3.1
GEN-2018-031 | 03 - Central | 543023 | CLAYCM25 | 161 | 14013.7 | 14022.6 | 8.9
GEN-2018-031 | 03 - Central | 543025 | LINECRK5 | 161 | 17857.6 | 17864.2 | 6.6
GEN-2018-031 | 03 - Central | 543027 | RANDLPH5 | 161 | 34333.8 | 34387.8 | 54
GEN-2018-031 | 03 - Central | 543028 | NASHUA-5 | 161 | 35087.2 | 35104.6 | 17.4
GEN-2018-031 | 03 - Central | 543029 | SHOLCRK5 | 161 | 18726.8 | 18734.5 | 7.7
GEN-2018-031 | 03 - Central | 543040 | ROEPARK5 | 161 | 31078.7 | 31095.5 | 16.8
GEN-2018-031 | 03 - Central | 543080 | HAWTH 2 | 69 | 13910.5 | 13913.5 | 3
GEN-2018-031 | 03 - Central | 543095 | LIBRTYS2 | 69 | 12492.6 | 12494.7 | 2.1
GEN-2018-031 | 03 - Central | 543116 | BLUEMLS2 | 69 | 7668.7 | 7669.3 | 0.6
GEN-2018-031 | 03 - Central | 543129 | HAWTHS_G65 | 161 | 58962.2 | 59146.4 | 184.2
GEN-2018-031 | 03 - Central | 543130 | HAWTHS_XF5 | 161 | 58900.1 | 59084.1 | 184
GEN-2018-031 | 03 - Central | 543133 | CHARLOT5 | 161 | 35491.6 | 35523.5 | 31.9
GEN-2018-031 | 03 - Central | 543663 | HAWT11_2 | 69 | 13910.5 | 13913.5 | 3
GEN-2018-031 | 03 - Central | 543664 | HAWT12_2 | 69 | 13910.5 | 13913.5 | 3
GEN-2018-031 | 03 - Central | 543665 | HAWTHN5 | 161 | 60516.1 | 60714.1 | 198
GEN-2018-031 | 03 - Central | 543666 | NEASTN5 | 161 | 48859.9 | 48930.7 | 70.8
GEN-2018-031 | 03 - Central | 548800 | SUB I | 69 | 19193.7 | 19198.6 | 4.9
GEN-2018-031 | 03 - Central | 548802 | SUB H | 69 | 22346 | 22352.2 | 6.2
GEN-2018-031 | 03 - Central | 548803 | SUB F | 69 | 15440.8 | 15444.5 | 3.7
GEN-2018-031 | 03 - Central | 548804 | SUB E | 69 | 16209.8 | 16214.6 | 4.8
GEN-2018-031 | 03 - Central | 548806 | BLUVLY | 69 | 23913 | 23920.1 | 7.1
GEN-2018-031 | 03 - Central | 548807 | BLUVLY-161 | 161 | 18493.9 | 18504.9 | 11
GEN-2018-031 | 03 - Central | 548809 | SHRNKRD | 69 | 18873.3 | 18878 | 4.7
GEN-2018-031 | 03 - Central | 548811 | SUB J | 69 | 18539.1 | 18543.2 | 4.1
GEN-2018-031 | 03 - Central | 548814 | SUB M-161 | 161 | 21189.6 | 21207.1 | 17.5
GEN-2018-031 | 03 - Central | 548815 | SUB M | 69 | 22935.4 | 22942 | 6.6
GEN-2018-031 | 03 - Central | 548820 | SUB N-161 | 161 | 17191.7 | 17225.5 | 33.8
GEN-2018-031 | 03 - Central | 548821 | SUB N | 69 | 18115.6 | 18121.7 | 6.1
GEN-2018-031 | 03 - Central | 548825 | SUB C | 69 | 16389.5 | 16393.5 | 4
GEN-2018-031 | 03 - Central | 548826 | STRLNGRD | 69 | 16601.4 | 16606.1 | 4.7
GEN-2018-031 | 03 - Central | 548832 | KCPL JCT | 69 | 14433.6 | 14436.9 | 3.3
GEN-2018-031 | 03 - Central | 588240 | GEN-2016-149 | 345 | 9126.8 | 9127.1 | 0.3
GEN-2018-031 | 03 - Central | 588250 | GEN-2016-174 | 345 | 5930 | 5930.1 | 0.1
GEN-2018-031 | 03 - Central | 588260 | GEN-2016-176 | 345 | 4804.3 | 4804.3 | 0
GEN-2018-031 | 03 - Central | 588270 | GEN-2016-150 | 345 | 3571.9 | 3572 | 0.1
GEN-2018-031 | 03 - Central | 761376 | GEN-2017-183 | 345 | 8876.4 | 8877.5 | 1.1
GEN-2018-031 | 03 - Central | 761383 | G17-183-TAP | 345 | 17954.2 | 17959.1 | 4.9
GEN-2018-031 | 03 - Central | 762581 | GEN-2018-022 | 345 | 8994.5 | 8994.7 | 0.2
GEN-2018-031 | 03 - Central | 762669 | GEN-2018-031 | 161 | Project Bus - Disconnected | 40234.1 | Project Bus - Disconnected
GEN-2018-031 | 03 - Central | 992001 | VSC2_1 | 276 | 5878 | 5878 | 0
GEN-2018-031 | 03 - Central | 992002 | VSC2_2 | 276 | 5878 | 5878 | 0
GEN-2018-031 | 03 - Central | 992003 | VSC2_3 | 345 | 7351.7 | 7351.7 | 0
GEN-2018-031 | 03 - Central | 992005 | VSC2_5 | 276 | 5878 | 5878 | 0
GEN-2018-031 | 03 - Central | 992006 | VSC2_6 | 276 | 5878 | 5878 | 0
GEN-2018-032 | 03 - Central | 300045 | 7MORGAN | 345 | 13497.2 | 13497.2 | 0
GEN-2018-032 | 03 - Central | 300069 | 5CHOTEAU1 | 161 | 42631.9 | 42631.9 | 0
GEN-2018-032 | 03 - Central | 300070 | 5CLARK | 161 | 8292.1 | 8292.1 | 0
GEN-2018-032 | 03 - Central | 300651 | 2LAMR | 69 | 10162.5 | 10162.5 | 0
GEN-2018-032 | 03 - Central | 300652 | 2LAMRCTS | 69 | 3950.3 | 3950.3 | 0
GEN-2018-032 | 03 - Central | 300685 | 2LAMARPT | 69 | 8576.9 | 8576.9 | 0
GEN-2018-032 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 15925.7 | 15925.8 | 0.1
GEN-2018-032 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24813.6 | 24813.6 | 0
GEN-2018-032 | 03 - Central | 300741 | 5SPORTSMAN | 161 | 41040.8 | 41040.8 | 0
GEN-2018-032 | 03 - Central | 300794 | 5LAMAR | 161 | 8973.2 | 8973.2 | 0
GEN-2018-032 | 03 - Central | 300949 | 7JASPER | 345 | 13033 | 13033.1 | 0.1
GEN-2018-032 | 03 - Central | 300950 | 5JASPER | 161 | 13113.3 | 13113.3 | 0
GEN-2018-032 | 03 - Central | 301348 | 5CHOTEAU2 | 161 | 42631.9 | 42631.9 | 0
GEN-2018-032 | 03 - Central | 506935 | FLINTCR7 | 345 | 15854.5 | 15854.5 | 0
GEN-2018-032 | 03 - Central | 506945 | CHAMSPR7 | 345 | 10603.1 | 10603.1 | 0
GEN-2018-032 | 03 - Central | 509721 | BA.NO-S4 | 138 | 12699.8 | 12699.8 | 0
GEN-2018-032 | 03 - Central | 509737 | BA101 S4 | 138 | 18733.5 | 18733.5 | 0
GEN-2018-032 | 03 - Central | 509743 | DENVR-E4 | 138 | 8307.1 | 8307.1 | 0
GEN-2018-032 | 03 - Central | 509745 | CLARKSV7 | 345 | 20644.2 | 20644.2 | 0
GEN-2018-032 | 03 - Central | 509746 | DENVTAP4 | 138 | 9743 | 9743 | 0
GEN-2018-032 | 03 - Central | 509755 | WEKIWA-7 | 345 | 22520.2 | 22520.2 | 0
GEN-2018-032 | 03 - Central | 509757 | WEKIWA-4 | 138 | 33818.2 | 33818.2 | 0
GEN-2018-032 | 03 - Central | 509768 | BA101ST4 | 138 | 19438 | 19438 | 0
GEN-2018-032 | 03 - Central | 509769 | BA101-N4 | 138 | 20328.1 | 20328.1 | 0
GEN-2018-032 | 03 - Central | 509773 | RSS T1 4 | 138 | 52866.8 | 52866.8 | 0
GEN-2018-032 | 03 - Central | 509782 | R.S.S.-7 | 345 | 31049.2 | 31049.2 | 0
GEN-2018-032 | 03 - Central | 509786 | BA.N-ST4 | 138 | 24737.2 | 24737.2 | 0
GEN-2018-032 | 03 - Central | 509806 | ONETA--4 | 138 | 51405.4 | 51405.4 | 0
GEN-2018-032 | 03 - Central | 509807 | ONETA--7 | 345 | 29784.4 | 29784.4 | 0
GEN-2018-032 | 03 - Central | 509817 | T.NO.--4 | 138 | 35927.5 | 35927.5 | 0
GEN-2018-032 | 03 - Central | 509822 | W.ED.-E4 | 138 | 8139.7 | 8139.7 | 0
GEN-2018-032 | 03 - Central | 509834 | COGENT 7 | 345 | 28975.9 | 28975.9 | 0
GEN-2018-032 | 03 - Central | 509836 | OEC 7 | 345 | 29508.3 | 29508.3 | 0
GEN-2018-032 | 03 - Central | 509852 | T.NO.--7 | 345 | 24442.3 | 24442.3 | 0
GEN-2018-032 | 03 - Central | 509869 | 121LYNN4 | 138 | 18327.4 | 18327.4 | 0
GEN-2018-032 | 03 - Central | 509870 | SAPLPRD7 | 345 | 22845.6 | 22845.6 | 0
GEN-2018-032 | 03 - Central | 509875 | RSS T2 4 | 138 | 53810.2 | 53810.2 | 0
GEN-2018-032 | 03 - Central | 509891 | BA_71ST4 | 138 | 24083.7 | 24083.7 | 0
GEN-2018-032 | 03 - Central | 509895 | T.NO.2-4 | 138 | 35868.9 | 35868.9 | 0
GEN-2018-032 | 03 - Central | 510378 | SCOFCTY4 | 138 | 9023.5 | 9023.6 | 0.1
GEN-2018-032 | 03 - Central | 510379 | DELWARE4 | 138 | 11588.3 | 11588.3 | 0
GEN-2018-032 | 03 - Central | 510380 | DELWARE7 | 345 | 12180.6 | 12180.7 | 0.1
GEN-2018-032 | 03 - Central | 510406 | N.E.S.-7 | 345 | 19681.2 | 19681.2 | 0
GEN-2018-032 | 03 - Central | 510420 | SCOFFEYV4 | 138 | 8620.2 | 8620.2 | 0
GEN-2018-032 | 03 - Central | 510422 | COFFEYT4 | 138 | 10384.7 | 10384.7 | 0
GEN-2018-032 | 03 - Central | 512631 | MIAMI 5 | 161 | 9732.2 | 9732.2 | 0
GEN-2018-032 | 03 - Central | 512648 | MAID 5 | 161 | 44894.8 | 44894.8 | 0
GEN-2018-032 | 03 - Central | 512650 | GRDA1 7 | 345 | 27261.9 | 27261.9 | 0
GEN-2018-032 | 03 - Central | 512651 | CLARMR 5 | 161 | 13223.2 | 13223.2 | 0
GEN-2018-032 | 03 - Central | 512656 | GRDA1 5 | 161 | 44439.3 | 44439.3 | 0
GEN-2018-032 | 03 - Central | 512694 | CLEVLND7 | 345 | 15092.6 | 15092.6 | 0
GEN-2018-032 | 03 - Central | 512700 | WAGNOR 5 | 161 | 9949.6 | 9949.6 | 0
GEN-2018-032 | 03 - Central | 512727 | GRDA1 2 | 69 | 12541.5 | 12541.5 | 0
GEN-2018-032 | 03 - Central | 512728 | ARKLIN2 | 69 | 3839 | 3839 | 0
GEN-2018-032 | 03 - Central | 512729 | CLEVLND 4 | 138 | 17240.4 | 17240.4 | 0
GEN-2018-032 | 03 - Central | 512734 | FARML 4 | 138 | 8715.1 | 8715.1 | 0
GEN-2018-032 | 03 - Central | 512735 | COFCTY2 | 69 | 9902.7 | 9902.7 | 0
GEN-2018-032 | 03 - Central | 512742 | WMAIN ST5 | 161 | 28231.4 | 28231.4 | 0
GEN-2018-032 | 03 - Central | 512745 | SSLINC2 | 69 | 2887.4 | 2887.4 | 0
GEN-2018-032 | 03 - Central | 512746 | SSNORT2 | 69 | 2943.6 | 2943.6 | 0
GEN-2018-032 | 03 - Central | 512747 | SSNEWN2 | 69 | 3192.9 | 3192.9 | 0
GEN-2018-032 | 03 - Central | 512750 | TONECE7 | 345 | 15616.7 | 15616.7 | 0
GEN-2018-032 | 03 - Central | 512751 | TONECE5 | 161 | 15628.7 | 15628.8 | 0.1
GEN-2018-032 | 03 - Central | 512753 | TONNEC2 | 69 | 4962.3 | 4962.3 | 0
GEN-2018-032 | 03 - Central | 512756 | TONECESTR2 | 69 | 3953 | 3953 | 0
GEN-2018-032 | 03 - Central | 512865 | GREC TAP5 | 345 | 26047.9 | 26048 | 0.1
GEN-2018-032 | 03 - Central | 513590 | CUSTDAY1 5 | 161 | 16885 | 16885 | 0
GEN-2018-032 | 03 - Central | 513591 | HERRON 5 | 161 | 17304.5 | 17304.5 | 0
GEN-2018-032 | 03 - Central | 513593 | IGLOOV1 5 | 161 | 17502.6 | 17502.6 | 0
GEN-2018-032 | 03 - Central | 513595 | IGLOOV2 5 | 161 | 17502.6 | 17502.6 | 0
GEN-2018-032 | 03 - Central | 513596 | IGLOOV 7 | 345 | 20657.7 | 20657.7 | 0
GEN-2018-032 | 03 - Central | 514803 | SOONER 7 | 345 | 25946 | 25946.1 | 0.1
GEN-2018-032 | 03 - Central | 514825 | KAYWIND7 | 345 | 12118.9 | 12118.9 | 0
GEN-2018-032 | 03 - Central | 514909 | REDBUD 7 | 345 | 27060.8 | 27060.8 | 0
GEN-2018-032 | 03 - Central | 515224 | MUSKOGE7 | 345 | 27636.1 | 27636.1 | 0
GEN-2018-032 | 03 - Central | 515235 | PECANCK7 | 345 | 22063.5 | 22063.5 | 0
GEN-2018-032 | 03 - Central | 515621 | OPENSKY7 | 345 | 12149.3 | 12149.3 | 0
GEN-2018-032 | 03 - Central | 515894 | THUNDER7 | 345 | 10501.4 | 10501.4 | 0
GEN-2018-032 | 03 - Central | 532768 | EMPEC 7 | 345 | 20003.1 | 20003.1 | 0
GEN-2018-032 | 03 - Central | 532771 | RENO 7 | 345 | 11834.8 | 11834.8 | 0
GEN-2018-032 | 03 - Central | 532774 | SWISVAL7 | 345 | 18597.4 | 18597.4 | 0
GEN-2018-032 | 03 - Central | 532775 | 87TH 7 | 345 | 22951.8 | 22951.8 | 0
GEN-2018-032 | 03 - Central | 532776 | READWF 7 | 345 | 16213.5 | 16213.5 | 0
GEN-2018-032 | 03 - Central | 532777 | G17-009-TAP | 345 | 12052.7 | 12052.9 | 0.2
GEN-2018-032 | 03 - Central | 532778 | GEN-2017-009 | 345 | 11156.4 | 11156.6 | 0.2
GEN-2018-032 | 03 - Central | 532780 | CANEYRV7 | 345 | 9833.1 | 9833.2 | 0.1
GEN-2018-032 | 03 - Central | 532781 | CANEYWF7 | 345 | 9556.5 | 9556.5 | 0
GEN-2018-032 | 03 - Central | 532782 | BUFFALO7 | 345 | 22486.8 | 22486.8 | 0
GEN-2018-032 | 03 - Central | 532783 | KINGMAN7 | 345 | 7360.5 | 7360.5 | 0
GEN-2018-032 | 03 - Central | 532784 | NINN1WF7 | 345 | 6126.1 | 6126.1 | 0
GEN-2018-032 | 03 - Central | 532785 | PRATTWF7 | 345 | 5079.2 | 5079.2 | 0
GEN-2018-032 | 03 - Central | 532790 | EXPED WF7 | 345 | 7204.2 | 7204.2 | 0
GEN-2018-032 | 03 - Central | 532791 | BENTON 7 | 345 | 19834.3 | 19834.3 | 0
GEN-2018-032 | 03 - Central | 532792 | FR2EAST7 | 345 | 7166.9 | 7166.9 | 0
GEN-2018-032 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18303.8 | 18304.4 | 0.6
GEN-2018-032 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19233 | 19233.1 | 0.1
GEN-2018-032 | 03 - Central | 532795 | FR2WEST7 | 345 | 5721.5 | 5721.5 | 0
GEN-2018-032 | 03 - Central | 532796 | WICHITA7 | 345 | 26332.6 | 26332.6 | 0
GEN-2018-032 | 03 - Central | 532797 | WOLFCRK7 | 345 | 18775 | 18775 | 0
GEN-2018-032 | 03 - Central | 532798 | VIOLA 7 | 345 | 14868.4 | 14868.4 | 0
GEN-2018-032 | 03 - Central | 532799 | WAVERLY7 | 345 | 16614.5 | 16614.5 | 0
GEN-2018-032 | 03 - Central | 532800 | LATHAMS7 | 345 | 10474 | 10474 | 0
GEN-2018-032 | 03 - Central | 532801 | ELKRVR17 | 345 | 9286.8 | 9286.8 | 0
GEN-2018-032 | 03 - Central | 532802 | WAVERTX7 | 345 | 13844.4 | 13844.4 | 0
GEN-2018-032 | 03 - Central | 532803 | EXPEDITION7 | 345 | 10661.2 | 10661.2 | 0
GEN-2018-032 | 03 - Central | 532856 | SWISVAL6 | 230 | 23044.8 | 23044.8 | 0
GEN-2018-032 | 03 - Central | 532926 | BAKER 2 | 69 | 5134.1 | 5134.1 | 0
GEN-2018-032 | 03 - Central | 532934 | MARMTNE5 | 161 | 8716.4 | 8716.4 | 0
GEN-2018-032 | 03 - Central | 532935 | MARMTNW5 | 161 | 8711.7 | 8711.7 | 0
GEN-2018-032 | 03 - Central | 532937 | NEOSHO 5 | 161 | 23835.9 | 23836.2 | 0.3
GEN-2018-032 | 03 - Central | 532938 | FRANKLIN5 | 161 | 8106.1 | 8106.1 | 0
GEN-2018-032 | 03 - Central | 532986 | BENTON 4 | 138 | 28964.8 | 28964.9 | 0.1
GEN-2018-032 | 03 - Central | 532988 | BELAIRE4 | 138 | 19545.4 | 19545.4 | 0
GEN-2018-032 | 03 - Central | 532990 | MIDIAN 4 | 138 | 11367 | 11367 | 0
GEN-2018-032 | 03 - Central | 532991 | WEAVER 4 | 138 | 22762.8 | 22762.8 | 0
GEN-2018-032 | 03 - Central | 532994 | TCBURNS4 | 138 | 4148.8 | 4148.8 | 0
GEN-2018-032 | 03 - Central | 533001 | ALTOONA4 | 138 | 9430.4 | 9430.4 | 0
GEN-2018-032 | 03 - Central | 533002 | DEARING4 | 138 | 9716.2 | 9716.2 | 0
GEN-2018-032 | 03 - Central | 533003 | LIBERTY4 | 138 | 7657.4 | 7657.4 | 0
GEN-2018-032 | 03 - Central | 533005 | NEPARSN4 | 138 | 13175.8 | 13175.9 | 0.1
GEN-2018-032 | 03 - Central | 533008 | TV1MNDV4 | 138 | 7288.5 | 7288.5 | 0
GEN-2018-032 | 03 - Central | 533020 | NEOSHOS4 | 138 | 25449.1 | 25449.4 | 0.3
GEN-2018-032 | 03 - Central | 533021 | NEOSHO 4 | 138 | 25492.4 | 25492.7 | 0.3
GEN-2018-032 | 03 - Central | 533022 | NEOSHON4 | 138 | 25373.1 | 25373.4 | 0.3
GEN-2018-032 | 03 - Central | 533024 | 29TH 4 | 138 | 20205.2 | 20205.2 | 0
GEN-2018-032 | 03 - Central | 533039 | ELPASO 4 | 138 | 25514.4 | 25514.5 | 0.1
GEN-2018-032 | 03 - Central | 533040 | EVANS N4 | 138 | 34015.8 | 34015.8 | 0
GEN-2018-032 | 03 - Central | 533052 | PARKCTY4 | 138 | 20967.9 | 20967.9 | 0
GEN-2018-032 | 03 - Central | 533062 | ROSEHIL4 | 138 | 31870.5 | 31870.5 | 0
GEN-2018-032 | 03 - Central | 533068 | STEARMN4 | 138 | 20072.4 | 20072.4 | 0
GEN-2018-032 | 03 - Central | 533624 | BURLING2 | 69 | 3548.7 | 3548.7 | 0
GEN-2018-032 | 03 - Central | 533625 | BURLIND2 | 69 | 3163.5 | 3163.5 | 0
GEN-2018-032 | 03 - Central | 533626 | BURLJCT2 | 69 | 5158.1 | 5158.1 | 0
GEN-2018-032 | 03 - Central | 533628 | CC1BURL2 | 69 | 3547.2 | 3547.2 | 0
GEN-2018-032 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4822.5 | 4822.5 | 0
GEN-2018-032 | 03 - Central | 533630 | CC3WEST2 | 69 | 4763.7 | 4763.7 | 0
GEN-2018-032 | 03 - Central | 533639 | MARMATN2 | 69 | 9115.7 | 9115.7 | 0
GEN-2018-032 | 03 - Central | 533640 | MCKEE 2 | 69 | 4380.6 | 4380.6 | 0
GEN-2018-032 | 03 - Central | 533645 | SE9HIAT2 | 69 | 3889.9 | 3889.9 | 0
GEN-2018-032 | 03 - Central | 533647 | UN1ELSM2 | 69 | 8184 | 8184 | 0
GEN-2018-032 | 03 - Central | 533650 | UN8HUMB2 | 69 | 4564.4 | 4564.4 | 0
GEN-2018-032 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6235.9 | 6235.9 | 0
GEN-2018-032 | 03 - Central | 533654 | ZILAJCT2 | 69 | 6489.8 | 6489.8 | 0
GEN-2018-032 | 03 - Central | 533671 | ALTAMNT2 | 69 | 2934.3 | 2934.3 | 0
GEN-2018-032 | 03 - Central | 533672 | ALTAMNS2 | 69 | 4206.7 | 4206.7 | 0
GEN-2018-032 | 03 - Central | 533673 | ALTOO E2 | 69 | 4380.1 | 4380.1 | 0
GEN-2018-032 | 03 - Central | 533674 | ALTOO W2 | 69 | 3178.5 | 3178.5 | 0
GEN-2018-032 | 03 - Central | 533675 | ARGO 2 | 69 | 3102.1 | 3102.1 | 0
GEN-2018-032 | 03 - Central | 533692 | YELLOWJ2 | 69 | 1467.3 | 1467.3 | 0
GEN-2018-032 | 03 - Central | 533695 | LABETTE2 | 69 | 4219.5 | 4219.5 | 0
GEN-2018-032 | 03 - Central | 533696 | LABETTS2 | 69 | 6397.1 | 6397.2 | 0.1
GEN-2018-032 | 03 - Central | 533697 | LIBERT-2 | 69 | 8748.8 | 8748.8 | 0
GEN-2018-032 | 03 - Central | 533699 | NEODESH2 | 69 | 2785.9 | 2785.9 | 0
GEN-2018-032 | 03 - Central | 533700 | NEODJCT2 | 69 | 3769 | 3769 | 0
GEN-2018-032 | 03 - Central | 533701 | NEW ALB2 | 69 | 1557.1 | 1557.1 | 0
GEN-2018-032 | 03 - Central | 533702 | ORDNCE 2 | 69 | 6331.2 | 6331.2 | 0
GEN-2018-032 | 03 - Central | 533703 | ORDNJCT2 | 69 | 8770.1 | 8770.1 | 0
GEN-2018-032 | 03 - Central | 533704 | PARSONS2 | 69 | 5089.4 | 5089.4 | 0
GEN-2018-032 | 03 - Central | 533705 | STUDBKR2 | 69 | 1888 | 1888 | 0
GEN-2018-032 | 03 - Central | 533706 | RA5HIPR2 | 69 | 4377.9 | 4378 | 0.1
GEN-2018-032 | 03 - Central | 533707 | RA6BROO2 | 69 | 2674.3 | 2674.3 | 0
GEN-2018-032 | 03 - Central | 533758 | CRAWFOR2 | 69 | 7575.7 | 7575.7 | 0
GEN-2018-032 | 03 - Central | 533761 | GIRARD 2 | 69 | 4685.7 | 4685.7 | 0
GEN-2018-032 | 03 - Central | 533762 | GIR JCT2 | 69 | 6696.9 | 6697 | 0.1
GEN-2018-032 | 03 - Central | 533763 | HUDSON-2 | 69 | 4811.7 | 4811.7 | 0
GEN-2018-032 | 03 - Central | 533766 | LITCH S2 | 69 | 13179.9 | 13179.9 | 0
GEN-2018-032 | 03 - Central | 533768 | NEOSHON2 | 69 | 24030 | 24030.1 | 0.1
GEN-2018-032 | 03 - Central | 533772 | SE1GREE2 | 69 | 6317.4 | 6317.4 | 0
GEN-2018-032 | 03 - Central | 533773 | SOPITT 2 | 69 | 5756.6 | 5756.6 | 0
GEN-2018-032 | 03 - Central | 533778 | NEOSHOS2 | 69 | 24055.1 | 24055.2 | 0.1
GEN-2018-032 | 03 - Central | 541198 | PECULR 7 | 345 | 21282.2 | 21282.2 | 0
GEN-2018-032 | 03 - Central | 541200 | PHILL 7 | 345 | 19308.1 | 19308.1 | 0
GEN-2018-032 | 03 - Central | 541341 | S.HARP 5 | 161 | 21900.4 | 21900.4 | 0
GEN-2018-032 | 03 - Central | 541342 | PECULR 5 | 161 | 23790.3 | 23790.3 | 0
GEN-2018-032 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2677.1 | 2677.1 | 0
GEN-2018-032 | 03 - Central | 542945 | CRAIG_CAP 5 | 161 | 35978.4 | 35978.4 | 0
GEN-2018-032 | 03 - Central | 542965 | W.GRDNR7 | 345 | 29873.7 | 29873.7 | 0
GEN-2018-032 | 03 - Central | 542966 | WGARDNR5 | 161 | 30884.6 | 30884.6 | 0
GEN-2018-032 | 03 - Central | 542968 | STILWEL7 | 345 | 26612 | 26612 | 0
GEN-2018-032 | 03 - Central | 542969 | STILWEL5 | 161 | 41769.4 | 41769.4 | 0
GEN-2018-032 | 03 - Central | 542977 | CRAIG 7 | 345 | 24917.5 | 24917.5 | 0
GEN-2018-032 | 03 - Central | 542978 | CRAIG 5 | 161 | 45438 | 45438 | 0
GEN-2018-032 | 03 - Central | 542981 | LACYGNE7 | 345 | 27808.8 | 27808.9 | 0.1
GEN-2018-032 | 03 - Central | 542994 | HICKMAN5 | 161 | 20207 | 20207 | 0
GEN-2018-032 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31655.8 | 31655.8 | 0
GEN-2018-032 | 03 - Central | 543050 | ANTIOCH5 | 161 | 23501 | 23501 | 0
GEN-2018-032 | 03 - Central | 543053 | REDEL 5 | 161 | 25421.1 | 25421.1 | 0
GEN-2018-032 | 03 - Central | 543054 | CEDARNL5 | 161 | 10948.8 | 10948.8 | 0
GEN-2018-032 | 03 - Central | 543057 | BUCYRUS5 | 161 | 21254.1 | 21254.1 | 0
GEN-2018-032 | 03 - Central | 543058 | NLOUISB5 | 161 | 9375.3 | 9375.3 | 0
GEN-2018-032 | 03 - Central | 543065 | CNTRVIL5 | 161 | 6464.1 | 6464.1 | 0
GEN-2018-032 | 03 - Central | 543077 | PLSTVAL5 | 161 | 10578.2 | 10578.2 | 0
GEN-2018-032 | 03 - Central | 543105 | BULLCRK5 | 161 | 29911.3 | 29911.3 | 0
GEN-2018-032 | 03 - Central | 543126 | LACKMAN5 | 161 | 13942.9 | 13942.9 | 0
GEN-2018-032 | 03 - Central | 543132 | BNSF 5 | 161 | 22610.4 | 22610.4 | 0
GEN-2018-032 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27072.5 | 27072.5 | 0
GEN-2018-032 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27072.5 | 27072.5 | 0
GEN-2018-032 | 03 - Central | 543650 | DAKOTA_5 | 161 | 7724.6 | 7724.6 | 0
GEN-2018-032 | 03 - Central | 543651 | PRQN_WIND5 | 161 | 6777 | 6777 | 0
GEN-2018-032 | 03 - Central | 543659 | LACYGNE2 | 69 | 2816.1 | 2816.1 | 0
GEN-2018-032 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 673.5 | 673.5 | 0
GEN-2018-032 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 645 | 645 | 0
GEN-2018-032 | 03 - Central | 547409 | SCAM66 2 | 69 | 2554.4 | 2554.4 | 0
GEN-2018-032 | 03 - Central | 547411 | COL282 2 | 69 | 4709.3 | 4709.3 | 0
GEN-2018-032 | 03 - Central | 547412 | SEK225T2 | 69 | 3625.7 | 3625.7 | 0
GEN-2018-032 | 03 - Central | 547413 | SEK225 2 | 69 | 3578.3 | 3578.3 | 0
GEN-2018-032 | 03 - Central | 547414 | SMN425 2 | 69 | 2038.2 | 2038.2 | 0
GEN-2018-032 | 03 - Central | 547415 | SHR444 2 | 69 | 2811.5 | 2811.5 | 0
GEN-2018-032 | 03 - Central | 547416 | CHE299T2 | 69 | 1909.7 | 1909.7 | 0
GEN-2018-032 | 03 - Central | 547417 | CHE299 2 | 69 | 1829 | 1829 | 0
GEN-2018-032 | 03 - Central | 547418 | CHE300 2 | 69 | 1870.6 | 1870.6 | 0
GEN-2018-032 | 03 - Central | 547419 | TWN388 2 | 69 | 1817.2 | 1817.2 | 0
GEN-2018-032 | 03 - Central | 547420 | WEL186 2 | 69 | 1168.3 | 1168.3 | 0
GEN-2018-032 | 03 - Central | 547431 | WEB105 2 | 69 | 8171.8 | 8171.8 | 0
GEN-2018-032 | 03 - Central | 547455 | SCM66T 2 | 69 | 4530.9 | 4530.9 | 0
GEN-2018-032 | 03 - Central | 547459 | WWR477 | 161 | 23947 | 23947 | 0
GEN-2018-032 | 03 - Central | 547462 | SVRCK469 5 | 161 | 15069.9 | 15069.9 | 0
GEN-2018-032 | 03 - Central | 547466 | ATL109 5 | 161 | 16926.1 | 16926.1 | 0
GEN-2018-032 | 03 - Central | 547467 | ORO110 5 | 161 | 20730 | 20730.1 | 0.1
GEN-2018-032 | 03 - Central | 547469 | RIV4525 | 161 | 25570.5 | 25570.5 | 0
GEN-2018-032 | 03 - Central | 547470 | JOP145 5 | 161 | 20066 | 20066 | 0
GEN-2018-032 | 03 - Central | 547472 | TIP292 5 | 161 | 18507.4 | 18507.4 | 0
GEN-2018-032 | 03 - Central | 547477 | CJ 366 5 | 161 | 12940.4 | 12940.4 | 0
GEN-2018-032 | 03 - Central | 547483 | JOP389 5 | 161 | 21521 | 21521 | 0
GEN-2018-032 | 03 - Central | 547486 | HOC404 4 | 138 | 6786.5 | 6786.5 | 0
GEN-2018-032 | 03 - Central | 547487 | HOC404 5 | 161 | 13747.9 | 13747.9 | 0
GEN-2018-032 | 03 - Central | 547490 | FIR417 5 | 161 | 14966.4 | 14966.4 | 0
GEN-2018-032 | 03 - Central | 547494 | OAK432 5 | 161 | 18687.4 | 18687.4 | 0
GEN-2018-032 | 03 - Central | 547498 | STL439 5 | 161 | 26352.4 | 26352.4 | 0
GEN-2018-032 | 03 - Central | 547501 | RIV453 5 | 161 | 24172.9 | 24172.9 | 0
GEN-2018-032 | 03 - Central | 547502 | RIV167 5 | 161 | 23648.3 | 23648.3 | 0
GEN-2018-032 | 03 - Central | 547503 | RIV452T 5 | 161 | 25100 | 25100 | 0
GEN-2018-032 | 03 - Central | 547525 | JOP 59 2 | 69 | 20292.2 | 20292.2 | 0
GEN-2018-032 | 03 - Central | 547526 | JOP 64 2 | 69 | 19912 | 19912 | 0
GEN-2018-032 | 03 - Central | 547527 | WEB436 2 | 69 | 9763.1 | 9763.1 | 0
GEN-2018-032 | 03 - Central | 547530 | COL 94 2 | 69 | 6610.8 | 6610.8 | 0
GEN-2018-032 | 03 - Central | 547534 | ORO110 2 | 69 | 18505.2 | 18505.2 | 0
GEN-2018-032 | 03 - Central | 547539 | JOP145 2 | 69 | 21628.4 | 21628.4 | 0
GEN-2018-032 | 03 - Central | 547541 | RIV167 2 | 69 | 18188.7 | 18188.7 | 0
GEN-2018-032 | 03 - Central | 547551 | GAT258 2 | 69 | 14849.5 | 14849.5 | 0
GEN-2018-032 | 03 - Central | 547554 | BAX271 2 | 69 | 9752.6 | 9752.6 | 0
GEN-2018-032 | 03 - Central | 547555 | GAL278 2 | 69 | 13463.4 | 13463.4 | 0
GEN-2018-032 | 03 - Central | 547556 | OAK280 2 | 69 | 16364.3 | 16364.3 | 0
GEN-2018-032 | 03 - Central | 547574 | JOP341 2 | 69 | 18686.9 | 18686.9 | 0
GEN-2018-032 | 03 - Central | 547592 | JOP389 2 | 69 | 15832.6 | 15832.6 | 0
GEN-2018-032 | 03 - Central | 547601 | HOC404 2 | 69 | 9868.1 | 9868.2 | 0.1
GEN-2018-032 | 03 - Central | 547602 | RIV406 2 | 69 | 16121 | 16121 | 0
GEN-2018-032 | 03 - Central | 547608 | JOP430 2 | 69 | 16321.4 | 16321.4 | 0
GEN-2018-032 | 03 - Central | 547690 | GLF339 2 | 69 | 12222.9 | 12222.9 | 0
GEN-2018-032 | 03 - Central | 547728 | GAL278T | 69 | 13763.1 | 13763.1 | 0
GEN-2018-032 | 03 - Central | 547729 | BAX488 5 | 161 | 15502.7 | 15502.7 | 0
GEN-2018-032 | 03 - Central | 560053 | G15-052T | 345 | 13167.9 | 13167.9 | 0
GEN-2018-032 | 03 - Central | 560056 | G15-066T | 345 | 18287.8 | 18287.8 | 0
GEN-2018-032 | 03 - Central | 560389 | GEN-2010-055 | 138 | 33818.2 | 33818.2 | 0
GEN-2018-032 | 03 - Central | 562476 | G14-001-TAP | 345 | 11236.2 | 11236.2 | 0
GEN-2018-032 | 03 - Central | 578530 | FR3HV | 345 | 5239.7 | 5239.7 | 0
GEN-2018-032 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7668.3 | 7668.3 | 0
GEN-2018-032 | 03 - Central | 584900 | GEN-2015-052 | 345 | 13120.2 | 13120.2 | 0
GEN-2018-032 | 03 - Central | 585040 | GEN-2015-066 | 345 | 18117.3 | 18117.3 | 0
GEN-2018-032 | 03 - Central | 587500 | GEN-2016-073 | 345 | 16347.6 | 16347.6 | 0
GEN-2018-032 | 03 - Central | 588039 | G16133G16146 | 345 | 31049.2 | 31049.2 | 0
GEN-2018-032 | 03 - Central | 588040 | G16133_345GS | 345 | 16106.9 | 16106.9 | 0
GEN-2018-032 | 03 - Central | 588041 | G16133_765GS | 765 | 5318.8 | 5318.8 | 0
GEN-2018-032 | 03 - Central | 588043 | G16133_765MP | 765 | 2771.6 | 2771.6 | 0
GEN-2018-032 | 03 - Central | 588045 | G16133_765CS | 765 | 1724.3 | 1724.3 | 0
GEN-2018-032 | 03 - Central | 588046 | G16133_345CS | 345 | 3517.9 | 3517.9 | 0
GEN-2018-032 | 03 - Central | 588050 | ZONE-1 SUB | 345 | 3092.9 | 3092.9 | 0
GEN-2018-032 | 03 - Central | 588060 | ZONE-2 SUB | 345 | 3096.1 | 3096.1 | 0
GEN-2018-032 | 03 - Central | 588070 | ZONE-3 SUB | 345 | 3160 | 3160 | 0
GEN-2018-032 | 03 - Central | 588080 | ZONE-4 SUB | 345 | 3491.2 | 3491.2 | 0
GEN-2018-032 | 03 - Central | 588090 | ZONE-5 SUB | 345 | 3153 | 3153 | 0
GEN-2018-032 | 03 - Central | 588100 | ZONE-6 SUB | 345 | 3293.1 | 3293.1 | 0
GEN-2018-032 | 03 - Central | 588300 | GEN-2016-157 | 345 | 5235.9 | 5235.9 | 0
GEN-2018-032 | 03 - Central | 588310 | GEN-2016-158 | 345 | 4937.1 | 4937.1 | 0
GEN-2018-032 | 03 - Central | 588360 | GEN-2016-153 | 345 | 7592.2 | 7592.2 | 0
GEN-2018-032 | 03 - Central | 588364 | G16-153-TAP | 345 | 7935.5 | 7935.5 | 0
GEN-2018-032 | 03 - Central | 588500 | GEN-2017-005 | 161 | 7092.2 | 7092.2 | 0
GEN-2018-032 | 03 - Central | 588504 | G17-005-TAP | 161 | 7180.8 | 7180.8 | 0
GEN-2018-032 | 03 - Central | 588660 | GEN-2017-022 | 138 | 9032 | 9032 | 0
GEN-2018-032 | 03 - Central | 588664 | G17-022-TAP | 138 | 9397.3 | 9397.3 | 0
GEN-2018-032 | 03 - Central | 588990 | GEN-2017-061 | 161 | 22621.2 | 22621.2 | 0
GEN-2018-032 | 03 - Central | 589060 | GEN-2017-068 | 138 | 30796.9 | 30796.9 | 0
GEN-2018-032 | 03 - Central | 589240 | GEN-2017-086 | 345 | 14868.4 | 14868.4 | 0
GEN-2018-032 | 03 - Central | 709400 | GI94_POI | 345 | 12235.6 | 12235.7 | 0.1
GEN-2018-032 | 03 - Central | 709401 | GI94_SUB | 345 | 12155 | 12155 | 0
GEN-2018-032 | 03 - Central | 709500 | GI-95_POI | 345 | 11523.8 | 11523.8 | 0
GEN-2018-032 | 03 - Central | 709501 | GI-95_HV | 345 | 11523.8 | 11523.8 | 0
GEN-2018-032 | 03 - Central | 760284 | GEN-2017-220 | 345 | 22358.6 | 22358.6 | 0
GEN-2018-032 | 03 - Central | 760389 | GEN-2017-140 | 345 | 1208.6 | 1208.6 | 0
GEN-2018-032 | 03 - Central | 760393 | G17-140-BUS | 345 | 1201.2 | 1201.2 | 0
GEN-2018-032 | 03 - Central | 760620 | GEN-2017-179 | 138 | 7287.6 | 7287.6 | 0
GEN-2018-032 | 03 - Central | 760641 | GEN-2017-226 | 138 | 33823.4 | 33823.4 | 0
GEN-2018-032 | 03 - Central | 760893 | GEN-2017-148 | 161 | 4859.9 | 4859.9 | 0
GEN-2018-032 | 03 - Central | 760914 | GEN-2017-209 | 345 | 19312.6 | 19312.6 | 0
GEN-2018-032 | 03 - Central | 760921 | G17-209-TAP | 345 | 19820.6 | 19820.6 | 0
GEN-2018-032 | 03 - Central | 761334 | GEN-2017-155 | 345 | 12025 | 12025 | 0
GEN-2018-032 | 03 - Central | 761733 | GEN-2017-228 | 345 | 26424.6 | 26424.7 | 0.1
GEN-2018-032 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5675.6 | 5675.6 | 0
GEN-2018-032 | 03 - Central | 761922 | GEN-2017-128 | 345 | 4756.2 | 4756.2 | 0
GEN-2018-032 | 03 - Central | 761943 | GEN-2017-191 | 345 | 18546.4 | 18546.4 | 0
GEN-2018-032 | 03 - Central | 762006 | GEN-2017-111 | 161 | 14480.5 | 14480.5 | 0
GEN-2018-032 | 03 - Central | 762010 | G17-111-TAP | 161 | 14480.5 | 14480.5 | 0
GEN-2018-032 | 03 - Central | 762279 | GEN-2017-195 | 345 | 29788.3 | 29788.3 | 0
GEN-2018-032 | 03 - Central | 762405 | ASG-2018-010 | 161 | 10570.1 | 10570.1 | 0
GEN-2018-032 | 03 - Central | 762680 | GEN-2018-032 | 345 | Project Bus - Disconnected | 12044 | Project Bus - Disconnected
GEN-2018-032 | 03 - Central | 762687 | G18-032_DUMY | 345 | Project Bus - Disconnected | 18304.4 | Project Bus - Disconnected
GEN-2018-032 | 03 - Central | 762823 | GEN-2018-048 | 345 | 16675.5 | 16675.5 | 0
GEN-2018-032 | 03 - Central | 762922 | GEN-2018-057 | 138 | 18123.6 | 18123.6 | 0
GEN-2018-049 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 15925.6 | 15925.8 | 0.2
GEN-2018-049 | 03 - Central | 511553 | CHISHOLM7 | 345 | 10512.4 | 10514.3 | 1.9
GEN-2018-049 | 03 - Central | 511557 | CHISHOLM6 | 230 | 11686.6 | 11687.6 | 1
GEN-2018-049 | 03 - Central | 514771 | TANGIER2 | 69 | 3853.3 | 3853.4 | 0.1
GEN-2018-049 | 03 - Central | 514773 | NEWMAN 2 | 69 | 1622.8 | 1622.8 | 0
GEN-2018-049 | 03 - Central | 514775 | TANGRTP2 | 69 | 5009.2 | 5009.3 | 0.1
GEN-2018-049 | 03 - Central | 514776 | NEWGRTP2 | 69 | 5718.8 | 5719 | 0.2
GEN-2018-049 | 03 - Central | 514778 | CLEOCOR4 | 138 | 5792.8 | 5793.1 | 0.3
GEN-2018-049 | 03 - Central | 514779 | WDNITRO2 | 69 | 4996.5 | 4996.7 | 0.2
GEN-2018-049 | 03 - Central | 514781 | CEDARAV2 | 69 | 5971 | 5971.2 | 0.2
GEN-2018-049 | 03 - Central | 514782 | WODWRD 2 | 69 | 11422.7 | 11423.5 | 0.8
GEN-2018-049 | 03 - Central | 514785 | WOODWRD4 | 138 | 13581.1 | 13583.8 | 2.7
GEN-2018-049 | 03 - Central | 514788 | GLASMTN4 | 138 | 5189.9 | 5190.1 | 0.2
GEN-2018-049 | 03 - Central | 514792 | ALVAOGE2 | 69 | 7694.2 | 7695.4 | 1.2
GEN-2018-049 | 03 - Central | 514794 | KNOBHIL2 | 69 | 9034.5 | 9036.4 | 1.9
GEN-2018-049 | 03 - Central | 514795 | KNOBHIL4 | 138 | 9821.5 | 9827.8 | 6.3
GEN-2018-049 | 03 - Central | 514796 | IODINE-4 | 138 | 7667.8 | 7668.8 | 1
GEN-2018-049 | 03 - Central | 514880 | NORTWST7 | 345 | 32210.5 | 32214.6 | 4.1
GEN-2018-049 | 03 - Central | 514901 | CIMARON7 | 345 | 33757.1 | 33762 | 4.9
GEN-2018-049 | 03 - Central | 515363 | CENT 4 | 138 | 3263.9 | 3264 | 0.1
GEN-2018-049 | 03 - Central | 515375 | WWRDEHV7 | 345 | 19143 | 19173.1 | 30.1
GEN-2018-049 | 03 - Central | 515376 | WWRDEHV4 | 138 | 24484.9 | 24499.3 | 14.4
GEN-2018-049 | 03 - Central | 515394 | KEENAN 4 | 138 | 9179.9 | 9181.7 | 1.8
GEN-2018-049 | 03 - Central | 515398 | OUSPRT 4 | 138 | 9827.5 | 9829.7 | 2.2
GEN-2018-049 | 03 - Central | 515407 | TATONGA7 | 345 | 17451.3 | 17461.2 | 9.9
GEN-2018-049 | 03 - Central | 515425 | WWDPST 4 | 138 | 17980.1 | 17986.8 | 6.7
GEN-2018-049 | 03 - Central | 515448 | CRSRDSW7 | 345 | 12271.5 | 12276.3 | 4.8
GEN-2018-049 | 03 - Central | 515458 | BORDER 7 | 345 | 7640.6 | 7641.5 | 0.9
GEN-2018-049 | 03 - Central | 515476 | HUNTERS7 | 345 | 12372.5 | 12375 | 2.5
GEN-2018-049 | 03 - Central | 515477 | CHSHLMV7 | 345 | 12355 | 12357.5 | 2.5
GEN-2018-049 | 03 - Central | 515497 | MATHWSN7 | 345 | 31432.1 | 31438.7 | 6.6
GEN-2018-049 | 03 - Central | 515533 | REDCLFT4 | 138 | 6995.3 | 6996 | 0.7
GEN-2018-049 | 03 - Central | 515543 | RENFROW7 | 345 | 12247.5 | 12251.4 | 3.9
GEN-2018-049 | 03 - Central | 515544 | RENFROW4 | 138 | 14346.3 | 14348.6 | 2.3
GEN-2018-049 | 03 - Central | 515554 | BVRCNTY7 | 345 | 12015.8 | 12019.8 | 4
GEN-2018-049 | 03 - Central | 515560 | CZYCRVT2 | 69 | 3378.9 | 3379 | 0.1
GEN-2018-049 | 03 - Central | 515582 | SLNGWND7 | 345 | 8670.7 | 8673 | 2.3
GEN-2018-049 | 03 - Central | 515585 | MAMTHPW7 | 345 | 13875.7 | 13881.8 | 6.1
GEN-2018-049 | 03 - Central | 515590 | PALDR2W7 | 345 | 10851.8 | 10855 | 3.2
GEN-2018-049 | 03 - Central | 515599 | G07621119-20 | 345 | 11939 | 11950.8 | 11.8
GEN-2018-049 | 03 - Central | 515600 | KNGFSHR7 | 345 | 12243.7 | 12244.1 | 0.4
GEN-2018-049 | 03 - Central | 515605 | CANADN7 | 345 | 13312.6 | 13313.2 | 0.6
GEN-2018-049 | 03 - Central | 515610 | FSHRTAP7 | 345 | 18027.6 | 18028.7 | 1.1
GEN-2018-049 | 03 - Central | 515618 | BALKOW 7 | 345 | 10413.9 | 10416.9 | 3
GEN-2018-049 | 03 - Central | 515634 | PALDR1W7 | 345 | 9841.1 | 9843.6 | 2.5
GEN-2018-049 | 03 - Central | 515646 | GRNTWD 7 | 345 | 10866.6 | 10869.5 | 2.9
GEN-2018-049 | 03 - Central | 515677 | BADGER 7 | 345 | 11697.9 | 11703 | 5.1
GEN-2018-049 | 03 - Central | 515686 | BLUWND 7 | 345 | 10657 | 10661.2 | 4.2
GEN-2018-049 | 03 - Central | 515785 | WINDFRM4 | 138 | 20632.6 | 20635.5 | 2.9
GEN-2018-049 | 03 - Central | 515786 | FPLWIND4 | 138 | 7118.9 | 7119.2 | 0.3
GEN-2018-049 | 03 - Central | 515825 | GRTWSRN7 | 345 | 8721.7 | 8728 | 6.3
GEN-2018-049 | 03 - Central | 515852 | DGRASSE7 | 345 | 14585.4 | 14650.5 | 65.1
GEN-2018-049 | 03 - Central | 515853 | DGRASSE4 | 138 | 14849.7 | 14867.2 | 17.5
GEN-2018-049 | 03 - Central | 515863 | REDCLF 4 | 138 | 6980.3 | 6980.9 | 0.6
GEN-2018-049 | 03 - Central | 515875 | REDNGTN7 | 345 | 16324.7 | 16326.9 | 2.2
GEN-2018-049 | 03 - Central | 515877 | REDDIRT7 | 345 | 16320.9 | 16323 | 2.1
GEN-2018-049 | 03 - Central | 515951 | PERSIMN7 | 345 | 10458.8 | 10467.8 | 9
GEN-2018-049 | 03 - Central | 515961 | GUTHRIE7 | 345 | 11963.3 | 11975.1 | 11.8
GEN-2018-049 | 03 - Central | 516025 | SUNDANC4 | 138 | 3788.7 | 3788.8 | 0.1
GEN-2018-049 | 03 - Central | 520425 | PIC4 | 138 | 8354.2 | 8354.6 | 0.4
GEN-2018-049 | 03 - Central | 520430 | NOELSW 4 | 138 | 9886.4 | 9892.8 | 6.4
GEN-2018-049 | 03 - Central | 520436 | ROSEVLY4 | 138 | 11370.9 | 11380.6 | 9.7
GEN-2018-049 | 03 - Central | 520437 | SALTPLN4 | 138 | 6370.1 | 6372 | 1.9
GEN-2018-049 | 03 - Central | 520462 | ASPEN 4 | 138 | 20345.5 | 20348.3 | 2.8
GEN-2018-049 | 03 - Central | 520480 | CURTIS 2 | 69 | 4120.4 | 4120.4 | 0
GEN-2018-049 | 03 - Central | 520500 | BEARCAT4 | 138 | 14984.2 | 14985.7 | 1.5
GEN-2018-049 | 03 - Central | 520507 | CEDRDAL4 | 138 | 4794.6 | 4794.7 | 0.1
GEN-2018-049 | 03 - Central | 520553 | SEILING4 | 138 | 7042.4 | 7042.8 | 0.4
GEN-2018-049 | 03 - Central | 520601 | AVARD 4 | 138 | 6680.4 | 6683.8 | 3.4
GEN-2018-049 | 03 - Central | 520848 | CDRDLTP4 | 138 | 5958 | 5958.2 | 0.2
GEN-2018-049 | 03 - Central | 520920 | FTSUPLY4 | 138 | 5771.8 | 5772 | 0.2
GEN-2018-049 | 03 - Central | 520922 | SLEEPBR4 | 138 | 4622.3 | 4622.4 | 0.1
GEN-2018-049 | 03 - Central | 520957 | IODINE 4 | 138 | 8231.9 | 8232.3 | 0.4
GEN-2018-049 | 03 - Central | 520995 | MOORLND2 | 69 | 8960.3 | 8960.6 | 0.3
GEN-2018-049 | 03 - Central | 520999 | MOORLND4 | 138 | 21088.8 | 21091.9 | 3.1
GEN-2018-049 | 03 - Central | 521065 | TALOGA 4 | 138 | 7709.8 | 7710.3 | 0.5
GEN-2018-049 | 03 - Central | 521197 | CRTSJCT2 | 69 | 8548.5 | 8548.9 | 0.4
GEN-2018-049 | 03 - Central | 523118 | BUFF_DUNES 7 | 345 | 6943.9 | 6944.9 | 1
GEN-2018-049 | 03 - Central | 523853 | FINNEY 7 | 345 | 10849.3 | 10852.2 | 2.9
GEN-2018-049 | 03 - Central | 525832 | TUCO_INT 7 | 345 | 12763.1 | 12763.2 | 0.1
GEN-2018-049 | 03 - Central | 525850 | ELK_CT1 | 345 | 12640.3 | 12640.4 | 0.1
GEN-2018-049 | 03 - Central | 530558 | KNOLL N 6 | 230 | 11992.7 | 11995.3 | 2.6
GEN-2018-049 | 03 - Central | 530582 | S HAYS6 | 230 | 9824.2 | 9826 | 1.8
GEN-2018-049 | 03 - Central | 530583 | POSTROCK7 | 345 | 8306 | 8308.4 | 2.4
GEN-2018-049 | 03 - Central | 530584 | POSTROCK6 | 230 | 12105.9 | 12108.6 | 2.7
GEN-2018-049 | 03 - Central | 530610 | SHAYS_230 | 230 | 4418.9 | 4419.1 | 0.2
GEN-2018-049 | 03 - Central | 530680 | HEIZER 6 | 230 | 8497.5 | 8499.4 | 1.9
GEN-2018-049 | 03 - Central | 530702 | BUCKEYE_230 | 230 | 9077.9 | 9079.3 | 1.4
GEN-2018-049 | 03 - Central | 530720 | KNOLL S 6 | 230 | 11992.7 | 11995.3 | 2.6
GEN-2018-049 | 03 - Central | 531448 | HOLCOMB3 | 115 | 21805.7 | 21807.3 | 1.6
GEN-2018-049 | 03 - Central | 531449 | HOLCOMB7 | 345 | 10903.3 | 10906.3 | 3
GEN-2018-049 | 03 - Central | 531465 | SETAB 7 | 345 | 7375.2 | 7376.1 | 0.9
GEN-2018-049 | 03 - Central | 531469 | SPERVIL7 | 345 | 13521.1 | 13541.5 | 20.4
GEN-2018-049 | 03 - Central | 531501 | BUCKNER7 | 345 | 10014.3 | 10019.9 | 5.6
GEN-2018-049 | 03 - Central | 531502 | CIMRRN 7 | 345 | 7857.4 | 7860.9 | 3.5
GEN-2018-049 | 03 - Central | 531504 | CIMWD2 7 | 345 | 8157.3 | 8160.9 | 3.6
GEN-2018-049 | 03 - Central | 532768 | EMPEC 7 | 345 | 19998.6 | 20003.1 | 4.5
GEN-2018-049 | 03 - Central | 532769 | LANG 7 | 345 | 19731.7 | 19736.1 | 4.4
GEN-2018-049 | 03 - Central | 532770 | MORRIS 7 | 345 | 13777.4 | 13778.6 | 1.2
GEN-2018-049 | 03 - Central | 532771 | RENO 7 | 345 | 11829.2 | 11834.8 | 5.6
GEN-2018-049 | 03 - Central | 532773 | SUMMIT 7 | 345 | 11710.1 | 11712 | 1.9
GEN-2018-049 | 03 - Central | 532774 | SWISVAL7 | 345 | 18596.3 | 18597.4 | 1.1
GEN-2018-049 | 03 - Central | 532776 | READWF 7 | 345 | 16210.5 | 16213.5 | 3
GEN-2018-049 | 03 - Central | 532782 | BUFFALO7 | 345 | 22420.4 | 22486.8 | 66.4
GEN-2018-049 | 03 - Central | 532783 | KINGMAN7 | 345 | 7355.2 | 7360.5 | 5.3
GEN-2018-049 | 03 - Central | 532784 | NINN1WF7 | 345 | 6122.7 | 6126.1 | 3.4
GEN-2018-049 | 03 - Central | 532785 | PRATTWF7 | 345 | 5077 | 5079.2 | 2.2
GEN-2018-049 | 03 - Central | 532790 | EXPED WF7 | 345 | 7201.8 | 7204.2 | 2.4
GEN-2018-049 | 03 - Central | 532791 | BENTON 7 | 345 | 19818.6 | 19834.3 | 15.7
GEN-2018-049 | 03 - Central | 532792 | FR2EAST7 | 345 | 7165.1 | 7166.9 | 1.8
GEN-2018-049 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19224.1 | 19233.1 | 9
GEN-2018-049 | 03 - Central | 532795 | FR2WEST7 | 345 | 5720.5 | 5721.5 | 1
GEN-2018-049 | 03 - Central | 532796 | WICHITA7 | 345 | 26275.9 | 26332.6 | 56.7
GEN-2018-049 | 03 - Central | 532797 | WOLFCRK7 | 345 | 18773.5 | 18775 | 1.5
GEN-2018-049 | 03 - Central | 532798 | VIOLA 7 | 345 | 14858.4 | 14868.4 | 10
GEN-2018-049 | 03 - Central | 532799 | WAVERLY7 | 345 | 16613.5 | 16614.5 | 1
GEN-2018-049 | 03 - Central | 532800 | LATHAMS7 | 345 | 10472.4 | 10474 | 1.6
GEN-2018-049 | 03 - Central | 532801 | ELKRVR17 | 345 | 9285.6 | 9286.8 | 1.2
GEN-2018-049 | 03 - Central | 532802 | WAVERTX7 | 345 | 13843.6 | 13844.4 | 0.8
GEN-2018-049 | 03 - Central | 532803 | EXPEDITION7 | 345 | 10656 | 10661.2 | 5.2
GEN-2018-049 | 03 - Central | 532871 | CIRCLE 6 | 230 | 9081.8 | 9083.3 | 1.5
GEN-2018-049 | 03 - Central | 532984 | SUMNER 4 | 138 | 12053.4 | 12055 | 1.6
GEN-2018-049 | 03 - Central | 532986 | BENTON 4 | 138 | 28952 | 28964.9 | 12.9
GEN-2018-049 | 03 - Central | 532988 | BELAIRE4 | 138 | 19539.7 | 19545.4 | 5.7
GEN-2018-049 | 03 - Central | 532990 | MIDIAN 4 | 138 | 11365.4 | 11367 | 1.6
GEN-2018-049 | 03 - Central | 532994 | TCBURNS4 | 138 | 4148.6 | 4148.8 | 0.2
GEN-2018-049 | 03 - Central | 533015 | BENTLEY4 | 138 | 11198.4 | 11200.9 | 2.5
GEN-2018-049 | 03 - Central | 533016 | WWUPLNT4 | 138 | 8475.6 | 8477 | 1.4
GEN-2018-049 | 03 - Central | 533024 | 29TH 4 | 138 | 20199.1 | 20205.2 | 6.1
GEN-2018-049 | 03 - Central | 533035 | CHISHLM4 | 138 | 22207.1 | 22215.6 | 8.5
GEN-2018-049 | 03 - Central | 533036 | CLEARWT4 | 138 | 14699.8 | 14704 | 4.2
GEN-2018-049 | 03 - Central | 533040 | EVANS N4 | 138 | 33990.8 | 34015.8 | 25
GEN-2018-049 | 03 - Central | 533041 | EVANS S4 | 138 | 33904.9 | 33929.7 | 24.8
GEN-2018-049 | 03 - Central | 533047 | GILL 4 | 138 | 22634.7 | 22644.1 | 9.4
GEN-2018-049 | 03 - Central | 533052 | PARKCTY4 | 138 | 20960.6 | 20967.9 | 7.3
GEN-2018-049 | 03 - Central | 533053 | LAKERDG4 | 138 | 17910.8 | 17917.2 | 6.4
GEN-2018-049 | 03 - Central | 533054 | MAIZE 4 | 138 | 21802.6 | 21812 | 9.4
GEN-2018-049 | 03 - Central | 533062 | ROSEHIL4 | 138 | 31858.9 | 31870.5 | 11.6
GEN-2018-049 | 03 - Central | 533065 | SG12COL4 | 138 | 20320.5 | 20329.2 | 8.7
GEN-2018-049 | 03 - Central | 533074 | 45TH ST4 | 138 | 24808.3 | 24821.3 | 13
GEN-2018-049 | 03 - Central | 533075 | VIOLA 4 | 138 | 25275.6 | 25289.7 | 14.1
GEN-2018-049 | 03 - Central | 533413 | CIRCLE 3 | 115 | 19486.2 | 19490.5 | 4.3
GEN-2018-049 | 03 - Central | 533415 | DAVIS 3 | 115 | 8470.9 | 8471.8 | 0.9
GEN-2018-049 | 03 - Central | 533416 | RENO 3 | 115 | 23524.1 | 23530.7 | 6.6
GEN-2018-049 | 03 - Central | 533429 | MOUNDRG3 | 115 | 8849.9 | 8850.9 | 1
GEN-2018-049 | 03 - Central | 533430 | MNDRGCT3 | 115 | 6819.6 | 6820.2 | 0.6
GEN-2018-049 | 03 - Central | 533438 | WMCPHER3 | 115 | 11498.9 | 11499.9 | 1
GEN-2018-049 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4822.5 | 4822.5 | 0
GEN-2018-049 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6235.9 | 6235.9 | 0
GEN-2018-049 | 03 - Central | 539000 | RAGO 4 | 138 | 4139.8 | 4141.4 | 1.6
GEN-2018-049 | 03 - Central | 539001 | ANTHONY4 | 138 | 5256.5 | 5258.6 | 2.1
GEN-2018-049 | 03 - Central | 539002 | BLF-CRK4 | 138 | 4918.2 | 4919.6 | 1.4
GEN-2018-049 | 03 - Central | 539008 | MILAN_GOAB | 138 | 12246.4 | 12250.3 | 3.9
GEN-2018-049 | 03 - Central | 539009 | CONWAY | 138 | 11751.2 | 11755.6 | 4.4
GEN-2018-049 | 03 - Central | 539117 | SPRVILL-EHVB | 230 | 12367.2 | 12376.4 | 9.2
GEN-2018-049 | 03 - Central | 539628 | NW-DGTP3 | 115 | 3534.4 | 3534.7 | 0.3
GEN-2018-049 | 03 - Central | 539631 | FLATRWD4 | 138 | 10848.5 | 10873.4 | 24.9
GEN-2018-049 | 03 - Central | 539638 | FLATRDG4 | 138 | 16221.4 | 16279 | 57.6
GEN-2018-049 | 03 - Central | 539641 | NW-DODG3 | 115 | 3649.2 | 3649.5 | 0.3
GEN-2018-049 | 03 - Central | 539645 | DCBEEF3 | 115 | 6884.8 | 6886.1 | 1.3
GEN-2018-049 | 03 - Central | 539649 | SAWYER 3 | 115 | 4797.4 | 4799.2 | 1.8
GEN-2018-049 | 03 - Central | 539661 | 24-FREY3 | 115 | 5509 | 5509.4 | 0.4
GEN-2018-049 | 03 - Central | 539667 | HAGGARD3 | 115 | 2437.6 | 2437.7 | 0.1
GEN-2018-049 | 03 - Central | 539668 | HARPER 4 | 138 | 7558.6 | 7564 | 5.4
GEN-2018-049 | 03 - Central | 539671 | FTDODGE3 | 115 | 9407.5 | 9410 | 2.5
GEN-2018-049 | 03 - Central | 539673 | MED-LDG3 | 115 | 8303.3 | 8312.2 | 8.9
GEN-2018-049 | 03 - Central | 539674 | BARBER 4 | 138 | 8595.1 | 8608.3 | 13.2
GEN-2018-049 | 03 - Central | 539675 | MILANTP4 | 138 | 10375.6 | 10379.3 | 3.7
GEN-2018-049 | 03 - Central | 539676 | MILAN 4 | 138 | 10873 | 10876 | 3
GEN-2018-049 | 03 - Central | 539678 | GRTBEND3 | 115 | 11659.5 | 11661.3 | 1.8
GEN-2018-049 | 03 - Central | 539679 | GRTBEND6 | 230 | 8550.9 | 8552.8 | 1.9
GEN-2018-049 | 03 - Central | 539680 | N-DODGE3 | 115 | 4675.1 | 4675.7 | 0.6
GEN-2018-049 | 03 - Central | 539681 | N-GBEND3 | 115 | 7925.2 | 7926.1 | 0.9
GEN-2018-049 | 03 - Central | 539684 | OTISSUB3 | 115 | 2993.9 | 2994.1 | 0.2
GEN-2018-049 | 03 - Central | 539688 | S-DODGE3 | 115 | 6708.7 | 6709.9 | 1.2
GEN-2018-049 | 03 - Central | 539689 | 2ND-KS 3 | 115 | 4978.9 | 4979.2 | 0.3
GEN-2018-049 | 03 - Central | 539694 | SPEARVL3 | 115 | 10094.8 | 10097.8 | 3
GEN-2018-049 | 03 - Central | 539695 | SPEARVL6 | 230 | 12663 | 12672.7 | 9.7
GEN-2018-049 | 03 - Central | 539699 | W-DODGE3 | 115 | 4322.6 | 4323.1 | 0.5
GEN-2018-049 | 03 - Central | 539740 | EDODGE 3 | 115 | 6304 | 6305.1 | 1.1
GEN-2018-049 | 03 - Central | 539758 | FORD 3 | 115 | 5278.8 | 5279.7 | 0.9
GEN-2018-049 | 03 - Central | 539759 | SPRVL 3 | 115 | 13090.5 | 13096.4 | 5.9
GEN-2018-049 | 03 - Central | 539760 | BARBER 3 | 115 | 8488.9 | 8498.2 | 9.3
GEN-2018-049 | 03 - Central | 539771 | NFTDODG3 | 115 | 9461.2 | 9463.7 | 2.5
GEN-2018-049 | 03 - Central | 539778 | GYCOTAP3 | 115 | 2437.6 | 2437.7 | 0.1
GEN-2018-049 | 03 - Central | 539779 | GRAY CO3 | 115 | 2437.6 | 2437.7 | 0.1
GEN-2018-049 | 03 - Central | 539800 | CLARKCOUNTY7 | 345 | 13276.7 | 13312.8 | 36.1
GEN-2018-049 | 03 - Central | 539801 | THISTLE7 | 345 | 17126.7 | 17358.5 | 231.8
GEN-2018-049 | 03 - Central | 539803 | IRONWOOD7 | 345 | 13002 | 13021.6 | 19.6
GEN-2018-049 | 03 - Central | 539804 | THISTLE4 | 138 | 18280.2 | 18360.1 | 79.9
GEN-2018-049 | 03 - Central | 539813 | TRANSFORMER | 345 | 11113.1 | 11138.1 | 25
GEN-2018-049 | 03 - Central | 539815 | IRONWOOD WF7 | 345 | 11724 | 11739.9 | 15.9
GEN-2018-049 | 03 - Central | 539840 | GEN-2011-008 | 345 | 11311.4 | 11335.7 | 24.3
GEN-2018-049 | 03 - Central | 539841 | G-2011-008-1 | 345 | 11311.4 | 11335.7 | 24.3
GEN-2018-049 | 03 - Central | 539855 | G-2011-008-2 | 345 | 9580.8 | 9597.7 | 16.9
GEN-2018-049 | 03 - Central | 539857 | G-2011-008-3 | 345 | 8820.2 | 8834.7 | 14.5
GEN-2018-049 | 03 - Central | 539944 | LOCHS | 115 | 3268.2 | 3268.4 | 0.2
GEN-2018-049 | 03 - Central | 560053 | G15-052T | 345 | 13165.4 | 13167.9 | 2.5
GEN-2018-049 | 03 - Central | 560071 | G16-003-TAP | 345 | 14086.6 | 14099.4 | 12.8
GEN-2018-049 | 03 - Central | 560078 | G16-037-TAP | 345 | 9115 | 9115.8 | 0.8
GEN-2018-049 | 03 - Central | 560080 | G16-046-TAP | 345 | 11644.5 | 11666.7 | 22.2
GEN-2018-049 | 03 - Central | 560082 | G16-050-TAP | 345 | 6826.3 | 6826.7 | 0.4
GEN-2018-049 | 03 - Central | 562476 | G14-001-TAP | 345 | 11230.9 | 11236.2 | 5.3
GEN-2018-049 | 03 - Central | 578530 | FR3HV | 345 | 5238.8 | 5239.7 | 0.9
GEN-2018-049 | 03 - Central | 579480 | GEN-2008-124 | 345 | 12582 | 12600.3 | 18.3
GEN-2018-049 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7666 | 7668.3 | 2.3
GEN-2018-049 | 03 - Central | 584900 | GEN-2015-052 | 345 | 13117.8 | 13120.2 | 2.4
GEN-2018-049 | 03 - Central | 585190 | GEN-2015-082 | 345 | 6375.9 | 6377.4 | 1.5
GEN-2018-049 | 03 - Central | 585300 | GEN-2015-095 | 138 | 14659.6 | 14676.7 | 17.1
GEN-2018-049 | 03 - Central | 585410 | GREAT_WESTRN | 345 | 8739 | 8745.3 | 6.3
GEN-2018-049 | 03 - Central | 585420 | COWBOY_RIDGE | 345 | 6758.2 | 6762 | 3.8
GEN-2018-049 | 03 - Central | 585430 | PRSIMN_CRK1 | 345 | 10554.9 | 10564 | 9.1
GEN-2018-049 | 03 - Central | 585440 | PRSIMN_CRK2 | 345 | 9710.5 | 9718.3 | 7.8
GEN-2018-049 | 03 - Central | 587020 | GEN-2016-003 | 345 | 14086.6 | 14099.4 | 12.8
GEN-2018-049 | 03 - Central | 587140 | GEN-2016-020 | 138 | 7211 | 7211.4 | 0.4
GEN-2018-049 | 03 - Central | 587230 | GEN-2016-037 | 345 | 7789.6 | 7790.1 | 0.5
GEN-2018-049 | 03 - Central | 587310 | GEN-2016-046 | 345 | 10229.6 | 10246.4 | 16.8
GEN-2018-049 | 03 - Central | 587311 | G16-046XFMR1 | 115 | 15370.7 | 15381.3 | 10.6
GEN-2018-049 | 03 - Central | 587350 | GEN-2016-050 | 345 | 5677.3 | 5677.6 | 0.3
GEN-2018-049 | 03 - Central | 587500 | GEN-2016-073 | 345 | 16313 | 16347.6 | 34.6
GEN-2018-049 | 03 - Central | 587880 | GEN-2016-111 | 345 | 6882.3 | 6883.6 | 1.3
GEN-2018-049 | 03 - Central | 587884 | G16-111-TAP | 345 | 10405.8 | 10408.9 | 3.1
GEN-2018-049 | 03 - Central | 588360 | GEN-2016-153 | 345 | 7590.2 | 7592.2 | 2
GEN-2018-049 | 03 - Central | 588364 | G16-153-TAP | 345 | 7933.3 | 7935.5 | 2.2
GEN-2018-049 | 03 - Central | 588560 | GEN-2017-011 | 345 | 11606.2 | 11614.9 | 8.7
GEN-2018-049 | 03 - Central | 588630 | GEN-2017-018 | 345 | 17126.7 | 17358.5 | 231.8
GEN-2018-049 | 03 - Central | 589060 | GEN-2017-068 | 138 | 30776.5 | 30796.9 | 20.4
GEN-2018-049 | 03 - Central | 589240 | GEN-2017-086 | 345 | 14858.4 | 14868.4 | 10
GEN-2018-049 | 03 - Central | 599950 | LAMAR7 | 345 | 4358.8 | 4359.3 | 0.5
GEN-2018-049 | 03 - Central | 640065 | AXTELL 3 | 345 | 9202.6 | 9202.9 | 0.3
GEN-2018-049 | 03 - Central | 755000 | WWDBORDT | 345 | 10498.2 | 10500.1 | 1.9
GEN-2018-049 | 03 - Central | 760284 | GEN-2017-220 | 345 | 22292.9 | 22358.6 | 65.7
GEN-2018-049 | 03 - Central | 760620 | GEN-2017-179 | 138 | 7286.6 | 7287.6 | 1
GEN-2018-049 | 03 - Central | 760641 | GEN-2017-226 | 138 | 33798.7 | 33823.4 | 24.7
GEN-2018-049 | 03 - Central | 760809 | GEN-2017-203 | 345 | 8748.2 | 8750.1 | 1.9
GEN-2018-049 | 03 - Central | 761838 | GEN-2017-121 | 138 | 9146.7 | 9147.6 | 0.9
GEN-2018-049 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5675.5 | 5675.6 | 0.1
GEN-2018-049 | 03 - Central | 761922 | GEN-2017-128 | 345 | 4756.1 | 4756.2 | 0.1
GEN-2018-049 | 03 - Central | 761943 | GEN-2017-191 | 345 | 18545.4 | 18546.4 | 1
GEN-2018-049 | 03 - Central | 762570 | GEN-2018-021 | 345 | 8270.6 | 8271.3 | 0.7
GEN-2018-049 | 03 - Central | 762658 | GEN-2018-030 | 345 | 5612.9 | 5613.6 | 0.7
GEN-2018-049 | 03 - Central | 762662 | G18-030-TAP | 345 | 6344.4 | 6345.4 | 1
GEN-2018-049 | 03 - Central | 762834 | GEN-2018-049 | 345 | Project Bus - Disconnected | 7280.8 | Project Bus - Disconnected
GEN-2018-049 | 03 - Central | 762922 | GEN-2018-057 | 138 | 18116.9 | 18123.6 | 6.7
GEN-2018-049 | 03 - Central | 900001 | TRAVERSE3 | 345 | 5460.1 | 5460.3 | 0.2
GEN-2018-049 | 03 - Central | 900002 | TRAVERSE-2 | 345 | 4091.1 | 4091.2 | 0.1
GEN-2018-049 | 03 - Central | 900003 | TRAVERSE1 | 345 | 3802.9 | 3803 | 0.1
GEN-2018-049 | 03 - Central | 900004 | TRW2-TRW3 | 345 | 4750 | 4750.2 | 0.2
GEN-2018-054 | 03 - Central | 541139 | FROSTRD_CAP5 | 161 | 12804 | 12841.6 | 37.6
GEN-2018-054 | 03 - Central | 541149 | WSTELEC_CAP5 | 161 | 15710.9 | 15778.2 | 67.3
GEN-2018-054 | 03 - Central | 541206 | PRALEE 5 | 161 | 21172.9 | 21225.4 | 52.5
GEN-2018-054 | 03 - Central | 541210 | MARTCTY5 | 161 | 28598 | 28687.2 | 89.2
GEN-2018-054 | 03 - Central | 541219 | RAYTOWN5 | 161 | 13313.6 | 13349.1 | 35.5
GEN-2018-054 | 03 - Central | 541220 | FROSTRD5 | 161 | 13828.7 | 13872.6 | 43.9
GEN-2018-054 | 03 - Central | 541222 | WSTELEC5 | 161 | 17282.6 | 17364 | 81.4
GEN-2018-054 | 03 - Central | 541223 | GRDVWE 5 | 161 | 20676.9 | 20759.2 | 82.3
GEN-2018-054 | 03 - Central | 541224 | LNGVW 5 | 161 | 23387 | 23563.4 | 176.4
GEN-2018-054 | 03 - Central | 541225 | PHILL 5 | 161 | 35453.7 | 35562.7 | 109
GEN-2018-054 | 03 - Central | 541231 | G18-054-TAP | 161 | 5967.6 | 6469.2 | 501.6
GEN-2018-054 | 03 - Central | 541238 | LKWOOD 5 | 161 | 13559.9 | 13590.9 | 31
GEN-2018-054 | 03 - Central | 541243 | LKWINBG5 | 161 | 25866.8 | 25973.4 | 106.6
GEN-2018-054 | 03 - Central | 541245 | KCSOUTH5 | 161 | 14303.6 | 14470.3 | 166.7
GEN-2018-054 | 03 - Central | 541246 | STROTHR5 | 161 | 14899.5 | 14943.1 | 43.6
GEN-2018-054 | 03 - Central | 541249 | HOOKRD 5 | 161 | 23486.4 | 23613.4 | 127
GEN-2018-054 | 03 - Central | 541282 | LNGVW 2 | 69 | 10689.2 | 10696.2 | 7
GEN-2018-054 | 03 - Central | 541283 | BRMALL 2 | 69 | 15541.1 | 15545.6 | 4.5
GEN-2018-054 | 03 - Central | 541284 | GRDVWTP2 | 69 | 9499.9 | 9504.2 | 4.3
GEN-2018-054 | 03 - Central | 541285 | GRDWCTY2 | 69 | 9103.3 | 9107.2 | 3.9
GEN-2018-054 | 03 - Central | 541287 | MARTCTY2 | 69 | 7360.1 | 7362.6 | 2.5
GEN-2018-054 | 03 - Central | 541288 | RGAFB 2 | 69 | 8429.7 | 8432.6 | 2.9
GEN-2018-054 | 03 - Central | 541317 | NRAYMORE | 161 | 9319.7 | 9537.6 | 217.9
GEN-2018-054 | 03 - Central | 541322 | RGAFBTP2 | 69 | 9169.8 | 9173.3 | 3.5
GEN-2018-054 | 03 - Central | 541382 | HONEYWL5 | 161 | 23084.6 | 23137.6 | 53
GEN-2018-054 | 03 - Central | 542950 | STHTOWN_CAP5 | 161 | 31052.9 | 31154.8 | 101.9
GEN-2018-054 | 03 - Central | 542973 | HAWTHS5 | 161 | 59895.8 | 60011.6 | 115.8
GEN-2018-054 | 03 - Central | 542992 | BENDIX 5 | 161 | 30619.9 | 30708.3 | 88.4
GEN-2018-054 | 03 - Central | 542993 | STHTOWN5 | 161 | 37858 | 38009.6 | 151.6
GEN-2018-054 | 03 - Central | 542994 | HICKMAN5 | 161 | 20173.4 | 20207 | 33.6
GEN-2018-054 | 03 - Central | 542996 | MIDTOWN5 | 161 | 36236.7 | 36312.5 | 75.8
GEN-2018-054 | 03 - Central | 542997 | LEEDS 5 | 161 | 36003.5 | 36115.4 | 111.9
GEN-2018-054 | 03 - Central | 542998 | LVISTA 5 | 161 | 24602.8 | 24804.5 | 201.7
GEN-2018-054 | 03 - Central | 543001 | FOREST 5 | 161 | 32388.7 | 32464.4 | 75.7
GEN-2018-054 | 03 - Central | 543002 | MARTCIT5 | 161 | 25525.8 | 25587.5 | 61.7
GEN-2018-054 | 03 - Central | 543006 | SWOPE N5 | 161 | 22272.3 | 22364.5 | 92.2
GEN-2018-054 | 03 - Central | 543007 | SWOPE S5 | 161 | 22355.5 | 22402.2 | 46.7
GEN-2018-054 | 03 - Central | 543008 | BUNKRDG5 | 161 | 24664 | 24814 | 150
GEN-2018-054 | 03 - Central | 543009 | WINJT N5 | 161 | 24298.2 | 24407.8 | 109.6
GEN-2018-054 | 03 - Central | 543010 | WINJT S5 | 161 | 23952 | 24005.6 | 53.6
GEN-2018-054 | 03 - Central | 543129 | HAWTHS_G65 | 161 | 59034 | 59146.4 | 112.4
GEN-2018-054 | 03 - Central | 548821 | SUB N | 69 | 18116 | 18121.7 | 5.7
GEN-2018-054 | 03 - Central | 762889 | GEN-2018-054 | 161 | Project Bus - Disconnected | 6401.9 | Project Bus - Disconnected
GEN-2018-057 | 03 - Central | 300739 | 7BLACKBERRY | 345 | 15924.1 | 15925.8 | 1.7
GEN-2018-057 | 03 - Central | 300740 | 7SPORTSMAN | 345 | 24813.2 | 24813.6 | 0.4
GEN-2018-057 | 03 - Central | 300949 | 7JASPER | 345 | 13032.3 | 13033.1 | 0.8
GEN-2018-057 | 03 - Central | 514715 | WOODRNG7 | 345 | 17218.5 | 17225.3 | 6.8
GEN-2018-057 | 03 - Central | 514825 | KAYWIND7 | 345 | 12111 | 12118.9 | 7.9
GEN-2018-057 | 03 - Central | 515375 | WWRDEHV7 | 345 | 19168.3 | 19173.1 | 4.8
GEN-2018-057 | 03 - Central | 515476 | HUNTERS7 | 345 | 12367.2 | 12375 | 7.8
GEN-2018-057 | 03 - Central | 515477 | CHSHLMV7 | 345 | 12349.7 | 12357.5 | 7.8
GEN-2018-057 | 03 - Central | 515543 | RENFROW7 | 345 | 12237.7 | 12251.4 | 13.7
GEN-2018-057 | 03 - Central | 515544 | RENFROW4 | 138 | 14342.6 | 14348.6 | 6
GEN-2018-057 | 03 - Central | 515546 | GRANTCO4 | 138 | 6617.2 | 6618.3 | 1.1
GEN-2018-057 | 03 - Central | 515569 | MDFRDTP4 | 138 | 11407.7 | 11411.3 | 3.6
GEN-2018-057 | 03 - Central | 515599 | G07621119-20 | 345 | 11948.9 | 11950.8 | 1.9
GEN-2018-057 | 03 - Central | 515621 | OPENSKY7 | 345 | 12141.4 | 12149.3 | 7.9
GEN-2018-057 | 03 - Central | 515646 | GRNTWD 7 | 345 | 10858.9 | 10869.5 | 10.6
GEN-2018-057 | 03 - Central | 515825 | GRTWSRN7 | 345 | 8727 | 8728 | 1
GEN-2018-057 | 03 - Central | 515852 | DGRASSE7 | 345 | 14641.8 | 14650.5 | 8.7
GEN-2018-057 | 03 - Central | 515853 | DGRASSE4 | 138 | 14864.3 | 14867.2 | 2.9
GEN-2018-057 | 03 - Central | 515951 | PERSIMN7 | 345 | 10466.4 | 10467.8 | 1.4
GEN-2018-057 | 03 - Central | 515961 | GUTHRIE7 | 345 | 11973.2 | 11975.1 | 1.9
GEN-2018-057 | 03 - Central | 515990 | SKELTON7 | 345 | 4273 | 4273.4 | 0.4
GEN-2018-057 | 03 - Central | 520409 | WFEC_RNFRO4 | 138 | 10716.3 | 10719.5 | 3.2
GEN-2018-057 | 03 - Central | 522397 | MEDFORD4 | 138 | 7583.1 | 7584.7 | 1.6
GEN-2018-057 | 03 - Central | 522398 | PONDCRK4 | 138 | 5215.3 | 5216.1 | 0.8
GEN-2018-057 | 03 - Central | 531469 | SPERVIL7 | 345 | 13538.3 | 13541.5 | 3.2
GEN-2018-057 | 03 - Central | 532766 | JEC N 7 | 345 | 25030.6 | 25034.6 | 4
GEN-2018-057 | 03 - Central | 532767 | GEARY 7 | 345 | 10661.2 | 10663.9 | 2.7
GEN-2018-057 | 03 - Central | 532768 | EMPEC 7 | 345 | 19983.3 | 20003.1 | 19.8
GEN-2018-057 | 03 - Central | 532769 | LANG 7 | 345 | 19716.7 | 19736.1 | 19.4
GEN-2018-057 | 03 - Central | 532770 | MORRIS 7 | 345 | 13773.1 | 13778.6 | 5.5
GEN-2018-057 | 03 - Central | 532771 | RENO 7 | 345 | 11810.4 | 11834.8 | 24.4
GEN-2018-057 | 03 - Central | 532773 | SUMMIT 7 | 345 | 11704.6 | 11712 | 7.4
GEN-2018-057 | 03 - Central | 532774 | SWISVAL7 | 345 | 18592.7 | 18597.4 | 4.7
GEN-2018-057 | 03 - Central | 532776 | READWF 7 | 345 | 16200.5 | 16213.5 | 13
GEN-2018-057 | 03 - Central | 532780 | CANEYRV7 | 345 | 9823.8 | 9833.2 | 9.4
GEN-2018-057 | 03 - Central | 532781 | CANEYWF7 | 345 | 9547.7 | 9556.5 | 8.8
GEN-2018-057 | 03 - Central | 532782 | BUFFALO7 | 345 | 22343.1 | 22486.8 | 143.7
GEN-2018-057 | 03 - Central | 532783 | KINGMAN7 | 345 | 7349 | 7360.5 | 11.5
GEN-2018-057 | 03 - Central | 532784 | NINN1WF7 | 345 | 6118.7 | 6126.1 | 7.4
GEN-2018-057 | 03 - Central | 532785 | PRATTWF7 | 345 | 5074.3 | 5079.2 | 4.9
GEN-2018-057 | 03 - Central | 532790 | EXPED WF7 | 345 | 7193.9 | 7204.2 | 10.3
GEN-2018-057 | 03 - Central | 532791 | BENTON 7 | 345 | 19729 | 19834.3 | 105.3
GEN-2018-057 | 03 - Central | 532792 | FR2EAST7 | 345 | 7158.8 | 7166.9 | 8.1
GEN-2018-057 | 03 - Central | 532793 | NEOSHO 7 | 345 | 18300.7 | 18304.4 | 3.7
GEN-2018-057 | 03 - Central | 532794 | ROSEHIL7 | 345 | 19162.4 | 19233.1 | 70.7
GEN-2018-057 | 03 - Central | 532795 | FR2WEST7 | 345 | 5716.7 | 5721.5 | 4.8
GEN-2018-057 | 03 - Central | 532796 | WICHITA7 | 345 | 26091.7 | 26332.6 | 240.9
GEN-2018-057 | 03 - Central | 532797 | WOLFCRK7 | 345 | 18764.2 | 18775 | 10.8
GEN-2018-057 | 03 - Central | 532798 | VIOLA 7 | 345 | 14822.8 | 14868.4 | 45.6
GEN-2018-057 | 03 - Central | 532799 | WAVERLY7 | 345 | 16607.1 | 16614.5 | 7.4
GEN-2018-057 | 03 - Central | 532800 | LATHAMS7 | 345 | 10461.6 | 10474 | 12.4
GEN-2018-057 | 03 - Central | 532801 | ELKRVR17 | 345 | 9277.1 | 9286.8 | 9.7
GEN-2018-057 | 03 - Central | 532802 | WAVERTX7 | 345 | 13839.3 | 13844.4 | 5.1
GEN-2018-057 | 03 - Central | 532803 | EXPEDITION7 | 345 | 10638.7 | 10661.2 | 22.5
GEN-2018-057 | 03 - Central | 532856 | SWISVAL6 | 230 | 23040.9 | 23044.8 | 3.9
GEN-2018-057 | 03 - Central | 532863 | MORRIS 6 | 230 | 14605.7 | 14609.6 | 3.9
GEN-2018-057 | 03 - Central | 532871 | CIRCLE 6 | 230 | 9078.9 | 9083.3 | 4.4
GEN-2018-057 | 03 - Central | 532873 | SUMMIT 6 | 230 | 13948 | 13953.7 | 5.7
GEN-2018-057 | 03 - Central | 532982 | OXFORD 4 | 138 | 10630.5 | 10641.5 | 11
GEN-2018-057 | 03 - Central | 532984 | SUMNER 4 | 138 | 12040.1 | 12055 | 14.9
GEN-2018-057 | 03 - Central | 532985 | TCROCK 4 | 138 | 6026.6 | 6030.2 | 3.6
GEN-2018-057 | 03 - Central | 532986 | BENTON 4 | 138 | 28822.4 | 28964.9 | 142.5
GEN-2018-057 | 03 - Central | 532987 | BUTLER 4 | 138 | 11292.8 | 11310.2 | 17.4
GEN-2018-057 | 03 - Central | 532988 | BELAIRE4 | 138 | 19479.6 | 19545.4 | 65.8
GEN-2018-057 | 03 - Central | 532990 | MIDIAN 4 | 138 | 11348.5 | 11367 | 18.5
GEN-2018-057 | 03 - Central | 532991 | WEAVER 4 | 138 | 22687.3 | 22762.8 | 75.5
GEN-2018-057 | 03 - Central | 532992 | TIMBJCT4 | 138 | 6479.5 | 6483.8 | 4.3
GEN-2018-057 | 03 - Central | 532994 | TCBURNS4 | 138 | 4146.4 | 4148.8 | 2.4
GEN-2018-057 | 03 - Central | 533011 | HALSTD 4 | 138 | 8593.4 | 8633.2 | 39.8
GEN-2018-057 | 03 - Central | 533013 | MOUND 4 | 138 | 7156.3 | 7174.8 | 18.5
GEN-2018-057 | 03 - Central | 533015 | BENTLEY4 | 138 | 11118.4 | 11200.9 | 82.5
GEN-2018-057 | 03 - Central | 533016 | WWUPLNT4 | 138 | 8429.6 | 8477 | 47.4
GEN-2018-057 | 03 - Central | 533024 | 29TH 4 | 138 | 20135 | 20205.2 | 70.2
GEN-2018-057 | 03 - Central | 533033 | CANAL 4 | 138 | 16848.1 | 16921 | 72.9
GEN-2018-057 | 03 - Central | 533034 | CENTENN4 | 138 | 15156 | 15284.8 | 128.8
GEN-2018-057 | 03 - Central | 533035 | CHISHLM4 | 138 | 22042.3 | 22215.6 | 173.3
GEN-2018-057 | 03 - Central | 533036 | CLEARWT4 | 138 | 14652.5 | 14704 | 51.5
GEN-2018-057 | 03 - Central | 533037 | COMOTAR4 | 138 | 19179.2 | 19243.3 | 64.1
GEN-2018-057 | 03 - Central | 533038 | COWSKIN4 | 138 | 17920.1 | 18131 | 210.9
GEN-2018-057 | 03 - Central | 533039 | ELPASO 4 | 138 | 25406.4 | 25514.5 | 108.1
GEN-2018-057 | 03 - Central | 533040 | EVANS N4 | 138 | 33051.6 | 34015.8 | 964.2
GEN-2018-057 | 03 - Central | 533041 | EVANS S4 | 138 | 32971.5 | 33929.7 | 958.2
GEN-2018-057 | 03 - Central | 533043 | FOWLER 4 | 138 | 16612.1 | 16688.3 | 76.2
GEN-2018-057 | 03 - Central | 533045 | GILL W 4 | 138 | 22496.6 | 22650.6 | 154
GEN-2018-057 | 03 - Central | 533046 | GILL S 4 | 138 | 22493.5 | 22647.2 | 153.7
GEN-2018-057 | 03 - Central | 533047 | GILL 4 | 138 | 22490.4 | 22644.1 | 153.7
GEN-2018-057 | 03 - Central | 533049 | HOOVERN4 | 138 | 17626.9 | 17778.4 | 151.5
GEN-2018-057 | 03 - Central | 533050 | HOOVERS4 | 138 | 17622.9 | 17774.1 | 151.2
GEN-2018-057 | 03 - Central | 533051 | INTERST4 | 138 | 16190.9 | 16301.9 | 111
GEN-2018-057 | 03 - Central | 533052 | PARKCTY4 | 138 | 20832.3 | 20967.9 | 135.6
GEN-2018-057 | 03 - Central | 533053 | LAKERDG4 | 138 | 17721.8 | 17917.2 | 195.4
GEN-2018-057 | 03 - Central | 533054 | MAIZE 4 | 138 | 21516.3 | 21812 | 295.7
GEN-2018-057 | 03 - Central | 533060 | NOEASTE4 | 138 | 21080.3 | 21158.2 | 77.9
GEN-2018-057 | 03 - Central | 533062 | ROSEHIL4 | 138 | 31750.5 | 31870.5 | 120
GEN-2018-057 | 03 - Central | 533063 | SC10BEL4 | 138 | 11925 | 11940.1 | 15.1
GEN-2018-057 | 03 - Central | 533064 | 17TH 4 | 138 | 18127.2 | 18229.4 | 102.2
GEN-2018-057 | 03 - Central | 533065 | SG12COL4 | 138 | 20003.9 | 20329.2 | 325.3
GEN-2018-057 | 03 - Central | 533068 | STEARMN4 | 138 | 19999.6 | 20072.4 | 72.8
GEN-2018-057 | 03 - Central | 533073 | WACO N 4 | 138 | 19530.3 | 19656 | 125.7
GEN-2018-057 | 03 - Central | 533074 | 45TH ST4 | 138 | 24346.1 | 24821.3 | 475.2
GEN-2018-057 | 03 - Central | 533075 | VIOLA 4 | 138 | 25212.9 | 25289.7 | 76.8
GEN-2018-057 | 03 - Central | 533304 | LANG 3 | 115 | 16201.8 | 16206.5 | 4.7
GEN-2018-057 | 03 - Central | 533369 | HILSBOR3 | 115 | 2664 | 2664.9 | 0.9
GEN-2018-057 | 03 - Central | 533380 | SPRGCRK3 | 115 | 3980.4 | 3982.4 | 2
GEN-2018-057 | 03 - Central | 533394 | CORONAD3 | 115 | 7349.9 | 7351 | 1.1
GEN-2018-057 | 03 - Central | 533411 | ARKVAL 3 | 115 | 10018.9 | 10023.2 | 4.3
GEN-2018-057 | 03 - Central | 533412 | ARKVALJ3 | 115 | 10214 | 10218.4 | 4.4
GEN-2018-057 | 03 - Central | 533413 | CIRCLE 3 | 115 | 19473.4 | 19490.5 | 17.1
GEN-2018-057 | 03 - Central | 533414 | CITIES 3 | 115 | 8278.9 | 8282.3 | 3.4
GEN-2018-057 | 03 - Central | 533415 | DAVIS 3 | 115 | 8468.1 | 8471.8 | 3.7
GEN-2018-057 | 03 - Central | 533416 | RENO 3 | 115 | 23500.3 | 23530.7 | 30.4
GEN-2018-057 | 03 - Central | 533419 | HEC 3 | 115 | 18196.4 | 18211.4 | 15
GEN-2018-057 | 03 - Central | 533421 | HEC GT 3 | 115 | 18927.5 | 18943.6 | 16.1
GEN-2018-057 | 03 - Central | 533426 | MANVILE3 | 115 | 8759.2 | 8761.1 | 1.9
GEN-2018-057 | 03 - Central | 533428 | MCPHER 3 | 115 | 11100.6 | 11103.8 | 3.2
GEN-2018-057 | 03 - Central | 533429 | MOUNDRG3 | 115 | 8836.6 | 8850.9 | 14.3
GEN-2018-057 | 03 - Central | 533430 | MNDRGCT3 | 115 | 6811.7 | 6820.2 | 8.5
GEN-2018-057 | 03 - Central | 533438 | WMCPHER3 | 115 | 11496.5 | 11499.9 | 3.4
GEN-2018-057 | 03 - Central | 533439 | WHEATLD3 | 115 | 7068.4 | 7069.6 | 1.2
GEN-2018-057 | 03 - Central | 533504 | CITYSVC2 | 69 | 4049.4 | 4049.9 | 0.5
GEN-2018-057 | 03 - Central | 533505 | NCTYSVC2 | 69 | 4076.4 | 4076.9 | 0.5
GEN-2018-057 | 03 - Central | 533506 | DAVIS 2 | 69 | 7539 | 7540.7 | 1.7
GEN-2018-057 | 03 - Central | 533518 | MWIRON 2 | 69 | 6383 | 6384.2 | 1.2
GEN-2018-057 | 03 - Central | 533519 | MWIRONJ2 | 69 | 6186.4 | 6187.5 | 1.1
GEN-2018-057 | 03 - Central | 533529 | MWIRNJ22 | 69 | 6564.7 | 6566 | 1.3
GEN-2018-057 | 03 - Central | 533597 | MIDIANW2 | 69 | 14652 | 14668.2 | 16.2
GEN-2018-057 | 03 - Central | 533624 | BURLING2 | 69 | 3548.6 | 3548.7 | 0.1
GEN-2018-057 | 03 - Central | 533625 | BURLIND2 | 69 | 3163.5 | 3163.5 | 0
GEN-2018-057 | 03 - Central | 533626 | BURLJCT2 | 69 | 5158 | 5158.1 | 0.1
GEN-2018-057 | 03 - Central | 533628 | CC1BURL2 | 69 | 3547.2 | 3547.2 | 0
GEN-2018-057 | 03 - Central | 533629 | CC2SHAR2 | 69 | 4822.4 | 4822.5 | 0.1
GEN-2018-057 | 03 - Central | 533653 | WOLFCRK2 | 69 | 6235.7 | 6235.9 | 0.2
GEN-2018-057 | 03 - Central | 533732 | BURRTON2 | 69 | 3002.7 | 3004.9 | 2.2
GEN-2018-057 | 03 - Central | 533736 | HALSTED2 | 69 | 7585 | 7599.1 | 14.1
GEN-2018-057 | 03 - Central | 533742 | MOUND 2 | 69 | 7347.6 | 7357.6 | 10
GEN-2018-057 | 03 - Central | 533743 | MUD CRK2 | 69 | 5471.4 | 5478 | 6.6
GEN-2018-057 | 03 - Central | 533744 | MUDCRKJ2 | 69 | 6187.9 | 6196.3 | 8.4
GEN-2018-057 | 03 - Central | 533786 | CHISHLM2 | 69 | 20538 | 20605.7 | 67.7
GEN-2018-057 | 03 - Central | 533788 | COWSKIN2 | 69 | 16486.2 | 16558.3 | 72.1
GEN-2018-057 | 03 - Central | 533799 | GRANT 2 | 69 | 12822.9 | 12847.9 | 25
GEN-2018-057 | 03 - Central | 533800 | GRANT J2 | 69 | 10057.9 | 10075 | 17.1
GEN-2018-057 | 03 - Central | 533805 | HOOVERN2 | 69 | 31473.2 | 31670.8 | 197.6
GEN-2018-057 | 03 - Central | 533806 | HOOVERS2 | 69 | 31497.4 | 31695.3 | 197.9
GEN-2018-057 | 03 - Central | 533814 | MASCOT 2 | 69 | 20301.5 | 20367.9 | 66.4
GEN-2018-057 | 03 - Central | 533818 | MEAD N 2 | 69 | 26131.5 | 26248 | 116.5
GEN-2018-057 | 03 - Central | 533820 | MOSSMAN2 | 69 | 18381.7 | 18428.1 | 46.4
GEN-2018-057 | 03 - Central | 533831 | RENEW 2 | 69 | 17961.5 | 18010.7 | 49.2
GEN-2018-057 | 03 - Central | 533835 | 17TH TP2 | 69 | 25461.5 | 25569.6 | 108.1
GEN-2018-057 | 03 - Central | 533840 | 17TH 2 | 69 | 27716.5 | 27840.7 | 124.2
GEN-2018-057 | 03 - Central | 533849 | VISTAPK2 | 69 | 17479.2 | 17535.6 | 56.4
GEN-2018-057 | 03 - Central | 533854 | WESTLNK2 | 69 | 15535.7 | 15594.5 | 58.8
GEN-2018-057 | 03 - Central | 533855 | WATER1 2 | 69 | 24232.5 | 24336.5 | 104
GEN-2018-057 | 03 - Central | 533859 | RIPLEYE2 | 69 | 23143 | 23229.2 | 86.2
GEN-2018-057 | 03 - Central | 533860 | RIPLEYM2 | 69 | 23146.4 | 23232.7 | 86.3
GEN-2018-057 | 03 - Central | 533861 | BU5FURL2 | 69 | 7297.6 | 7304.2 | 6.6
GEN-2018-057 | 03 - Central | 533874 | SG9STMK2 | 69 | 16455.1 | 16527 | 71.9
GEN-2018-057 | 03 - Central | 533879 | GODDTAP2 | 69 | 8345 | 8362.4 | 17.4
GEN-2018-057 | 03 - Central | 533880 | GODDARD2 | 69 | 6422.3 | 6432.6 | 10.3
GEN-2018-057 | 03 - Central | 539003 | CLDWELL4 | 138 | 5834.8 | 5838.3 | 3.5
GEN-2018-057 | 03 - Central | 539008 | MILAN_GOAB | 138 | 12232.9 | 12250.3 | 17.4
GEN-2018-057 | 03 - Central | 539009 | CONWAY | 138 | 11740.5 | 11755.6 | 15.1
GEN-2018-057 | 03 - Central | 539631 | FLATRWD4 | 138 | 10869 | 10873.4 | 4.4
GEN-2018-057 | 03 - Central | 539638 | FLATRDG4 | 138 | 16268.8 | 16279 | 10.2
GEN-2018-057 | 03 - Central | 539675 | MILANTP4 | 138 | 10367.9 | 10379.3 | 11.4
GEN-2018-057 | 03 - Central | 539676 | MILAN 4 | 138 | 10862.3 | 10876 | 13.7
GEN-2018-057 | 03 - Central | 539800 | CLARKCOUNTY7 | 345 | 13307.9 | 13312.8 | 4.9
GEN-2018-057 | 03 - Central | 539801 | THISTLE7 | 345 | 17331.1 | 17358.5 | 27.4
GEN-2018-057 | 03 - Central | 539804 | THISTLE4 | 138 | 18347.3 | 18360.1 | 12.8
GEN-2018-057 | 03 - Central | 539813 | TRANSFORMER | 345 | 11134.7 | 11138.1 | 3.4
GEN-2018-057 | 03 - Central | 539840 | GEN-2011-008 | 345 | 11332.4 | 11335.7 | 3.3
GEN-2018-057 | 03 - Central | 539841 | G-2011-008-1 | 345 | 11332.4 | 11335.7 | 3.3
GEN-2018-057 | 03 - Central | 539855 | G-2011-008-2 | 345 | 9595.4 | 9597.7 | 2.3
GEN-2018-057 | 03 - Central | 539857 | G-2011-008-3 | 345 | 8832.7 | 8834.7 | 2
GEN-2018-057 | 03 - Central | 541541 | LAC_LAKE_2 | 69 | 2677.1 | 2677.1 | 0
GEN-2018-057 | 03 - Central | 542965 | W.GRDNR7 | 345 | 29870.9 | 29873.7 | 2.8
GEN-2018-057 | 03 - Central | 542981 | LACYGNE7 | 345 | 27805.9 | 27808.9 | 3
GEN-2018-057 | 03 - Central | 543629 | LACYGNE11_7 | 345 | 27069.7 | 27072.5 | 2.8
GEN-2018-057 | 03 - Central | 543632 | LACYGNE22_7 | 345 | 27069.7 | 27072.5 | 2.8
GEN-2018-057 | 03 - Central | 543659 | LACYGNE2 | 69 | 2816.1 | 2816.1 | 0
GEN-2018-057 | 03 - Central | 543667 | LAC3_STAR7 | 345 | 673.4 | 673.5 | 0.1
GEN-2018-057 | 03 - Central | 543669 | LAC8_STAR7 | 345 | 645 | 645 | 0
GEN-2018-057 | 03 - Central | 560053 | G15-052T | 345 | 13150.1 | 13167.9 | 17.8
GEN-2018-057 | 03 - Central | 560080 | G16-046-TAP | 345 | 11663.5 | 11666.7 | 3.2
GEN-2018-057 | 03 - Central | 562476 | G14-001-TAP | 345 | 11213.3 | 11236.2 | 22.9
GEN-2018-057 | 03 - Central | 578530 | FR3HV | 345 | 5235.7 | 5239.7 | 4
GEN-2018-057 | 03 - Central | 583850 | GEN-2014-001 | 345 | 7658.4 | 7668.3 | 9.9
GEN-2018-057 | 03 - Central | 584900 | GEN-2015-052 | 345 | 13102.6 | 13120.2 | 17.6
GEN-2018-057 | 03 - Central | 585300 | GEN-2015-095 | 138 | 14673.8 | 14676.7 | 2.9
GEN-2018-057 | 03 - Central | 585410 | GREAT_WESTRN | 345 | 8744.3 | 8745.3 | 1
GEN-2018-057 | 03 - Central | 585420 | COWBOY_RIDGE | 345 | 6761.4 | 6762 | 0.6
GEN-2018-057 | 03 - Central | 585430 | PRSIMN_CRK1 | 345 | 10562.6 | 10564 | 1.4
GEN-2018-057 | 03 - Central | 585440 | PRSIMN_CRK2 | 345 | 9717 | 9718.3 | 1.3
GEN-2018-057 | 03 - Central | 587310 | GEN-2016-046 | 345 | 10244 | 10246.4 | 2.4
GEN-2018-057 | 03 - Central | 587311 | G16-046XFMR1 | 115 | 15379.8 | 15381.3 | 1.5
GEN-2018-057 | 03 - Central | 587500 | GEN-2016-073 | 345 | 16272.6 | 16347.6 | 75
GEN-2018-057 | 03 - Central | 587880 | GEN-2016-111 | 345 | 6878.4 | 6883.6 | 5.2
GEN-2018-057 | 03 - Central | 587884 | G16-111-TAP | 345 | 10396.2 | 10408.9 | 12.7
GEN-2018-057 | 03 - Central | 588190 | GEN-2016-128 | 345 | 4074.3 | 4074.7 | 0.4
GEN-2018-057 | 03 - Central | 588300 | GEN-2016-157 | 345 | 5235.8 | 5235.9 | 0.1
GEN-2018-057 | 03 - Central | 588310 | GEN-2016-158 | 345 | 4937 | 4937.1 | 0.1
GEN-2018-057 | 03 - Central | 588360 | GEN-2016-153 | 345 | 7582.9 | 7592.2 | 9.3
GEN-2018-057 | 03 - Central | 588364 | G16-153-TAP | 345 | 7925.3 | 7935.5 | 10.2
GEN-2018-057 | 03 - Central | 588490 | GEN-2017-004 | 345 | 8615.2 | 8618.8 | 3.6
GEN-2018-057 | 03 - Central | 588494 | G17-004-TAP | 345 | 10020.4 | 10025.4 | 5
GEN-2018-057 | 03 - Central | 588630 | GEN-2017-018 | 345 | 17331.1 | 17358.5 | 27.4
GEN-2018-057 | 03 - Central | 589060 | GEN-2017-068 | 138 | 30006.8 | 30796.9 | 790.1
GEN-2018-057 | 03 - Central | 589240 | GEN-2017-086 | 345 | 14822.8 | 14868.4 | 45.6
GEN-2018-057 | 03 - Central | 760284 | GEN-2017-220 | 345 | 22216.5 | 22358.6 | 142.1
GEN-2018-057 | 03 - Central | 760620 | GEN-2017-179 | 138 | 7250.3 | 7287.6 | 37.3
GEN-2018-057 | 03 - Central | 760641 | GEN-2017-226 | 138 | 32870.4 | 33823.4 | 953
GEN-2018-057 | 03 - Central | 760809 | GEN-2017-203 | 345 | 8743.2 | 8750.1 | 6.9
GEN-2018-057 | 03 - Central | 761838 | GEN-2017-121 | 138 | 9139.4 | 9147.6 | 8.2
GEN-2018-057 | 03 - Central | 761901 | GEN-2017-125 | 345 | 5675.2 | 5675.6 | 0.4
GEN-2018-057 | 03 - Central | 761922 | GEN-2017-128 | 345 | 4755.9 | 4756.2 | 0.3
GEN-2018-057 | 03 - Central | 761943 | GEN-2017-191 | 345 | 18541.8 | 18546.4 | 4.6
GEN-2018-057 | 03 - Central | 762279 | GEN-2017-195 | 345 | 29785.6 | 29788.3 | 2.7
GEN-2018-057 | 03 - Central | 762321 | GEN-2017-164 | 345 | 10507.3 | 10509.8 | 2.5
GEN-2018-057 | 03 - Central | 762342 | GEN-2017-178 | 345 | 7560.5 | 7561.8 | 1.3
GEN-2018-057 | 03 - Central | 762680 | GEN-2018-032 | 345 | 12042.4 | 12044 | 1.6
GEN-2018-057 | 03 - Central | 762687 | G18-032_DUMY | 345 | 18300.7 | 18304.4 | 3.7
GEN-2018-057 | 03 - Central | 762834 | GEN-2018-049 | 345 | 7276.2 | 7280.8 | 4.6
GEN-2018-057 | 03 - Central | 762922 | GEN-2018-057 | 138 | Project Bus - Disconnected | 18123.6 | Project Bus - Disconnected
GEN-2018-062 | 03 - Central | 532912 | EDWRDVL5 | 161 | 22506.4 | 22589.1 | 82.7
GEN-2018-062 | 03 - Central | 533238 | EDWARVL3 | 115 | 14610.6 | 14618.9 | 8.3
GEN-2018-062 | 03 - Central | 541145 | RNRIDGE_CAP5 | 161 | 21807.4 | 21828.7 | 21.3
GEN-2018-062 | 03 - Central | 541230 | RNRIDGE5 | 161 | 24957.9 | 24985.8 | 27.9
GEN-2018-062 | 03 - Central | 542947 | MERRIAM_CAP5 | 161 | 27716.2 | 27749.2 | 33
GEN-2018-062 | 03 - Central | 543017 | WETHRBY5 | 161 | 17556.6 | 17588.3 | 31.7
GEN-2018-062 | 03 - Central | 543026 | TIFFANY5 | 161 | 21360.1 | 21387.2 | 27.1
GEN-2018-062 | 03 - Central | 543031 | SHWNMSN5 | 161 | 37758.9 | 37858.3 | 99.4
GEN-2018-062 | 03 - Central | 543032 | MERRIAM5 | 161 | 33012.9 | 33059.8 | 46.9
GEN-2018-062 | 03 - Central | 543038 | LENEXA 5 | 161 | 39308 | 39362.8 | 54.8
GEN-2018-062 | 03 - Central | 543041 | SHAWNEE5 | 161 | 28255.6 | 28323.6 | 68
GEN-2018-062 | 03 - Central | 543049 | CEDRCRK5 | 161 | 31623.9 | 31655.8 | 31.9
GEN-2018-062 | 03 - Central | 546651 | BARBER 5 | 161 | 31050.5 | 31172.8 | 122.3
GEN-2018-062 | 03 - Central | 546652 | QUIND 5 | 161 | 18842 | 18999.2 | 157.2
GEN-2018-062 | 03 - Central | 546653 | NEARMAN5 | 161 | 22531.6 | 22843.8 | 312.2
GEN-2018-062 | 03 - Central | 546654 | SUNSET 5 | 161 | 19534 | 19692.3 | 158.3
GEN-2018-062 | 03 - Central | 546655 | KAW W 5 | 161 | 24453.5 | 24592.3 | 138.8
GEN-2018-062 | 03 - Central | 546656 | MAYWOOD5 | 161 | 22749.6 | 22886.6 | 137
GEN-2018-062 | 03 - Central | 546658 | GIBBS 5 | 161 | 23484.1 | 23579.5 | 95.4
GEN-2018-062 | 03 - Central | 546659 | CTR CTY5 | 161 | 18583.8 | 18662.5 | 78.7
GEN-2018-062 | 03 - Central | 546663 | GM PLT 5 | 161 | 17078.3 | 17176.2 | 97.9
GEN-2018-062 | 03 - Central | 546665 | TURNER 5 | 161 | 22955.3 | 23058.5 | 103.2
GEN-2018-062 | 03 - Central | 546667 | FAIRFX-5 | 161 | 17456.7 | 17539 | 82.3
GEN-2018-062 | 03 - Central | 546668 | PIPER 5 | 161 | 15102.1 | 15158.9 | 56.8
GEN-2018-062 | 03 - Central | 546669 | WOLCOTT5 | 161 | 18752.9 | 18826.3 | 73.4
GEN-2018-062 | 03 - Central | 546670 | OAK KNOL | 69 | 8858.3 | 8865.9 | 7.6
GEN-2018-062 | 03 - Central | 546672 | MORRIS 2 | 69 | 10185.8 | 10195.7 | 9.9
GEN-2018-062 | 03 - Central | 546673 | GR WHL 2 | 69 | 12170.4 | 12184.2 | 13.8
GEN-2018-062 | 03 - Central | 546674 | SPEAKER2 | 69 | 12061.1 | 12074 | 12.9
GEN-2018-062 | 03 - Central | 546675 | GW TAP 1 | 69 | 12296.7 | 12310.9 | 14.2
GEN-2018-062 | 03 - Central | 546676 | GW TAP 2 | 69 | 8882.6 | 8890.3 | 7.7
GEN-2018-062 | 03 - Central | 546677 | MAYWOOD2 | 69 | 11619.9 | 11633.5 | 13.6
GEN-2018-062 | 03 - Central | 546678 | KAW 2 | 69 | 14193.4 | 14210.5 | 17.1
GEN-2018-062 | 03 - Central | 546681 | MUNCIE 2 | 69 | 12156.8 | 12169.6 | 12.8
GEN-2018-062 | 03 - Central | 546682 | EVERETT2 | 69 | 11001 | 11011.7 | 10.7
GEN-2018-062 | 03 - Central | 546684 | FIBGLAS5 | 161 | 17221.9 | 17307.3 | 85.4
GEN-2018-062 | 03 - Central | 546687 | COL PAL2 | 69 | 13715.7 | 13731.7 | 16
GEN-2018-062 | 03 - Central | 546690 | KAW WST2 | 69 | 13570.1 | 13587.3 | 17.2
GEN-2018-062 | 03 - Central | 546692 | QUINDA 2 | 69 | 15016.2 | 15037.1 | 20.9
GEN-2018-062 | 03 - Central | 546693 | V WEST2 | 69 | 10412.1 | 10422.8 | 10.7
GEN-2018-062 | 03 - Central | 546694 | QUINDB 2 | 69 | 14916.8 | 14937.4 | 20.6
GEN-2018-062 | 03 - Central | 546695 | QUINDC 2 | 69 | 14733.9 | 14753.8 | 19.9
GEN-2018-062 | 03 - Central | 546722 | MAYSOTH5 | 161 | 22725.5 | 22860 | 134.5
GEN-2018-062 | 03 - Central | 546742 | METRO 5 | 161 | 27782.7 | 27915.6 | 132.9
GEN-2018-062 | 03 - Central | 546751 | NM4BUS | 161 | 21615.1 | 21900.6 | 285.5
GEN-2018-062 | 03 - Central | 762976 | GEN-2018-062 | 161 | Project Bus - Disconnected | 12490.6 | Project Bus - Disconnected
GEN-2018-003 | 04 - Southeast | 337672 | 4MURFBORO | 138 | 2926.8 | 2918.7 | -8.1
GEN-2018-003 | 04 - Southeast | 508091 | ALUMAX 4 | 138 | 17028.9 | 17151.2 | 122.3
GEN-2018-003 | 04 - Southeast | 509658 | ANDRCKT2 | 69 | 8167.7 | 8362.1 | 194.4
GEN-2018-003 | 04 - Southeast | 508050 | ANDRSNC4 | 138 | 7264.9 | 7514.8 | 249.9
GEN-2018-003 | 04 - Southeast | 508051 | ASHDOWN2 | 69 | 11723.5 | 11777 | 53.5
GEN-2018-003 | 04 - Southeast | 504124 | ASHDWN_W 4 | 138 | 9829.5 | 9912.1 | 82.6
GEN-2018-003 | 04 - Southeast | 507402 | ASHDWNR4 | 138 | 10059.4 | 10144.2 | 84.8
GEN-2018-003 | 04 - Southeast | 508053 | BANN 2 | 69 | 19208.8 | 19299.1 | 90.3
GEN-2018-003 | 04 - Southeast | 508054 | BANN 4 | 138 | 20128 | 20318.7 | 190.7
GEN-2018-003 | 04 - Southeast | 507463 | BARITERDTP 4 | 138 | 3595.2 | 3608.3 | 13.1
GEN-2018-003 | 04 - Southeast | 508056 | BRYANML4 | 138 | 6946.8 | 7074.3 | 127.5
GEN-2018-003 | 04 - Southeast | 509656 | BUCHANN4 | 138 | 6083.7 | 6079.6 | -4.1
GEN-2018-003 | 04 - Southeast | 508287 | BUFORDR2 | 69 | 3885.8 | 3899.9 | 14.1
GEN-2018-003 | 04 - Southeast | 510890 | CRAIGJT4 | 138 | 8708.6 | 8711 | 2.4
GEN-2018-003 | 04 - Southeast | 508289 | DEKALB 2 | 69 | 3957.3 | 3980.1 | 22.8
GEN-2018-003 | 04 - Southeast | 508832 | DIANA 7 | 345 | 18717.2 | 18714.6 | -2.6
GEN-2018-003 | 04 - Southeast | 509655 | EYLAU 4 | 138 | 8577.3 | 8586 | 8.7
GEN-2018-003 | 04 - Southeast | 507421 | FOREMAN2 | 69 | 3692.3 | 3697.4 | 5.1
GEN-2018-003 | 04 - Southeast | 762431 | G18-003-TAP | 138 | 10411.8 | 11246 | 834.2
GEN-2018-003 | 04 - Southeast | 762427 | GEN-2018-003 | 138 | 10411.8 | 11246 | 834.2
GEN-2018-003 | 04 - Southeast | 508057 | HOOKS 2 | 69 | 8063.6 | 8108 | 44.4
GEN-2018-003 | 04 - Southeast | 521157 | HUGO 7 | 345 | 11298.9 | 11219 | -79.9
GEN-2018-003 | 04 - Southeast | 508059 | IPC T 4 | 138 | 8019 | 8021.7 | 2.7
GEN-2018-003 | 04 - Southeast | 508060 | IPC-DOM4 | 138 | 8495.6 | 8500.8 | 5.2
GEN-2018-003 | 04 - Southeast | 508061 | KINGHWY2 | 69 | 11799.2 | 11816.8 | 17.6
GEN-2018-003 | 04 - Southeast | 504123 | LOCKSBRG 4 | 138 | 5825.9 | 5860.4 | 34.5
GEN-2018-003 | 04 - Southeast | 508093 | LSORD 2 | 69 | 7287 | 7316.9 | 29.9
GEN-2018-003 | 04 - Southeast | 508063 | LSORDTP2 | 69 | 8970.1 | 9012.6 | 42.5
GEN-2018-003 | 04 - Southeast | 508298 | LYDIA 7 | 345 | 12551.3 | 12518.5 | -32.8
GEN-2018-003 | 04 - Southeast | 508105 | MANDEVILTP4 | 138 | 9263 | 9281.5 | 18.5
GEN-2018-003 | 04 - Southeast | 509657 | MAUD 2 | 69 | 3369.3 | 3431.6 | 62.3
GEN-2018-003 | 04 - Southeast | 508064 | MUNZCTY4 | 138 | 7071 | 7187.9 | 116.9
GEN-2018-003 | 04 - Southeast | 508049 | NASH 4 | 138 | 19246.7 | 19415.7 | 169
GEN-2018-003 | 04 - Southeast | 508065 | NEKOOSA2 | 69 | 6347.8 | 6366.1 | 18.3
GEN-2018-003 | 04 - Southeast | 504363 | NE-TEXARK2 | 69 | 5303.7 | 5300.2 | -3.5
GEN-2018-003 | 04 - Southeast | 508067 | NEWBOST2 | 69 | 7043.9 | 7126.5 | 82.6
GEN-2018-003 | 04 - Southeast | 508068 | NNBOSTN2 | 69 | 6933.3 | 7025.5 | 92.2
GEN-2018-003 | 04 - Southeast | 508069 | NNBOSTN4 | 138 | 9834.5 | 10529.9 | 695.4
GEN-2018-003 | 04 - Southeast | 508070 | NWT-BNT4 | 138 | 23653.9 | 23957.4 | 303.5
GEN-2018-003 | 04 - Southeast | 508071 | NWTXARK4 | 138 | 24636.3 | 24941.4 | 305.1
GEN-2018-003 | 04 - Southeast | 508072 | NWTXARK7 | 345 | 13088.2 | 13159.5 | 71.3
GEN-2018-003 | 04 - Southeast | 507428 | OKAY 4 | 138 | 9900.8 | 9948.6 | 47.8
GEN-2018-003 | 04 - Southeast | 507429 | PATTERS2 | 69 | 13926 | 14007.1 | 81.1
GEN-2018-003 | 04 - Southeast | 507431 | PATTERS4 | 138 | 12990.9 | 13154.3 | 163.4
GEN-2018-003 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 14161.2 | 14118.5 | -42.7
GEN-2018-003 | 04 - Southeast | 508073 | REDLICK2 | 69 | 16609.6 | 16669 | 59.4
GEN-2018-003 | 04 - Southeast | 508074 | REDRVR-2 | 69 | 7009.2 | 7067 | 57.8
GEN-2018-003 | 04 - Southeast | 508075 | REDSPRG4 | 138 | 13786.1 | 13848.2 | 62.1
GEN-2018-003 | 04 - Southeast | 509654 | REDWATR4 | 138 | 5482.7 | 5476.9 | -5.8
GEN-2018-003 | 04 - Southeast | 508076 | RICHMND2 | 69 | 14324.4 | 14360.1 | 35.7
GEN-2018-003 | 04 - Southeast | 508104 | RIFFIN REC4 | 138 | 9358.9 | 9960.3 | 601.4
GEN-2018-003 | 04 - Southeast | 508077 | SETEXAR2 | 69 | 14527.4 | 14552.8 | 25.4
GEN-2018-003 | 04 - Southeast | 508078 | SETEXAR4 | 138 | 10669.4 | 10698.4 | 29
GEN-2018-003 | 04 - Southeast | 504030 | SFORE_1 2 | 69 | 2822.3 | 2864.7 | 42.4
GEN-2018-003 | 04 - Southeast | 504029 | SFOREMAN 4 | 138 | 8166.1 | 8436.3 | 270.2
GEN-2018-003 | 04 - Southeast | 509659 | SIMMS 2 | 69 | 6539.4 | 6684 | 144.6
GEN-2018-003 | 04 - Southeast | 507434 | SNASHVL4 | 138 | 3714.4 | 3714.2 | -0.2
GEN-2018-003 | 04 - Southeast | 5917 | SPPMAINBUS | 345 | 20559.1 | 20616.3 | 57.2
GEN-2018-003 | 04 - Southeast | 508079 | SUGARHL2 | 69 | 17007.3 | 17060.7 | 53.4
GEN-2018-003 | 04 - Southeast | 508080 | SUGARHL4 | 138 | 11967.8 | 12009.2 | 41.4
GEN-2018-003 | 04 - Southeast | 508081 | SUGHLET2 | 69 | 16321.2 | 16370.2 | 49
GEN-2018-003 | 04 - Southeast | 508082 | SUGHLWT2 | 69 | 16299.3 | 16346.8 | 47.5
GEN-2018-003 | 04 - Southeast | 508086 | TEXARK 2 | 69 | 14936.2 | 14965 | 28.8
GEN-2018-003 | 04 - Southeast | 508087 | TEXOPER2 | 69 | 11536.6 | 11550.9 | 14.3
GEN-2018-003 | 04 - Southeast | 507456 | TURK 3 | 115 | 16450.1 | 16482.9 | 32.8
GEN-2018-003 | 04 - Southeast | 507454 | TURK 4 | 138 | 24085.5 | 24217.3 | 131.8
GEN-2018-003 | 04 - Southeast | 507455 | TURK 7 | 345 | 8898 | 8926.9 | 28.9
GEN-2018-003 | 04 - Southeast | 510918 | VALIANT4 | 138 | 14830.6 | 14735.6 | -95
GEN-2018-003 | 04 - Southeast | 510911 | VALIANT7 | 345 | 13306.9 | 13221.3 | -85.6
GEN-2018-003 | 04 - Southeast | 508359 | WELSH 7 | 345 | 20559.1 | 20616.3 | 57.2
GEN-2018-003 | 04 - Southeast | 508841 | WILKES 7 | 345 | 15083.4 | 15105.6 | 22.2
GEN-2018-011 | 04 - Southeast | 520462 | ASPEN 4 | 138 | 20305.5 | 20313.4 | 7.9
GEN-2018-011 | 04 - Southeast | 514813 | BOWMAN 2 | 69 | 3551.8 | 3556.7 | 4.9
GEN-2018-011 | 04 - Southeast | 514815 | BRECKNR4 | 138 | 15178.1 | 15196.7 | 18.6
GEN-2018-011 | 04 - Southeast | 515960 | BULFOOT4 | 138 | 9118.3 | 9344.1 | 225.8
GEN-2018-011 | 04 - Southeast | 520535 | BULFTTP4 | 138 | 9673.1 | 9927.7 | 254.6
GEN-2018-011 | 04 - Southeast | 520839 | CALUMET4 | 138 | 8531 | 8564.1 | 33.1
GEN-2018-011 | 04 - Southeast | 520502 | CANA 4 | 138 | 10105.4 | 10124.6 | 19.2
GEN-2018-011 | 04 - Southeast | 520843 | CANTON-2 | 69 | 4783.5 | 4781.3 | -2.2
GEN-2018-011 | 04 - Southeast | 520479 | CASHION4 | 138 | 5975.1 | 6000.4 | 25.3
GEN-2018-011 | 04 - Southeast | 520848 | CDRDLTP4 | 138 | 5822.6 | 5828.5 | 5.9
GEN-2018-011 | 04 - Southeast | 520507 | CEDRDAL4 | 138 | 4676 | 4679.7 | 3.7
GEN-2018-011 | 04 - Southeast | 520855 | CLEOSW 2 | 69 | 7744.3 | 7738 | -6.3
GEN-2018-011 | 04 - Southeast | 520865 | CONCHO 4 | 138 | 7187.1 | 7226.2 | 39.1
GEN-2018-011 | 04 - Southeast | 515377 | CRESENT4 | 138 | 10820.1 | 10871.5 | 51.4
GEN-2018-011 | 04 - Southeast | 514827 | CTNWOOD4 | 138 | 18657 | 18695.1 | 38.1
GEN-2018-011 | 04 - Southeast | 515853 | DGRASSE4 | 138 | 16668.6 | 16603 | -65.6
GEN-2018-011 | 04 - Southeast | 520879 | DOVER 4 | 138 | 7699.5 | 7798.6 | 99.1
GEN-2018-011 | 04 - Southeast | 520881 | DOVERSW2 | 69 | 6894.8 | 6951.5 | 56.7
GEN-2018-011 | 04 - Southeast | 520882 | DOVERSW4 | 138 | 10872.9 | 11241.1 | 368.2
GEN-2018-011 | 04 - Southeast | 514772 | DOVERTP2 | 69 | 6006.7 | 6047.7 | 41
GEN-2018-011 | 04 - Southeast | 520890 | EAGLCHF2 | 69 | 4688.6 | 4681.3 | -7.3
GEN-2018-011 | 04 - Southeast | 520600 | EKFSHTP4 | 138 | 8071 | 8159.2 | 88.2
GEN-2018-011 | 04 - Southeast | 520484 | EKNGFSH4 | 138 | 6493 | 6549 | 56
GEN-2018-011 | 04 - Southeast | 520909 | FAIRVEW2 | 69 | 4580.7 | 4580 | -0.7
GEN-2018-011 | 04 - Southeast | 520538 | FAY 4 | 138 | 3169.9 | 3175.3 | 5.4
GEN-2018-011 | 04 - Southeast | 520545 | FOURCTP4 | 138 | 7204.5 | 7246.1 | 41.6
GEN-2018-011 | 04 - Southeast | 514709 | FRMNTAP4 | 138 | 19896.5 | 19934.2 | 37.7
GEN-2018-011 | 04 - Southeast | 587140 | GEN-2016-020 | 138 | 7647.7 | 7648.5 | 0.8
GEN-2018-011 | 04 - Southeast | 587210 | GEN-2016-032 | 138 | 7982.5 | 8001.6 | 19.1
GEN-2018-011 | 04 - Southeast | 587940 | GEN-2016-118 | 138 | 5272.8 | 5332.5 | 59.7
GEN-2018-011 | 04 - Southeast | 762493 | GEN-2018-011 | 138 | 10342.5 | 10711.7 | 369.2
GEN-2018-011 | 04 - Southeast | 514788 | GLASMTN4 | 138 | 5208.2 | 5207.5 | -0.7
GEN-2018-011 | 04 - Southeast | 520940 | HENESEY2 | 69 | 5537.6 | 5575.7 | 38.1
GEN-2018-011 | 04 - Southeast | 514774 | HENESEY4 | 138 | 10100 | 10350.4 | 250.4
GEN-2018-011 | 04 - Southeast | 514790 | IMO 4 | 138 | 12650.8 | 12664.7 | 13.9
GEN-2018-011 | 04 - Southeast | 520957 | IODINE 4 | 138 | 8076.9 | 8076.2 | -0.7
GEN-2018-011 | 04 - Southeast | 520533 | KGFSHSW4 | 138 | 8650.3 | 8733 | 82.7
GEN-2018-011 | 04 - Southeast | 520405 | KGFSJCT4 | 138 | 7890.7 | 7986.2 | 95.5
GEN-2018-011 | 04 - Southeast | 515625 | KNGINDT2 | 69 | 3521.7 | 3525.1 | 3.4
GEN-2018-011 | 04 - Southeast | 520967 | LACEY 2 | 69 | 2572 | 2580.7 | 8.7
GEN-2018-011 | 04 - Southeast | 514733 | MARSHL 4 | 138 | 8237.2 | 8238.6 | 1.4
GEN-2018-011 | 04 - Southeast | 520995 | MOORLND2 | 69 | 8720.1 | 8717 | -3.1
GEN-2018-011 | 04 - Southeast | 520999 | MOORLND4 | 138 | 21071.4 | 21079.9 | 8.5
GEN-2018-011 | 04 - Southeast | 520603 | NKNGFSH4 | 138 | 7954 | 8079.5 | 125.5
GEN-2018-011 | 04 - Southeast | 521015 | OKEENE 2 | 69 | 6467.7 | 6479.5 | 11.8
GEN-2018-011 | 04 - Southeast | 521016 | OKEENE 4 | 138 | 7117.5 | 7158 | 40.5
GEN-2018-011 | 04 - Southeast | 520964 | OMEGA 4 | 138 | 6067.8 | 6096.3 | 28.5
GEN-2018-011 | 04 - Southeast | 529343 | OMFAIRV2 | 69 | 3854 | 3853.2 | -0.8
GEN-2018-011 | 04 - Southeast | 529280 | OMKINGF2 | 69 | 3544.3 | 3549.2 | 4.9
GEN-2018-011 | 04 - Southeast | 514708 | OTTER 4 | 138 | 11571.8 | 11579.6 | 7.8
GEN-2018-011 | 04 - Southeast | 520475 | PARKCOM4 | 138 | 6194.4 | 6229 | 34.6
GEN-2018-011 | 04 - Southeast | 520425 | PIC4 | 138 | 8193.4 | 8198.7 | 5.3
GEN-2018-011 | 04 - Southeast | 515976 | REDWING2 | 69 | 5960 | 6000.4 | 40.4
GEN-2018-011 | 04 - Southeast | 521037 | REEDING4 | 138 | 7115.2 | 7158.8 | 43.6
GEN-2018-011 | 04 - Southeast | 521039 | RNGWODJ2 | 69 | 7048.4 | 7042.1 | -6.3
GEN-2018-011 | 04 - Southeast | 520899 | SCOTTSW4 | 138 | 11923.1 | 11941.6 | 18.5
GEN-2018-011 | 04 - Southeast | 520553 | SEILING4 | 138 | 6860.2 | 6859.5 | -0.7
GEN-2018-011 | 04 - Southeast | 514730 | SO4TH 2 | 69 | 14423.6 | 14429 | 5.4
GEN-2018-011 | 04 - Southeast | 514731 | SO4TH 4 | 138 | 16643.3 | 16678.8 | 35.5
GEN-2018-011 | 04 - Southeast | 520454 | STALOGA2 | 69 | 4507.5 | 4505.5 | -2
GEN-2018-011 | 04 - Southeast | 521064 | TALOGA 2 | 69 | 8343.4 | 8339.9 | -3.5
GEN-2018-011 | 04 - Southeast | 521065 | TALOGA 4 | 138 | 7513.4 | 7512.1 | -1.3
GEN-2018-011 | 04 - Southeast | 514735 | TURCRK 2 | 69 | 5743.7 | 5780.4 | 36.7
GEN-2018-011 | 04 - Southeast | 515517 | TURCRKT2 | 69 | 5769.5 | 5806.5 | 37
GEN-2018-011 | 04 - Southeast | 520540 | TWNLAKE4 | 138 | 10077.3 | 10142.9 | 65.6
GEN-2018-011 | 04 - Southeast | 520847 | TWNLKJT4 | 138 | 7587 | 7629.8 | 42.8
GEN-2018-011 | 04 - Southeast | 521073 | TWNLKSW4 | 138 | 10077.3 | 10142.9 | 65.6
GEN-2018-011 | 04 - Southeast | 521082 | VICI 2 | 69 | 3878.1 | 3875.1 | -3
GEN-2018-011 | 04 - Southeast | 520536 | WATNGSW4 | 138 | 7046.7 | 7081.5 | 34.8
GEN-2018-011 | 04 - Southeast | 521091 | WATONGA4 | 138 | 4457.9 | 4470.3 | 12.4
GEN-2018-011 | 04 - Southeast | 514710 | WAUKOMI4 | 138 | 11128.5 | 11211.3 | 82.8
GEN-2018-011 | 04 - Southeast | 514711 | WAUKOTP4 | 138 | 17031.9 | 17086.5 | 54.6
GEN-2018-011 | 04 - Southeast | 515785 | WINDFRM4 | 138 | 20594.4 | 20602 | 7.6
GEN-2018-011 | 04 - Southeast | 514714 | WOODRNG4 | 138 | 21390 | 21433.6 | 43.6
GEN-2018-011 | 04 - Southeast | 514715 | WOODRNG7 | 345 | 20442.6 | 20446.2 | 3.6
GEN-2018-021 | 04 - Southeast | 520530 | AMBERTP4 | 138 | 8297.6 | 8294.7 | -2.9
GEN-2018-021 | 04 - Southeast | 520810 | ANADARK2 | 69 | 14694.3 | 14695.4 | 1.1
GEN-2018-021 | 04 - Southeast | 520814 | ANADARK4 | 138 | 36919.7 | 36966.8 | 47.1
GEN-2018-021 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 27716.6 | 27798.6 | 82
GEN-2018-021 | 04 - Southeast | 515677 | BADGER 7 | 345 | 11808.7 | 11792 | -16.7
GEN-2018-021 | 04 - Southeast | 520512 | BC SW 4 | 138 | 6492.3 | 6491.8 | -0.5
GEN-2018-021 | 04 - Southeast | 520513 | BCV SW 4 | 138 | 5885.1 | 5885.5 | 0.4
GEN-2018-021 | 04 - Southeast | 520514 | BCVI_HVB | 138 | 7599.9 | 7599.6 | -0.3
GEN-2018-021 | 04 - Southeast | 520827 | BINGERJ4 | 138 | 7987.6 | 7987.5 | -0.1
GEN-2018-021 | 04 - Southeast | 515458 | BORDER 7 | 345 | 7691.5 | 7694 | 2.5
GEN-2018-021 | 04 - Southeast | 511542 | BUFFCK6 | 230 | 6456.6 | 6452 | -4.6
GEN-2018-021 | 04 - Southeast | 520838 | CADDO 2 | 69 | 11491.7 | 11492 | 0.3
GEN-2018-021 | 04 - Southeast | 515605 | CANADN7 | 345 | 13399.5 | 13413.7 | 14.2
GEN-2018-021 | 04 - Southeast | 511445 | CARNEG-4 | 138 | 8037 | 8038.6 | 1.6
GEN-2018-021 | 04 - Southeast | 521129 | CHERRYRD 4 | 138 | 6379.8 | 6380.4 | 0.6
GEN-2018-021 | 04 - Southeast | 514957 | CHERYCK4 | 138 | 22968.9 | 22994 | 25.1
GEN-2018-021 | 04 - Southeast | 511557 | CHISHOLM6 | 230 | 11713.9 | 11717.2 | 3.3
GEN-2018-021 | 04 - Southeast | 511553 | CHISHOLM7 | 345 | 10871.7 | 10897 | 25.3
GEN-2018-021 | 04 - Southeast | 514898 | CIMARON4 | 138 | 46879.8 | 47141.7 | 261.9
GEN-2018-021 | 04 - Southeast | 514901 | CIMARON7 | 345 | 36994.7 | 37158.1 | 163.4
GEN-2018-021 | 04 - Southeast | 520473 | CKSHATP4 | 138 | 11189.9 | 11187.4 | -2.5
GEN-2018-021 | 04 - Southeast | 511446 | CL-AFTP4 | 138 | 6594.8 | 6591.1 | -3.7
GEN-2018-021 | 04 - Southeast | 511485 | CLINTJC4 | 138 | 6320 | 6318 | -2
GEN-2018-021 | 04 - Southeast | 520508 | CLVLDSW4 | 138 | 12851.9 | 12855.3 | 3.4
GEN-2018-021 | 04 - Southeast | 520859 | COGAR 4 | 138 | 9217.6 | 9221.9 | 4.3
GEN-2018-021 | 04 - Southeast | 511437 | COMANC-4 | 138 | 18598.6 | 18665.7 | 67.1
GEN-2018-021 | 04 - Southeast | 511494 | COMMTAP4 | 138 | 22235.4 | 22315.5 | 80.1
GEN-2018-021 | 04 - Southeast | 515448 | CRSRDSW7 | 345 | 12560 | 12552.2 | -7.8
GEN-2018-021 | 04 - Southeast | 514894 | CZECHAL4 | 138 | 29693.3 | 29936.5 | 243.2
GEN-2018-021 | 04 - Southeast | 511544 | DEMPSEY6 | 230 | 5226.6 | 5222 | -4.6
GEN-2018-021 | 04 - Southeast | 515853 | DGRASSE4 | 138 | 16668.6 | 16603 | -65.6
GEN-2018-021 | 04 - Southeast | 515852 | DGRASSE7 | 345 | 15247.6 | 15194.4 | -53.2
GEN-2018-021 | 04 - Southeast | 514933 | DRAPER 4 | 138 | 43020.3 | 43132.9 | 112.6
GEN-2018-021 | 04 - Southeast | 514934 | DRAPER 7 | 345 | 26206.4 | 26290.2 | 83.8
GEN-2018-021 | 04 - Southeast | 511486 | ELGINJT4 | 138 | 10220.4 | 10224.7 | 4.3
GEN-2018-021 | 04 - Southeast | 525850 | ELK_CT1 | 345 | 12374.3 | 12367.3 | -7
GEN-2018-021 | 04 - Southeast | 511490 | ELKCITY6 | 230 | 7460.5 | 7457.1 | -3.4
GEN-2018-021 | 04 - Southeast | 511459 | ELKCTY-2 | 69 | 7186.7 | 7179.8 | -6.9
GEN-2018-021 | 04 - Southeast | 511458 | ELKCTY-4 | 138 | 11494.9 | 11490.9 | -4
GEN-2018-021 | 04 - Southeast | 514819 | EL-RENO4 | 138 | 17315.4 | 17342.9 | 27.5
GEN-2018-021 | 04 - Southeast | 511563 | ELSWORTH 4 | 138 | 10145.7 | 10149.9 | 4.2
GEN-2018-021 | 04 - Southeast | 511511 | FALCNRD4 | 138 | 8012.4 | 8008.1 | -4.3
GEN-2018-021 | 04 - Southeast | 511423 | FLE TAP4 | 138 | 9022.4 | 9024.8 | 2.4
GEN-2018-021 | 04 - Southeast | 520912 | FLETCH-4 | 138 | 7233 | 7226.7 | -6.3
GEN-2018-021 | 04 - Southeast | 515610 | FSHRTAP7 | 345 | 18428.1 | 18459 | 30.9
GEN-2018-021 | 04 - Southeast | 515599 | G07621119-20 | 345 | 13520.8 | 13499 | -21.8
GEN-2018-021 | 04 - Southeast | 560071 | G16-003-TAP | 345 | 15250 | 15226.5 | -23.5
GEN-2018-021 | 04 - Southeast | 560078 | G16-037-TAP | 345 | 10235.1 | 10357.7 | 122.6
GEN-2018-021 | 04 - Southeast | 587744 | G16-091-TAP | 345 | 16130 | 16201.1 | 71.1
GEN-2018-021 | 04 - Southeast | 587794 | G16-097-TAP | 138 | 11834.6 | 11839.4 | 4.8
GEN-2018-021 | 04 - Southeast | 762216 | G17-151TAP | 345 | 7736.5 | 7726.2 | -10.3
GEN-2018-021 | 04 - Southeast | 914902 | G17-152_TAP | 138 | 37684.5 | 37776 | 91.5
GEN-2018-021 | 04 - Southeast | 760938 | G17-171-TAP | 345 | 11452.1 | 11648.9 | 196.8
GEN-2018-021 | 04 - Southeast | 762467 | G18-015-TAP | 345 | 5062.4 | 5051.1 | -11.3
GEN-2018-021 | 04 - Southeast | 563269 | GEN-2015-093 | 345 | 10728.5 | 10745.9 | 17.4
GEN-2018-021 | 04 - Southeast | 587020 | GEN-2016-003 | 345 | 15250 | 15226.5 | -23.5
GEN-2018-021 | 04 - Southeast | 587230 | GEN-2016-037 | 345 | 8944.3 | 9029.1 | 84.8
GEN-2018-021 | 04 - Southeast | 587740 | GEN-2016-091 | 345 | 11095.8 | 11120.8 | 25
GEN-2018-021 | 04 - Southeast | 587770 | GEN-2016-095 | 345 | 11589.9 | 11617.3 | 27.4
GEN-2018-021 | 04 - Southeast | 588560 | GEN-2017-011 | 345 | 12345.4 | 12325.7 | -19.7
GEN-2018-021 | 04 - Southeast | 588760 | GEN-2017-033 | 345 | 3842.7 | 3832.8 | -9.9
GEN-2018-021 | 04 - Southeast | 761229 | GEN-2017-150 | 345 | 23033.5 | 23093.1 | 59.6
GEN-2018-021 | 04 - Southeast | 760939 | GEN-2017-171 | 345 | 11452.1 | 11648.9 | 196.8
GEN-2018-021 | 04 - Southeast | 761250 | GEN-2017-233 | 345 | 23079.1 | 23138.9 | 59.8
GEN-2018-021 | 04 - Southeast | 762570 | GEN-2018-021 | 345 | 9130.2 | 9253.5 | 123.3
GEN-2018-021 | 04 - Southeast | 520923 | GEORGIA4 | 138 | 18785.8 | 18794.5 | 8.7
GEN-2018-021 | 04 - Southeast | 515802 | GRACMNT4 | 138 | 34054.9 | 34095.8 | 40.9
GEN-2018-021 | 04 - Southeast | 515800 | GRACMNT7 | 345 | 19727.6 | 19818.3 | 90.7
GEN-2018-021 | 04 - Southeast | 523771 | GRAPEVINE 6 | 230 | 5779.2 | 5771.9 | -7.3
GEN-2018-021 | 04 - Southeast | 585410 | GREAT_WESTRN | 345 | 9839.7 | 9822.3 | -17.4
GEN-2018-021 | 04 - Southeast | 515825 | GRTWSRN7 | 345 | 10342.9 | 10331.8 | -11.1
GEN-2018-021 | 04 - Southeast | 515961 | GUTHRIE7 | 345 | 14147.7 | 14129.1 | -18.6
GEN-2018-021 | 04 - Southeast | 520440 | HARPER2 | 69 | 13922.3 | 13923 | 0.7
GEN-2018-021 | 04 - Southeast | 514863 | HAYMAKR4 | 138 | 27746.2 | 27929.1 | 182.9
GEN-2018-021 | 04 - Southeast | 514953 | HOLLYWD4 | 138 | 37414.9 | 37505.5 | 90.6
GEN-2018-021 | 04 - Southeast | 514796 | IODINE-4 | 138 | 7531.8 | 7521.9 | -9.9
GEN-2018-021 | 04 - Southeast | 514820 | JENSENT4 | 138 | 18772.4 | 18802.1 | 29.7
GEN-2018-021 | 04 - Southeast | 515394 | KEENAN 4 | 138 | 9057.9 | 9044.7 | -13.2
GEN-2018-021 | 04 - Southeast | 515600 | KNGFSHR7 | 345 | 12288 | 12299.1 | 11.1
GEN-2018-021 | 04 - Southeast | 511466 | L.E.S.-2 | 69 | 16515.4 | 16524.7 | 9.3
GEN-2018-021 | 04 - Southeast | 511467 | L.E.S.-4 | 138 | 25561.1 | 25671.6 | 110.5
GEN-2018-021 | 04 - Southeast | 511468 | L.E.S.-7 | 345 | 13957.6 | 14097.6 | 140
GEN-2018-021 | 04 - Southeast | 511439 | LWSTAP 4 | 138 | 11752.4 | 11765.9 | 13.5
GEN-2018-021 | 04 - Southeast | 515585 | MAMTHPW7 | 345 | 14262.5 | 14253.9 | -8.6
GEN-2018-021 | 04 - Southeast | 515497 | MATHWSN7 | 345 | 34955.7 | 35072.3 | 116.6
GEN-2018-021 | 04 - Southeast | 514902 | MCCLAIN4 | 138 | 37936 | 38027.9 | 91.9
GEN-2018-021 | 04 - Southeast | 515444 | MCNOWND7 | 345 | 23781.2 | 23845.4 | 64.2
GEN-2018-021 | 04 - Southeast | 514801 | MINCO 7 | 345 | 23878.2 | 23943 | 64.8
GEN-2018-021 | 04 - Southeast | 515549 | MNCWND37 | 345 | 14808 | 14827.1 | 19.1
GEN-2018-021 | 04 - Southeast | 515939 | MNCWND47 | 345 | 10556 | 10563 | 7
GEN-2018-021 | 04 - Southeast | 515980 | MNCWND57 | 345 | 7747.4 | 7749.7 | 2.3
GEN-2018-021 | 04 - Southeast | 511483 | NORGE--4 | 138 | 11584.8 | 11581.6 | -3.2
GEN-2018-021 | 04 - Southeast | 514879 | NORTWST4 | 138 | 46201.6 | 46520.6 | 319
GEN-2018-021 | 04 - Southeast | 514880 | NORTWST7 | 345 | 34437.5 | 34597.8 | 160.3
GEN-2018-021 | 04 - Southeast | 555234 | NSUB345 | 345 | 27439.2 | 27532.6 | 93.4
GEN-2018-021 | 04 - Southeast | 511456 | O.K.U.-7 | 345 | 5444.6 | 5435.5 | -9.1
GEN-2018-021 | 04 - Southeast | 511565 | OKLAUN HVDC7 | 345 | 5428.8 | 5419.7 | -9.1
GEN-2018-021 | 04 - Southeast | 521017 | ONEY 4 | 138 | 11270.7 | 11272.5 | 1.8
GEN-2018-021 | 04 - Southeast | 515398 | OUSPRT 4 | 138 | 9772.6 | 9758.1 | -14.5
GEN-2018-021 | 04 - Southeast | 521024 | PARADSE4 | 138 | 6003.3 | 6003.7 | 0.4
GEN-2018-021 | 04 - Southeast | 515951 | PERSIMN7 | 345 | 12262.2 | 12245.1 | -17.1
GEN-2018-021 | 04 - Southeast | 521027 | PINERTP2 | 69 | 4929.4 | 4928.6 | -0.8
GEN-2018-021 | 04 - Southeast | 514929 | PLVALLY4 | 138 | 46680 | 46818 | 138
GEN-2018-021 | 04 - Southeast | 521031 | POCASET4 | 138 | 8197.1 | 8197 | -0.1
GEN-2018-021 | 04 - Southeast | 585430 | PRSIMN_CRK1 | 345 | 11811.9 | 11792.5 | -19.4
GEN-2018-021 | 04 - Southeast | 521116 | REDHLSW4 | 138 | 7262.6 | 7263.1 | 0.5
GEN-2018-021 | 04 - Southeast | 515875 | REDNGTN7 | 345 | 18869.6 | 18880.4 | 10.8
GEN-2018-021 | 04 - Southeast | 511547 | ROARK6 | 230 | 5137 | 5133.1 | -3.9
GEN-2018-021 | 04 - Southeast | 511476 | S.W.S.-2 | 69 | 4312.2 | 4312.4 | 0.2
GEN-2018-021 | 04 - Southeast | 511477 | S.W.S.-4 | 138 | 34996 | 35038.8 | 42.8
GEN-2018-021 | 04 - Southeast | 514895 | SARA 4 | 138 | 20319.7 | 20353.6 | 33.9
GEN-2018-021 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 28591.5 | 28664.8 | 73.3
GEN-2018-021 | 04 - Southeast | 520547 | SEQOYAH4 | 138 | 20594.4 | 20607.9 | 13.5
GEN-2018-021 | 04 - Southeast | 520422 | SEQUOYAHJ4 | 138 | 26258.1 | 26280.5 | 22.4
GEN-2018-021 | 04 - Southeast | 511474 | SHERID4 | 138 | 12563.9 | 12580.8 | 16.9
GEN-2018-021 | 04 - Southeast | 521103 | SLKHILLS 4 | 138 | 7620.3 | 7620 | -0.3
GEN-2018-021 | 04 - Southeast | 515582 | SLNGWND7 | 345 | 8746 | 8739.2 | -6.8
GEN-2018-021 | 04 - Southeast | 514881 | SPRNGCK7 | 345 | 24231.9 | 24289.2 | 57.3
GEN-2018-021 | 04 - Southeast | 511541 | SWEETWT6 | 230 | 8742.5 | 8738.5 | -4
GEN-2018-021 | 04 - Southeast | 515407 | TATONGA7 | 345 | 18219.2 | 18212.2 | -7
GEN-2018-021 | 04 - Southeast | 511568 | TERRYRD7 | 345 | 10464.2 | 10759.4 | 295.2
GEN-2018-021 | 04 - Southeast | 539801 | THISTLE7 | 345 | 16668.2 | 16608.5 | -59.7
GEN-2018-021 | 04 - Southeast | 900001 | TRAVERSE3 | 345 | 7077.2 | 7079.3 | 2.1
GEN-2018-021 | 04 - Southeast | 525830 | TUCO_INT 6 | 230 | 21571.4 | 21575 | 3.6
GEN-2018-021 | 04 - Southeast | 525832 | TUCO_INT 7 | 345 | 12494.6 | 12487.7 | -6.9
GEN-2018-021 | 04 - Southeast | 514992 | TURNER 4 | 138 | 34922.4 | 35007.4 | 85
GEN-2018-021 | 04 - Southeast | 511425 | TUTCONT4 | 138 | 10637 | 10638.6 | 1.6
GEN-2018-021 | 04 - Southeast | 521072 | TUTLETP4 | 138 | 7356.2 | 7355.1 | -1.1
GEN-2018-021 | 04 - Southeast | 511421 | VERDEN 4 | 138 | 10049.9 | 10049.1 | -0.8
GEN-2018-021 | 04 - Southeast | 521088 | WASHITA2 | 69 | 9283.2 | 9283.7 | 0.5
GEN-2018-021 | 04 - Southeast | 521089 | WASHITA4 | 138 | 30895 | 30925.6 | 30.6
GEN-2018-021 | 04 - Southeast | 523776 | WHEELER 3 | 115 | 6743.8 | 6733.4 | -10.4
GEN-2018-021 | 04 - Southeast | 523777 | WHEELER 6 | 230 | 6230 | 6222.1 | -7.9
GEN-2018-021 | 04 - Southeast | 514785 | WOODWRD4 | 138 | 13370.1 | 13353.5 | -16.6
GEN-2018-021 | 04 - Southeast | 755000 | WWDBORDT | 345 | 10844.7 | 10868.8 | 24.1
GEN-2018-021 | 04 - Southeast | 515425 | WWDPST 4 | 138 | 18150.5 | 18124 | -26.5
GEN-2018-021 | 04 - Southeast | 515376 | WWRDEHV4 | 138 | 25334.4 | 25295.8 | -38.6
GEN-2018-021 | 04 - Southeast | 515375 | WWRDEHV7 | 345 | 22067.4 | 22038.4 | -29
GEN-2018-021 | 04 - Southeast | 526936 | YOAKUM_345 | 345 | 9352.4 | 9348.9 | -3.5
GEN-2018-024 | 04 - Southeast | 515228 | 5TRIBES5 | 161 | 15692.5 | 15749.8 | 57.3
GEN-2018-024 | 04 - Southeast | 337909 | 8ANO% | 500 | 18109.2 | 18113 | 3.8
GEN-2018-024 | 04 - Southeast | 515230 | AGENCY 5 | 161 | 14256.4 | 14291.1 | 34.7
GEN-2018-024 | 04 - Southeast | 514907 | ARCADIA4 | 138 | 46415.2 | 46590.2 | 175
GEN-2018-024 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 27716.6 | 27798.6 | 82
GEN-2018-024 | 04 - Southeast | 515306 | ARKOMA 5 | 161 | 16374.7 | 16281.3 | -93.4
GEN-2018-024 | 04 - Southeast | 506944 | CHAMSPR5 | 161 | 23530.6 | 23514.4 | -16.2
GEN-2018-024 | 04 - Southeast | 506945 | CHAMSPR7 | 345 | 10217.7 | 10195.8 | -21.9
GEN-2018-024 | 04 - Southeast | 509745 | CLARKSV7 | 345 | 20231.1 | 20321 | 89.9
GEN-2018-024 | 04 - Southeast | 509834 | COGENT 7 | 345 | 29350.1 | 29519.5 | 169.4
GEN-2018-024 | 04 - Southeast | 510946 | C-RIVER4 | 138 | 13144 | 13112 | -32
GEN-2018-024 | 04 - Southeast | 515422 | C-RIVER7 | 345 | 10106.6 | 10121.1 | 14.5
GEN-2018-024 | 04 - Southeast | 516006 | DMNDSPG7 | 345 | 8018.8 | 7995.2 | -23.6
GEN-2018-024 | 04 - Southeast | 514933 | DRAPER 4 | 138 | 43020.3 | 43132.9 | 112.6
GEN-2018-024 | 04 - Southeast | 514934 | DRAPER 7 | 345 | 26206.4 | 26290.2 | 83.8
GEN-2018-024 | 04 - Southeast | 588839 | FIREWHL-TAP | 345 | 11256.3 | 11439.7 | 183.4
GEN-2018-024 | 04 - Southeast | 515302 | FTSMITH7 | 345 | 10221.9 | 10123.2 | -98.7
GEN-2018-024 | 04 - Southeast | 515305 | FTSMITH8 | 500 | 8594 | 8544.8 | -49.2
GEN-2018-024 | 04 - Southeast | 515300 | FTSMTHE5 | 161 | 23536 | 23399.7 | -136.3
GEN-2018-024 | 04 - Southeast | 515301 | FTSMTHW5 | 161 | 23406.7 | 23269.8 | -136.9
GEN-2018-024 | 04 - Southeast | 588039 | G16133G16146 | 345 | 31623.7 | 31821.2 | 197.5
GEN-2018-024 | 04 - Southeast | 588838 | G17-092-SWYD | 345 | 11256.3 | 11439.7 | 183.4
GEN-2018-024 | 04 - Southeast | 760393 | G17-140-BUS | 345 | 1710.5 | 1710.4 | -0.1
GEN-2018-024 | 04 - Southeast | 588810 | GEN-2017-040 | 345 | 11104.5 | 11282.4 | 177.9
GEN-2018-024 | 04 - Southeast | 589300 | GEN-2017-092 | 345 | 9903.1 | 10040.7 | 137.6
GEN-2018-024 | 04 - Southeast | 760032 | GEN-2017-132 | 345 | 6295.8 | 6298.8 | 3
GEN-2018-024 | 04 - Southeast | 760389 | GEN-2017-140 | 345 | 1721.8 | 1721.7 | -0.1
GEN-2018-024 | 04 - Southeast | 760830 | GEN-2017-149 | 345 | 4100.4 | 4091.9 | -8.5
GEN-2018-024 | 04 - Southeast | 761334 | GEN-2017-155 | 345 | 12056.6 | 12148.8 | 92.2
GEN-2018-024 | 04 - Southeast | 760368 | GEN-2017-213 | 345 | 16334.7 | 16389.4 | 54.7
GEN-2018-024 | 04 - Southeast | 762592 | GEN-2018-024 | 345 | 11044.2 | 11229 | 184.8
GEN-2018-024 | 04 - Southeast | 762823 | GEN-2018-048 | 345 | 15762.5 | 16386.3 | 623.8
GEN-2018-024 | 04 - Southeast | 521157 | HUGO 7 | 345 | 11298.9 | 11219 | -79.9
GEN-2018-024 | 04 - Southeast | 514808 | JOHNCO 4 | 138 | 15979.5 | 15916.1 | -63.4
GEN-2018-024 | 04 - Southeast | 514809 | JOHNCO 7 | 345 | 11293.7 | 11272.2 | -21.5
GEN-2018-024 | 04 - Southeast | 510925 | KIOWA 7 | 345 | 13907.6 | 13864.7 | -42.9
GEN-2018-024 | 04 - Southeast | 515977 | LKKONWA4 | 138 | 39834.9 | 39884.3 | 49.4
GEN-2018-024 | 04 - Southeast | 508298 | LYDIA 7 | 345 | 12551.3 | 12518.5 | -32.8
GEN-2018-024 | 04 - Southeast | 515055 | MAUD 4 | 138 | 20332.4 | 20329.3 | -3.1
GEN-2018-024 | 04 - Southeast | 510908 | MCALEST4 | 138 | 9820.2 | 9785.6 | -34.6
GEN-2018-024 | 04 - Southeast | 510909 | MCALESTIND 4 | 138 | 5663.6 | 5639.9 | -23.7
GEN-2018-024 | 04 - Southeast | 515224 | MUSKOGE7 | 345 | 27171 | 27664 | 493
GEN-2018-024 | 04 - Southeast | 510406 | N.E.S.-7 | 345 | 19054.5 | 19071.3 | 16.8
GEN-2018-024 | 04 - Southeast | 514880 | NORTWST7 | 345 | 34437.5 | 34597.8 | 160.3
GEN-2018-024 | 04 - Southeast | 555234 | NSUB345 | 345 | 27439.2 | 27532.6 | 93.4
GEN-2018-024 | 04 - Southeast | 508072 | NWTXARK7 | 345 | 13088.2 | 13159.5 | 71.3
GEN-2018-024 | 04 - Southeast | 509836 | OEC 7 | 345 | 28822.6 | 28933.7 | 111.1
GEN-2018-024 | 04 - Southeast | 509806 | ONETA--4 | 138 | 49079.3 | 49212.5 | 133.2
GEN-2018-024 | 04 - Southeast | 509807 | ONETA--7 | 345 | 29108.6 | 29222.2 | 113.6
GEN-2018-024 | 04 - Southeast | 515100 | PAOLI- 4 | 138 | 10568 | 10551 | -17
GEN-2018-024 | 04 - Southeast | 515233 | PECANCK4 | 138 | 9818.7 | 9832.4 | 13.7
GEN-2018-024 | 04 - Southeast | 515234 | PECANCK5 | 161 | 21229.9 | 21391 | 161.1
GEN-2018-024 | 04 - Southeast | 515235 | PECANCK7 | 345 | 21209 | 21844.1 | 635.1
GEN-2018-024 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 14161.2 | 14118.5 | -42.7
GEN-2018-024 | 04 - Southeast | 509782 | R.S.S.-7 | 345 | 31623.7 | 31821.2 | 197.5
GEN-2018-024 | 04 - Southeast | 514909 | REDBUD 7 | 345 | 26648.4 | 26715.4 | 67
GEN-2018-024 | 04 - Southeast | 509773 | RSS T1 4 | 138 | 50830.1 | 51049 | 218.9
GEN-2018-024 | 04 - Southeast | 509875 | RSS T2 4 | 138 | 51729.1 | 51956.4 | 227.3
GEN-2018-024 | 04 - Southeast | 509870 | SAPLPRD7 | 345 | 22644.3 | 22719.1 | 74.8
GEN-2018-024 | 04 - Southeast | 515044 | SEMINOL4 | 138 | 40748.6 | 40800.9 | 52.3
GEN-2018-024 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 28591.5 | 28664.8 | 73.3
GEN-2018-024 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12217.7 | 12233.9 | 16.2
GEN-2018-024 | 04 - Southeast | 510951 | TALAWANDA 4 | 138 | 9697.7 | 9662.6 | -35.1
GEN-2018-024 | 04 - Southeast | 506959 | TONTITN7 | 345 | 9204.3 | 9186.7 | -17.6
GEN-2018-024 | 04 - Southeast | 510918 | VALIANT4 | 138 | 14830.6 | 14735.6 | -95
GEN-2018-024 | 04 - Southeast | 510911 | VALIANT7 | 345 | 13306.9 | 13221.3 | -85.6
GEN-2018-024 | 04 - Southeast | 515531 | VANOSTP4 | 138 | 13523 | 13503.7 | -19.3
GEN-2018-026 | 04 - Southeast | 514888 | 36&MER 4 | 138 | 28404.8 | 28619.4 | 214.6
GEN-2018-026 | 04 - Southeast | 514845 | 38TH ST2 | 69 | 18051.7 | 18126.4 | 74.7
GEN-2018-026 | 04 - Southeast | 514846 | 38TH ST4 | 138 | 23527.6 | 24071.4 | 543.8
GEN-2018-026 | 04 - Southeast | 514844 | BELISLE4 | 138 | 28081.4 | 28577.6 | 496.2
GEN-2018-026 | 04 - Southeast | 514914 | BETHANY2 | 69 | 13101.7 | 13133.3 | 31.6
GEN-2018-026 | 04 - Southeast | 514854 | BRADEN 4 | 138 | 32940.7 | 33155.8 | 215.1
GEN-2018-026 | 04 - Southeast | 511576 | CEMRD_TP4 | 138 | 6983.8 | 6983 | -0.8
GEN-2018-026 | 04 - Southeast | 515367 | CHEMTRN4 | 138 | 22083.8 | 22226.3 | 142.5
GEN-2018-026 | 04 - Southeast | 515374 | CHISHOM4 | 138 | 23421.1 | 23552.3 | 131.2
GEN-2018-026 | 04 - Southeast | 514898 | CIMARON4 | 138 | 46879.8 | 47141.7 | 261.9
GEN-2018-026 | 04 - Southeast | 514901 | CIMARON7 | 345 | 36994.7 | 37158.1 | 163.4
GEN-2018-026 | 04 - Southeast | 514922 | CLASSEN4 | 138 | 31635.3 | 31978.5 | 343.2
GEN-2018-026 | 04 - Southeast | 514865 | COUNCIL4 | 138 | 30447 | 30817.4 | 370.4
GEN-2018-026 | 04 - Southeast | 515851 | CROSTWN4 | 138 | 25911.4 | 26107.4 | 196
GEN-2018-026 | 04 - Southeast | 514894 | CZECHAL4 | 138 | 29693.3 | 29936.5 | 243.2
GEN-2018-026 | 04 - Southeast | 514892 | DAYTON 4 | 138 | 26635.6 | 26861.7 | 226.1
GEN-2018-026 | 04 - Southeast | 514868 | DOUGLTP4 | 138 | 31789.1 | 32158.1 | 369
GEN-2018-026 | 04 - Southeast | 514853 | DVISION4 | 138 | 37758 | 38269.9 | 511.9
GEN-2018-026 | 04 - Southeast | 514818 | ELRENO 2 | 69 | 7550.2 | 7546.4 | -3.8
GEN-2018-026 | 04 - Southeast | 514819 | EL-RENO4 | 138 | 17315.4 | 17342.9 | 27.5
GEN-2018-026 | 04 - Southeast | 515610 | FSHRTAP7 | 345 | 18428.1 | 18459 | 30.9
GEN-2018-026 | 04 - Southeast | 762614 | GEN-2018-026 | 115 | 44989.7 | 45755.9 | 766.2
GEN-2018-026 | 04 - Southeast | 762636 | GEN-2018-028 | 138 | 23256.6 | 24159.8 | 903.2
GEN-2018-026 | 04 - Southeast | 514863 | HAYMAKR4 | 138 | 27746.2 | 27929.1 | 182.9
GEN-2018-026 | 04 - Southeast | 514848 | HEFNER 4 | 138 | 25545.8 | 26305.6 | 759.8
GEN-2018-026 | 04 - Southeast | 515338 | HOBBYLO4 | 138 | 25724.1 | 25919.5 | 195.4
GEN-2018-026 | 04 - Southeast | 514821 | JENSEN 4 | 138 | 15828.5 | 15846.4 | 17.9
GEN-2018-026 | 04 - Southeast | 514820 | JENSENT4 | 138 | 18772.4 | 18802.1 | 29.7
GEN-2018-026 | 04 - Southeast | 514977 | KENTUKT2 | 69 | 17368 | 17400.4 | 32.4
GEN-2018-026 | 04 - Southeast | 514976 | KENTUKY2 | 69 | 16721.5 | 16752.4 | 30.9
GEN-2018-026 | 04 - Southeast | 514828 | KETCHTP4 | 138 | 27687.5 | 27833.6 | 146.1
GEN-2018-026 | 04 - Southeast | 514849 | LAKESID4 | 138 | 25502.3 | 26059.5 | 557.2
GEN-2018-026 | 04 - Southeast | 514923 | LIGHTCK4 | 138 | 25421.5 | 25601.6 | 180.1
GEN-2018-026 | 04 - Southeast | 514873 | LNEOAK 4 | 138 | 28202.6 | 28344.7 | 142.1
GEN-2018-026 | 04 - Southeast | 515497 | MATHWSN7 | 345 | 34955.7 | 35072.3 | 116.6
GEN-2018-026 | 04 - Southeast | 514913 | MAY AVE2 | 69 | 16678.3 | 16734.3 | 56
GEN-2018-026 | 04 - Southeast | 514917 | MCARTHR2 | 69 | 11778.2 | 11791.7 | 13.5
GEN-2018-026 | 04 - Southeast | 514902 | MCCLAIN4 | 138 | 37936 | 38027.9 | 91.9
GEN-2018-026 | 04 - Southeast | 514835 | MEMRIAL4 | 138 | 37270.2 | 37758.6 | 488.4
GEN-2018-026 | 04 - Southeast | 514867 | MERIDAN4 | 138 | 24035.8 | 24248.2 | 212.4
GEN-2018-026 | 04 - Southeast | 514801 | MINCO 7 | 345 | 23878.2 | 23943 | 64.8
GEN-2018-026 | 04 - Southeast | 514896 | MORGAN 4 | 138 | 34402.4 | 34839.4 | 437
GEN-2018-026 | 04 - Southeast | 514860 | MSTANG 2 | 69 | 22380.1 | 22440.2 | 60.1
GEN-2018-026 | 04 - Southeast | 514861 | MUSTANG4 | 138 | 40082.5 | 40755.3 | 672.8
GEN-2018-026 | 04 - Southeast | 514879 | NORTWST4 | 138 | 46201.6 | 46520.6 | 319
GEN-2018-026 | 04 - Southeast | 514880 | NORTWST7 | 345 | 34437.5 | 34597.8 | 160.3
GEN-2018-026 | 04 - Southeast | 555234 | NSUB345 | 345 | 27439.2 | 27532.6 | 93.4
GEN-2018-026 | 04 - Southeast | 515506 | OKRCHET2 | 69 | 3709.4 | 3710.4 | 1
GEN-2018-026 | 04 - Southeast | 515962 | OMEGA 4 | 138 | 5833.4 | 5835.8 | 2.4
GEN-2018-026 | 04 - Southeast | 514924 | PENN 2 | 69 | 17873.7 | 17903.7 | 30
GEN-2018-026 | 04 - Southeast | 514925 | PENN 4 | 138 | 30956.7 | 31106.6 | 149.9
GEN-2018-026 | 04 - Southeast | 514864 | PIEDMNT4 | 138 | 23439.7 | 23543.7 | 104
GEN-2018-026 | 04 - Southeast | 514851 | QUAILCK4 | 138 | 30686.1 | 30917.6 | 231.5
GEN-2018-026 | 04 - Southeast | 514862 | RICHRDS4 | 138 | 22722.6 | 22864.2 | 141.6
GEN-2018-026 | 04 - Southeast | 514926 | SANTAFE4 | 138 | 27255.1 | 27364.2 | 109.1
GEN-2018-026 | 04 - Southeast | 514895 | SARA 4 | 138 | 20319.7 | 20353.6 | 33.9
GEN-2018-026 | 04 - Southeast | 514850 | SKYLINE4 | 138 | 33460.9 | 33800.7 | 339.8
GEN-2018-026 | 04 - Southeast | 514852 | SLVRLAK4 | 138 | 34294.5 | 34598.5 | 304
GEN-2018-026 | 04 - Southeast | 514891 | SMITHCO4 | 138 | 26128.4 | 26345.2 | 216.8
GEN-2018-026 | 04 - Southeast | 514870 | STNWAL 4 | 138 | 27284.1 | 27563.6 | 279.5
GEN-2018-026 | 04 - Southeast | 514817 | SVCELRN2 | 69 | 6565.9 | 6562.5 | -3.4
GEN-2018-026 | 04 - Southeast | 514919 | SW 5TH 2 | 69 | 18682.2 | 18738.2 | 56
GEN-2018-026 | 04 - Southeast | 514920 | SW 5TH 4 | 138 | 30884 | 31204.8 | 320.8
GEN-2018-026 | 04 - Southeast | 514918 | SW 64TH2 | 69 | 12446.8 | 12460.8 | 14
GEN-2018-026 | 04 - Southeast | 514975 | SW22ND 2 | 69 | 15789.9 | 15823.2 | 33.3
GEN-2018-026 | 04 - Southeast | 514838 | TENNESE4 | 138 | 24355.6 | 24721.8 | 366.2
GEN-2018-026 | 04 - Southeast | 514963 | TROSPER4 | 138 | 28863.9 | 29060.5 | 196.6
GEN-2018-026 | 04 - Southeast | 514847 | TULSA 4 | 138 | 23263.7 | 24166.9 | 903.2
GEN-2018-026 | 04 - Southeast | 511425 | TUTCONT4 | 138 | 10637 | 10638.6 | 1.6
GEN-2018-026 | 04 - Southeast | 511501 | TUTTLE4 | 138 | 10472.2 | 10473.1 | 0.9
GEN-2018-026 | 04 - Southeast | 514869 | WESTERN4 | 138 | 30832.4 | 31249.5 | 417.1
GEN-2018-026 | 04 - Southeast | 514887 | WESTMOR4 | 138 | 30349.3 | 30446.4 | 97.1
GEN-2018-026 | 04 - Southeast | 514866 | WESTOAK4 | 138 | 25286 | 25529.2 | 243.2
GEN-2018-026 | 04 - Southeast | 514916 | WILROGR2 | 69 | 5968.7 | 5972.9 | 4.2
GEN-2018-026 | 04 - Southeast | 514836 | WILSHIR4 | 138 | 23061.6 | 23584.2 | 522.6
GEN-2018-026 | 04 - Southeast | 514915 | WODLAWN2 | 69 | 13077.1 | 13104.2 | 27.1
GEN-2018-026 | 04 - Southeast | 514889 | WRAIRPT4 | 138 | 26651.5 | 26806.8 | 155.3
GEN-2018-026 | 04 - Southeast | 514893 | XEROX 4 | 138 | 31020.9 | 31326.1 | 305.2
GEN-2018-026 | 04 - Southeast | 514816 | YUKON 2 | 69 | 7492.7 | 7493.4 | 0.7
GEN-2018-027 | 04 - Southeast | 509753 | 116JENK4 | 138 | 42776.5 | 42944.1 | 167.6
GEN-2018-027 | 04 - Southeast | 509775 | 136YALE4 | 138 | 23569.4 | 23612.1 | 42.7
GEN-2018-027 | 04 - Southeast | 509828 | 21STTAP4 | 138 | 29915.3 | 29997.2 | 81.9
GEN-2018-027 | 04 - Southeast | 509724 | 36&OLY-4 | 138 | 33129.8 | 33429 | 299.2
GEN-2018-027 | 04 - Southeast | 509800 | 36LEWIS4 | 138 | 33551.5 | 33789.7 | 238.2
GEN-2018-027 | 04 - Southeast | 509776 | 52DELTP4 | 138 | 33260.8 | 33453.1 | 192.3
GEN-2018-027 | 04 - Southeast | 509856 | 52DEL-W4 | 138 | 12072.2 | 12094.1 | 21.9
GEN-2018-027 | 04 - Southeast | 509814 | 52DELWT4 | 138 | 22872.5 | 22948.8 | 76.3
GEN-2018-027 | 04 - Southeast | 509734 | 53GARN 4 | 138 | 18783.5 | 18815.5 | 32
GEN-2018-027 | 04 - Southeast | 509774 | 53GARNS4 | 138 | 18082 | 18108.9 | 26.9
GEN-2018-027 | 04 - Southeast | 509762 | 53GARNT4 | 138 | 21416.3 | 21458.4 | 42.1
GEN-2018-027 | 04 - Southeast | 509763 | 53GARST4 | 138 | 20514.9 | 20550.2 | 35.3
GEN-2018-027 | 04 - Southeast | 509888 | 72ELWOD4 | 138 | 23453.8 | 23576.1 | 122.3
GEN-2018-027 | 04 - Southeast | 509765 | 77MEMTP4 | 138 | 18221.7 | 18249.7 | 28
GEN-2018-027 | 04 - Southeast | 509766 | 77MEM-W4 | 138 | 23117.2 | 23166.9 | 49.7
GEN-2018-027 | 04 - Southeast | 509810 | 81YALES4 | 138 | 20089 | 20124.9 | 35.9
GEN-2018-027 | 04 - Southeast | 509809 | 81YALTP4 | 138 | 25373.8 | 25433.4 | 59.6
GEN-2018-027 | 04 - Southeast | 509847 | 96YALE-4 | 138 | 27551.9 | 27619.7 | 67.8
GEN-2018-027 | 04 - Southeast | 509767 | B111---4 | 138 | 15994.7 | 16010.5 | 15.8
GEN-2018-027 | 04 - Southeast | 509718 | BAWATAP2 | 69 | 2714.5 | 2712.8 | -1.7
GEN-2018-027 | 04 - Southeast | 515246 | BEELINE2 | 69 | 11928.2 | 11928.5 | 0.3
GEN-2018-027 | 04 - Southeast | 515247 | BEELINE4 | 138 | 22196.6 | 22233.3 | 36.7
GEN-2018-027 | 04 - Southeast | 515242 | BLUEBEL4 | 138 | 17307.5 | 17322.6 | 15.1
GEN-2018-027 | 04 - Southeast | 509749 | CARSN-C4 | 138 | 17164 | 17242.7 | 78.7
GEN-2018-027 | 04 - Southeast | 509756 | CARSN-S4 | 138 | 17795.1 | 17888 | 92.9
GEN-2018-027 | 04 - Southeast | 509739 | CARSN-T4 | 138 | 32580.1 | 32866.6 | 286.5
GEN-2018-027 | 04 - Southeast | 509865 | CARSONT4 | 138 | 12025.7 | 12030.2 | 4.5
GEN-2018-027 | 04 - Southeast | 509834 | COGENT 7 | 345 | 29350.1 | 29519.5 | 169.4
GEN-2018-027 | 04 - Southeast | 509896 | DENV_WTAP4 | 138 | 28036.2 | 28112.8 | 76.6
GEN-2018-027 | 04 - Southeast | 509742 | DENVR-C4 | 138 | 12900.1 | 12948.7 | 48.6
GEN-2018-027 | 04 - Southeast | 509748 | DENVR-W4 | 138 | 9607.8 | 9613.1 | 5.3
GEN-2018-027 | 04 - Southeast | 509795 | DX----E2 | 69 | 5257.5 | 5261.5 | 4
GEN-2018-027 | 04 - Southeast | 509796 | DX----W2 | 69 | 3805.2 | 3803.7 | -1.5
GEN-2018-027 | 04 - Southeast | 509831 | E.61ST-4 | 138 | 24552.3 | 24610.8 | 58.5
GEN-2018-027 | 04 - Southeast | 510923 | EC.HEN-4 | 138 | 8587 | 8573.1 | -13.9
GEN-2018-027 | 04 - Southeast | 510904 | EXP_OKM4 | 138 | 9882.5 | 9876.8 | -5.7
GEN-2018-027 | 04 - Southeast | 515473 | EXPGLNT4 | 138 | 24478 | 24524.6 | 46.6
GEN-2018-027 | 04 - Southeast | 515248 | EXPLGLN4 | 138 | 24041.7 | 24086.6 | 44.9
GEN-2018-027 | 04 - Southeast | 509772 | FORD---4 | 138 | 18319.6 | 18344.2 | 24.6
GEN-2018-027 | 04 - Southeast | 509829 | FULTONW4 | 138 | 17148.5 | 17178.5 | 30
GEN-2018-027 | 04 - Southeast | 588039 | G16133G16146 | 345 | 31623.7 | 31821.2 | 197.5
GEN-2018-027 | 04 - Southeast | 762629 | G18-027-TAP | 138 | 38238.4 | 38755.2 | 516.8
GEN-2018-027 | 04 - Southeast | 762625 | GEN-2018-027 | 138 | 32957.2 | 33456.1 | 498.9
GEN-2018-027 | 04 - Southeast | 510892 | HENRYET4 | 138 | 8527.5 | 8514.1 | -13.4
GEN-2018-027 | 04 - Southeast | 509821 | HWY20-T4 | 138 | 3947.6 | 3947 | -0.6
GEN-2018-027 | 04 - Southeast | 509759 | JENKS--4 | 138 | 25452.5 | 25521.5 | 69
GEN-2018-027 | 04 - Southeast | 510931 | KELCO 4 | 138 | 10150.6 | 10141.2 | -9.4
GEN-2018-027 | 04 - Southeast | 509830 | KENSH-E-TP4 | 138 | 20320.4 | 20363.4 | 43
GEN-2018-027 | 04 - Southeast | 509777 | KENSH-W4 | 138 | 14985.8 | 15051.6 | 65.8
GEN-2018-027 | 04 - Southeast | 509845 | KIMCLRK4 | 138 | 22361.5 | 22399.3 | 37.8
GEN-2018-027 | 04 - Southeast | 515245 | LONESTR4 | 138 | 13357.1 | 13366.8 | 9.7
GEN-2018-027 | 04 - Southeast | 509780 | MAYO--S4 | 138 | 21370 | 21409.4 | 39.4
GEN-2018-027 | 04 - Southeast | 509760 | MINGO-N4 | 138 | 27460.1 | 27522.4 | 62.3
GEN-2018-027 | 04 - Southeast | 509761 | MINGO-S4 | 138 | 25671.5 | 25734.6 | 63.1
GEN-2018-027 | 04 - Southeast | 509727 | OAKS W4 | 138 | 15639.3 | 15695.6 | 56.3
GEN-2018-027 | 04 - Southeast | 509846 | OAKS--E4 | 138 | 13941.5 | 14001.7 | 60.2
GEN-2018-027 | 04 - Southeast | 509850 | OAKSETP4 | 138 | 29489.8 | 29753.8 | 264
GEN-2018-027 | 04 - Southeast | 509848 | OAKSWTP4 | 138 | 25026.4 | 25171.3 | 144.9
GEN-2018-027 | 04 - Southeast | 509751 | OGMARTN2 | 69 | 5431.4 | 5435.6 | 4.2
GEN-2018-027 | 04 - Southeast | 510898 | OKMULGE4 | 138 | 11373.8 | 11365.5 | -8.3
GEN-2018-027 | 04 - Southeast | 509807 | ONETA--7 | 345 | 29108.6 | 29222.2 | 113.6
GEN-2018-027 | 04 - Southeast | 509738 | ORU E4 | 138 | 24719 | 24773 | 54
GEN-2018-027 | 04 - Southeast | 509732 | ORU W4 | 138 | 23396.8 | 23445.7 | 48.9
GEN-2018-027 | 04 - Southeast | 509849 | ORU ETP4 | 138 | 34179.7 | 34283.1 | 103.4
GEN-2018-027 | 04 - Southeast | 509853 | ORU-WTP4 | 138 | 29947.4 | 30027.9 | 80.5
GEN-2018-027 | 04 - Southeast | 515235 | PECANCK7 | 345 | 21209 | 21844.1 | 635.1
GEN-2018-027 | 04 - Southeast | 509758 | PRATTV-4 | 138 | 20517.6 | 20551 | 33.4
GEN-2018-027 | 04 - Southeast | 509783 | R.S.S.-4 | 138 | 61175.5 | 61503.5 | 328
GEN-2018-027 | 04 - Southeast | 509782 | R.S.S.-7 | 345 | 31623.7 | 31821.2 | 197.5
GEN-2018-027 | 04 - Southeast | 514909 | REDBUD 7 | 345 | 26648.4 | 26715.4 | 67
GEN-2018-027 | 04 - Southeast | 509773 | RSS T1 4 | 138 | 50830.1 | 51049 | 218.9
GEN-2018-027 | 04 - Southeast | 509875 | RSS T2 4 | 138 | 51729.1 | 51956.4 | 227.3
GEN-2018-027 | 04 - Southeast | 509859 | S HILLW4 | 138 | 16792.1 | 16833.8 | 41.7
GEN-2018-027 | 04 - Southeast | 509731 | S.HIL E4 | 138 | 21541.8 | 21583.3 | 41.5
GEN-2018-027 | 04 - Southeast | 509833 | S.HUD.-4 | 138 | 28853.9 | 28938.1 | 84.2
GEN-2018-027 | 04 - Southeast | 509816 | S.S.---2 | 69 | 6316.9 | 6315.3 | -1.6
GEN-2018-027 | 04 - Southeast | 509815 | S.S.---4 | 138 | 28757.6 | 28838 | 80.4
GEN-2018-027 | 04 - Southeast | 509808 | S21ST--4 | 138 | 20493.1 | 20529.8 | 36.7
GEN-2018-027 | 04 - Southeast | 509716 | S52DEL 4 | 138 | 20098.9 | 20168.2 | 69.3
GEN-2018-027 | 04 - Southeast | 509871 | SAPLPRD4 | 138 | 33107 | 33259 | 152
GEN-2018-027 | 04 - Southeast | 509870 | SAPLPRD7 | 345 | 22644.3 | 22719.1 | 74.8
GEN-2018-027 | 04 - Southeast | 509812 | SHEFFD-4 | 138 | 25993.9 | 26052 | 58.1
GEN-2018-027 | 04 - Southeast | 509813 | SHILETP4 | 138 | 27970.3 | 28041 | 70.7
GEN-2018-027 | 04 - Southeast | 514803 | SOONER 7 | 345 | 29241.4 | 29219.7 | -21.7
GEN-2018-027 | 04 - Southeast | 509852 | T.NO.--7 | 345 | 24027.3 | 24032.9 | 5.6
GEN-2018-027 | 04 - Southeast | 509789 | T.P.S.-2 | 69 | 9131 | 9142.8 | 11.8
GEN-2018-027 | 04 - Southeast | 509788 | T.P.S.-4 | 138 | 39555.8 | 40019.8 | 464
GEN-2018-027 | 04 - Southeast | 509820 | T.S.E.-2 | 69 | 6355.3 | 6362 | 6.7
GEN-2018-027 | 04 - Southeast | 509811 | T.S.E.-4 | 138 | 39018.7 | 39184.7 | 166
GEN-2018-027 | 04 - Southeast | 515237 | TIBBENS4 | 138 | 17533.3 | 17554.5 | 21.2
GEN-2018-027 | 04 - Southeast | 509740 | UNIONAV4 | 138 | 20985.3 | 21103.4 | 118.1
GEN-2018-027 | 04 - Southeast | 509858 | WARNTAP4 | 138 | 28822.3 | 28896.3 | 74
GEN-2018-027 | 04 - Southeast | 509823 | WED-TAP4 | 138 | 19241.5 | 19262.1 | 20.6
GEN-2018-027 | 04 - Southeast | 509757 | WEKIWA-4 | 138 | 32596.1 | 32624.9 | 28.8
GEN-2018-027 | 04 - Southeast | 509755 | WEKIWA-7 | 345 | 22309.7 | 22339.1 | 29.4
GEN-2018-027 | 04 - Southeast | 510902 | WELETK4 | 138 | 14724.4 | 14697.9 | -26.5
GEN-2018-027 | 04 - Southeast | 509754 | WHORSE-4 | 138 | 3938.9 | 3938.3 | -0.6
GEN-2018-027 | 04 - Southeast | 509750 | WILLPIP2 | 69 | 5464 | 5468.2 | 4.2
GEN-2018-027 | 04 - Southeast | 509897 | WLDCT_HIL4 | 138 | 3939.8 | 3939.2 | -0.6
GEN-2018-027 | 04 - Southeast | 509764 | WRNMEDT4 | 138 | 25542.7 | 25605.1 | 62.4
GEN-2018-027 | 04 - Southeast | 509824 | YARCH-S4 | 138 | 14587.7 | 14608.9 | 21.2
GEN-2018-027 | 04 - Southeast | 509826 | ZUNIS-S4 | 138 | 16061 | 16104.8 | 43.8
GEN-2018-028 | 04 - Southeast | 509869 | 121LYNN4 | 138 | 17761.5 | 17781.3 | 19.8
GEN-2018-028 | 04 - Southeast | 300927 | 2CLEVLND | 69 | 9843.5 | 9826.6 | -16.9
GEN-2018-028 | 04 - Southeast | 509837 | 46ST--E4 | 138 | 2925.1 | 2922.6 | -2.5
GEN-2018-028 | 04 - Southeast | 509900 | 46ST-TP-4 | 138 | 9657 | 9650.3 | -6.7
GEN-2018-028 | 04 - Southeast | 300138 | 4CLEVLND | 138 | 16798.9 | 16775.7 | -23.2
GEN-2018-028 | 04 - Southeast | 300131 | 4FISHERTP | 138 | 14988.9 | 14982.4 | -6.5
GEN-2018-028 | 04 - Southeast | 300996 | 4JAVINE | 138 | 6509.5 | 6497.4 | -12.1
GEN-2018-028 | 04 - Southeast | 300140 | 4SILVCTY | 138 | 15841.4 | 15827.1 | -14.3
GEN-2018-028 | 04 - Southeast | 509888 | 72ELWOD4 | 138 | 23453.8 | 23576.1 | 122.3
GEN-2018-028 | 04 - Southeast | 300739 | 7BLACKBERRY | 345 | 15173.9 | 15105.1 | -68.8
GEN-2018-028 | 04 - Southeast | 300740 | 7SPORTSMAN | 345 | 24130.1 | 24132 | 1.9
GEN-2018-028 | 04 - Southeast | 509784 | A.A.---4 | 138 | 16811.4 | 16802.6 | -8.8
GEN-2018-028 | 04 - Southeast | 510429 | ALWUETP4 | 138 | 5762.9 | 5751 | -11.9
GEN-2018-028 | 04 - Southeast | 509786 | BA.N-ST4 | 138 | 23890.4 | 23902.4 | 12
GEN-2018-028 | 04 - Southeast | 509891 | BA_71ST4 | 138 | 23300.6 | 23332.7 | 32.1
GEN-2018-028 | 04 - Southeast | 509769 | BA101-N4 | 138 | 19699.3 | 19722.5 | 23.2
GEN-2018-028 | 04 - Southeast | 509768 | BA101ST4 | 138 | 18808.2 | 18827.9 | 19.7
GEN-2018-028 | 04 - Southeast | 510433 | BARNPMP4 | 138 | 6609.6 | 6599.7 | -9.9
GEN-2018-028 | 04 - Southeast | 510388 | BARNSAL4 | 138 | 6650.1 | 6640.6 | -9.5
GEN-2018-028 | 04 - Southeast | 509899 | BIRDCREE-4 | 138 | 17232.5 | 17226.8 | -5.7
GEN-2018-028 | 04 - Southeast | 510394 | BLUESTM4 | 138 | 8312.8 | 8296.2 | -16.6
GEN-2018-028 | 04 - Southeast | 510390 | BV-COM-4 | 138 | 10150.6 | 10130.9 | -19.7
GEN-2018-028 | 04 - Southeast | 510391 | BV-SE--4 | 138 | 12053.1 | 12030.3 | -22.8
GEN-2018-028 | 04 - Southeast | 509865 | CARSONT4 | 138 | 12025.7 | 12030.2 | 4.5
GEN-2018-028 | 04 - Southeast | 509799 | CATOOSA2 | 69 | 10370.7 | 10361.7 | -9
GEN-2018-028 | 04 - Southeast | 509790 | CATOOSA4 | 138 | 35707.5 | 35710 | 2.5
GEN-2018-028 | 04 - Southeast | 512638 | CATSAGR5 | 161 | 23810.7 | 23811.4 | 0.7
GEN-2018-028 | 04 - Southeast | 509715 | CDC 4 | 138 | 13508.3 | 13500.1 | -8.2
GEN-2018-028 | 04 - Southeast | 509839 | CDC-ET 4 | 138 | 18788.3 | 18779.3 | -9
GEN-2018-028 | 04 - Southeast | 509842 | CDC-WT 4 | 138 | 19555.6 | 19546.4 | -9.2
GEN-2018-028 | 04 - Southeast | 506945 | CHAMSPR7 | 345 | 10217.7 | 10195.8 | -21.9
GEN-2018-028 | 04 - Southeast | 510410 | CHELSA4 | 138 | 6022.2 | 6010.5 | -11.7
GEN-2018-028 | 04 - Southeast | 509714 | CIP 4 | 138 | 13517.7 | 13509.5 | -8.2
GEN-2018-028 | 04 - Southeast | 509745 | CLARKSV7 | 345 | 20231.1 | 20321 | 89.9
GEN-2018-028 | 04 - Southeast | 512707 | CLARMR 4 | 138 | 13281.2 | 13271.6 | -9.6
GEN-2018-028 | 04 - Southeast | 512651 | CLARMR 5 | 161 | 12752.9 | 12742 | -10.9
GEN-2018-028 | 04 - Southeast | 509864 | CLARTOK4 | 138 | 13714.4 | 13709.6 | -4.8
GEN-2018-028 | 04 - Southeast | 512729 | CLEVLND 4 | 138 | 16799 | 16775.8 | -23.2
GEN-2018-028 | 04 - Southeast | 512694 | CLEVLND7 | 345 | 15119.9 | 15104.6 | -15.3
GEN-2018-028 | 04 - Southeast | 509834 | COGENT 7 | 345 | 29350.1 | 29519.5 | 169.4
GEN-2018-028 | 04 - Southeast | 513590 | CUSTDAY1 5 | 161 | 16318.3 | 16314.9 | -3.4
GEN-2018-028 | 04 - Southeast | 509787 | DAWSN-N4 | 138 | 17629.2 | 17620.6 | -8.6
GEN-2018-028 | 04 - Southeast | 510379 | DELWARE4 | 138 | 11042.3 | 11016.6 | -25.7
GEN-2018-028 | 04 - Southeast | 510380 | DELWARE7 | 345 | 11721.1 | 11695.9 | -25.2
GEN-2018-028 | 04 - Southeast | 509896 | DENV_WTAP4 | 138 | 28036.2 | 28112.8 | 76.6
GEN-2018-028 | 04 - Southeast | 509743 | DENVR-E4 | 138 | 8006 | 8000.3 | -5.7
GEN-2018-028 | 04 - Southeast | 509746 | DENVTAP4 | 138 | 9391.2 | 9384.8 | -6.4
GEN-2018-028 | 04 - Southeast | 512734 | FARML 4 | 138 | 8428.1 | 8409.9 | -18.2
GEN-2018-028 | 04 - Southeast | 516066 | FRNT2WD7 | 345 | 11577.3 | 11545.4 | -31.9
GEN-2018-028 | 04 - Southeast | 515688 | FRNTWND7 | 345 | 11970 | 11937.1 | -32.9
GEN-2018-028 | 04 - Southeast | 560056 | G15-066T | 345 | 19544.5 | 19524.8 | -19.7
GEN-2018-028 | 04 - Southeast | 587804 | G16-119-TAP | 345 | 16400.5 | 16395.5 | -5
GEN-2018-028 | 04 - Southeast | 588039 | G16133G16146 | 345 | 31623.7 | 31821.2 | 197.5
GEN-2018-028 | 04 - Southeast | 532777 | G17-009-TAP | 345 | 11568.3 | 11530.9 | -37.4
GEN-2018-028 | 04 - Southeast | 760921 | G17-209-TAP | 345 | 18923 | 18885.4 | -37.6
GEN-2018-028 | 04 - Southeast | 762687 | G18-032_DUMY | 345 | 17450.3 | 17395.3 | -55
GEN-2018-028 | 04 - Southeast | 560389 | GEN-2010-055 | 138 | 32596.1 | 32624.9 | 28.8
GEN-2018-028 | 04 - Southeast | 585040 | GEN-2015-066 | 345 | 19352.8 | 19333.2 | -19.6
GEN-2018-028 | 04 - Southeast | 587950 | GEN-2016-119 | 345 | 10180.3 | 10175.5 | -4.8
GEN-2018-028 | 04 - Southeast | 760389 | GEN-2017-140 | 345 | 1721.8 | 1721.7 | -0.1
GEN-2018-028 | 04 - Southeast | 760368 | GEN-2017-213 | 345 | 16334.7 | 16389.4 | 54.7
GEN-2018-028 | 04 - Southeast | 512656 | GRDA1 5 | 161 | 43972.1 | 43962.6 | -9.5
GEN-2018-028 | 04 - Southeast | 512650 | GRDA1 7 | 345 | 26527.7 | 26536.4 | 8.7
GEN-2018-028 | 04 - Southeast | 512865 | GREC TAP5 | 345 | 25318.7 | 25325.3 | 6.6
GEN-2018-028 | 04 - Southeast | 510413 | HAWTHRN4 | 138 | 20268 | 20262 | -6
GEN-2018-028 | 04 - Southeast | 513591 | HERRON 5 | 161 | 16725.1 | 16721.7 | -3.4
GEN-2018-028 | 04 - Southeast | 513596 | IGLOOV 7 | 345 | 20039.7 | 20039.9 | 0.2
GEN-2018-028 | 04 - Southeast | 513593 | IGLOOV1 5 | 161 | 16913 | 16909.6 | -3.4
GEN-2018-028 | 04 - Southeast | 513595 | IGLOOV2 5 | 161 | 16913 | 16909.6 | -3.4
GEN-2018-028 | 04 - Southeast | 509752 | INOLATP4 | 138 | 9397.8 | 9386.7 | -11.1
GEN-2018-028 | 04 - Southeast | 509759 | JENKS--4 | 138 | 25452.5 | 25521.5 | 69
GEN-2018-028 | 04 - Southeast | 505610 | KEYSTON4 | 138 | 22636.7 | 22640.8 | 4.1
GEN-2018-028 | 04 - Southeast | 505609 | KEYSTON5 | 161 | 7144.5 | 7139.9 | -4.6
GEN-2018-028 | 04 - Southeast | 516019 | KINGWD 7 | 345 | 17489 | 17498.3 | 9.3
GEN-2018-028 | 04 - Southeast | 509771 | LLAN ET4 | 138 | 24341.9 | 24344.6 | 2.7
GEN-2018-028 | 04 - Southeast | 509804 | LLANETP4 | 138 | 27181.2 | 27179.2 | -2
GEN-2018-028 | 04 - Southeast | 514704 | MILLERT4 | 138 | 20910 | 20910.1 | 0.1
GEN-2018-028 | 04 - Southeast | 509802 | MINGORD4 | 138 | 16826.6 | 16817.9 | -8.7
GEN-2018-028 | 04 - Southeast | 509801 | MOHAWK 4 | 138 | 11017 | 11009.7 | -7.3
GEN-2018-028 | 04 - Southeast | 515447 | MORISNT4 | 138 | 14195.5 | 14190.2 | -5.3
GEN-2018-028 | 04 - Southeast | 510395 | MOUNDRD4 | 138 | 9194.4 | 9178.7 | -15.7
GEN-2018-028 | 04 - Southeast | 515224 | MUSKOGE7 | 345 | 27171 | 27664 | 493
GEN-2018-028 | 04 - Southeast | 510396 | N.E.S.-4 | 138 | 35552.9 | 35562.1 | 9.2
GEN-2018-028 | 04 - Southeast | 510406 | N.E.S.-7 | 345 | 19054.5 | 19071.3 | 16.8
GEN-2018-028 | 04 - Southeast | 510386 | NBVILLE4 | 138 | 9354.3 | 9333 | -21.3
GEN-2018-028 | 04 - Southeast | 533021 | NEOSHO 4 | 138 | 24603.7 | 24531.9 | -71.8
GEN-2018-028 | 04 - Southeast | 532937 | NEOSHO 5 | 161 | 22375.2 | 22312.6 | -62.6
GEN-2018-028 | 04 - Southeast | 532793 | NEOSHO 7 | 345 | 17450.3 | 17395.3 | -55
GEN-2018-028 | 04 - Southeast | 510397 | NOWATA-4 | 138 | 8387.9 | 8377.8 | -10.1
GEN-2018-028 | 04 - Southeast | 509848 | OAKSWTP4 | 138 | 25026.4 | 25171.3 | 144.9
GEN-2018-028 | 04 - Southeast | 509836 | OEC 7 | 345 | 28822.6 | 28933.7 | 111.1
GEN-2018-028 | 04 - Southeast | 529200 | OMCDLEC7 | 345 | 14676.4 | 14636.7 | -39.7
GEN-2018-028 | 04 - Southeast | 509806 | ONETA--4 | 138 | 49079.3 | 49212.5 | 133.2
GEN-2018-028 | 04 - Southeast | 509807 | ONETA--7 | 345 | 29108.6 | 29222.2 | 113.6
GEN-2018-028 | 04 - Southeast | 513124 | OOLOGAHKM 4 | 138 | 20520.6 | 20518 | -2.6
GEN-2018-028 | 04 - Southeast | 515621 | OPENSKY7 | 345 | 12827.2 | 12788.1 | -39.1
GEN-2018-028 | 04 - Southeast | 509860 | OWAS1094 | 138 | 14474.1 | 14470.5 | -3.6
GEN-2018-028 | 04 - Southeast | 509887 | OWAS88_4 | 138 | 16722.2 | 16713.5 | -8.7
GEN-2018-028 | 04 - Southeast | 509726 | OWASO1_4 | 138 | 14002.7 | 13997.8 | -4.9
GEN-2018-028 | 04 - Southeast | 509843 | OWASO2_4 | 138 | 14016.7 | 14013.3 | -3.4
GEN-2018-028 | 04 - Southeast | 509844 | OWASOTP4 | 138 | 15066 | 15061 | -5
GEN-2018-028 | 04 - Southeast | 509851 | P&P WTP4 | 138 | 15290.1 | 15287.2 | -2.9
GEN-2018-028 | 04 - Southeast | 512749 | PAWNSW4 | 138 | 9941.6 | 9927.9 | -13.7
GEN-2018-028 | 04 - Southeast | 509841 | PCATSAT4 | 138 | 17797.7 | 17792.1 | -5.6
GEN-2018-028 | 04 - Southeast | 515235 | PECANCK7 | 345 | 21209 | 21844.1 | 635.1
GEN-2018-028 | 04 - Southeast | 514707 | PERRY 4 | 138 | 11508.6 | 11506.8 | -1.8
GEN-2018-028 | 04 - Southeast | 516010 | PINTAIL7 | 345 | 17551.1 | 17560.3 | 9.2
GEN-2018-028 | 04 - Southeast | 509818 | PP----E4 | 138 | 7822 | 7816.3 | -5.7
GEN-2018-028 | 04 - Southeast | 509863 | PPTAP 4 | 138 | 10435.4 | 10428.4 | -7
GEN-2018-028 | 04 - Southeast | 509805 | PP----W4 | 138 | 8417.9 | 8414.1 | -3.8
GEN-2018-028 | 04 - Southeast | 509782 | R.S.S.-7 | 345 | 31623.7 | 31821.2 | 197.5
GEN-2018-028 | 04 - Southeast | 515576 | RANCHRD7 | 345 | 14704.7 | 14664.9 | -39.8
GEN-2018-028 | 04 - Southeast | 514909 | REDBUD 7 | 345 | 26648.4 | 26715.4 | 67
GEN-2018-028 | 04 - Southeast | 510385 | RICE CK4 | 138 | 11231.4 | 11211.8 | -19.6
GEN-2018-028 | 04 - Southeast | 509773 | RSS T1 4 | 138 | 50830.1 | 51049 | 218.9
GEN-2018-028 | 04 - Southeast | 509875 | RSS T2 4 | 138 | 51729.1 | 51956.4 | 227.3
GEN-2018-028 | 04 - Southeast | 509815 | S.S.---4 | 138 | 28757.6 | 28838 | 80.4
GEN-2018-028 | 04 - Southeast | 509871 | SAPLPRD4 | 138 | 33107 | 33259 | 152
GEN-2018-028 | 04 - Southeast | 509870 | SAPLPRD7 | 345 | 22644.3 | 22719.1 | 74.8
GEN-2018-028 | 04 - Southeast | 509812 | SHEFFD-4 | 138 | 25993.9 | 26052 | 58.1
GEN-2018-028 | 04 - Southeast | 512726 | SILVCTYGR4 | 138 | 15688 | 15673.9 | -14.1
GEN-2018-028 | 04 - Southeast | 509884 | SKIATOK4 | 138 | 10524.7 | 10514.7 | -10
GEN-2018-028 | 04 - Southeast | 514798 | SNRPMPT4 | 138 | 20950.8 | 20950.8 | 0
GEN-2018-028 | 04 - Southeast | 514802 | SOONER 4 | 138 | 32499.7 | 32507.6 | 7.9
GEN-2018-028 | 04 - Southeast | 514803 | SOONER 7 | 345 | 29241.4 | 29219.7 | -21.7
GEN-2018-028 | 04 - Southeast | 509722 | SPNKY CK4 | 138 | 30173.2 | 30170.2 | -3
GEN-2018-028 | 04 - Southeast | 514881 | SPRNGCK7 | 345 | 24231.9 | 24289.2 | 57.3
GEN-2018-028 | 04 - Southeast | 509895 | T.NO.2-4 | 138 | 34856.9 | 34852.3 | -4.6
GEN-2018-028 | 04 - Southeast | 509817 | T.NO.--4 | 138 | 34909.1 | 34904.7 | -4.4
GEN-2018-028 | 04 - Southeast | 509852 | T.NO.--7 | 345 | 24027.3 | 24032.9 | 5.6
GEN-2018-028 | 04 - Southeast | 509835 | TERNITP4 | 138 | 15907.5 | 15901.4 | -6.1
GEN-2018-028 | 04 - Southeast | 515894 | THUNDER7 | 345 | 11830 | 11817.7 | -12.3
GEN-2018-028 | 04 - Southeast | 512750 | TONECE7 | 345 | 15062 | 15045.7 | -16.3
GEN-2018-028 | 04 - Southeast | 509854 | VERDIGS4 | 138 | 13719.3 | 13714.4 | -4.9
GEN-2018-028 | 04 - Southeast | 509822 | W.ED.-E4 | 138 | 7843.2 | 7837.6 | -5.6
GEN-2018-028 | 04 - Southeast | 510384 | WATOVA 4 | 138 | 9040.5 | 9032.7 | -7.8
GEN-2018-028 | 04 - Southeast | 509823 | WED-TAP4 | 138 | 19241.5 | 19262.1 | 20.6
GEN-2018-028 | 04 - Southeast | 509757 | WEKIWA-4 | 138 | 32596.1 | 32624.9 | 28.8
GEN-2018-028 | 04 - Southeast | 509755 | WEKIWA-7 | 345 | 22309.7 | 22339.1 | 29.4
GEN-2018-028 | 04 - Southeast | 509840 | WHIRLPO4 | 138 | 18512.7 | 18503.5 | -9.2
GEN-2018-028 | 04 - Southeast | 514715 | WOODRNG7 | 345 | 20442.6 | 20446.2 | 3.6
GEN-2018-028 | 04 - Southeast | 509825 | YARCH-N4 | 138 | 6749 | 6743.9 | -5.1
GEN-2018-028 | 04 - Southeast | 509862 | YARCHT 4 | 138 | 8824.2 | 8817.9 | -6.3
GEN-2018-029 | 04 - Southeast | 300834 | 2CARNEY | 69 | 4875.7 | 4867.6 | -8.1
GEN-2018-029 | 04 - Southeast | 300856 | 2LUTHER | 69 | 6528.7 | 6527.6 | -1.1
GEN-2018-029 | 04 - Southeast | 300839 | 2MERIDAN | 69 | 5136.6 | 5130.9 | -5.7
GEN-2018-029 | 04 - Southeast | 514979 | 44&SUNL2 | 69 | 11673.1 | 11688 | 14.9
GEN-2018-029 | 04 - Southeast | 300135 | 4LUTHER | 138 | 8338.9 | 8337.4 | -1.5
GEN-2018-029 | 04 - Southeast | 301372 | 4LUTHERD | 138 | 8328.4 | 8326.8 | -1.6
GEN-2018-029 | 04 - Southeast | 301541 | 4MEMORAL | 138 | 21263.1 | 21322.7 | 59.6
GEN-2018-029 | 04 - Southeast | 300136 | 4MEMORALT | 138 | 21481.6 | 21542.6 | 61
GEN-2018-029 | 04 - Southeast | 300915 | 4WARWICK | 138 | 4503.6 | 4498.5 | -5.1
GEN-2018-029 | 04 - Southeast | 515459 | ACORN 4 | 138 | 27112.1 | 27313.9 | 201.8
GEN-2018-029 | 04 - Southeast | 515457 | AIRDEPT4 | 138 | 20776.5 | 20820.4 | 43.9
GEN-2018-029 | 04 - Southeast | 514907 | ARCADIA4 | 138 | 46415.2 | 46590.2 | 175
GEN-2018-029 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 27716.6 | 27798.6 | 82
GEN-2018-029 | 04 - Southeast | 515003 | BARNES 4 | 138 | 16533.4 | 16559 | 25.6
GEN-2018-029 | 04 - Southeast | 515369 | BELLCOW4 | 138 | 6646.8 | 6642.1 | -4.7
GEN-2018-029 | 04 - Southeast | 514839 | BRYANT 4 | 138 | 30153.8 | 30436.4 | 282.6
GEN-2018-029 | 04 - Southeast | 514510 | BURGETT4 | 138 | 23496.2 | 23578.3 | 82.1
GEN-2018-029 | 04 - Southeast | 514948 | CEDARLN4 | 138 | 24150 | 24171.7 | 21.7
GEN-2018-029 | 04 - Southeast | 514842 | CHTWOOD4 | 138 | 21435.8 | 21532.6 | 96.8
GEN-2018-029 | 04 - Southeast | 514901 | CIMARON7 | 345 | 36994.7 | 37158.1 | 163.4
GEN-2018-029 | 04 - Southeast | 515377 | CRESENT4 | 138 | 10820.1 | 10871.5 | 51.4
GEN-2018-029 | 04 - Southeast | 515851 | CROSTWN4 | 138 | 25911.4 | 26107.4 | 196
GEN-2018-029 | 04 - Southeast | 514827 | CTNWOOD4 | 138 | 18657 | 18695.1 | 38.1
GEN-2018-029 | 04 - Southeast | 514987 | DALE 4 | 138 | 14061.3 | 14091 | 29.7
GEN-2018-029 | 04 - Southeast | 514833 | DANFRTH4 | 138 | 27176.2 | 27324 | 147.8
GEN-2018-029 | 04 - Southeast | 514970 | DEEPFKT2 | 69 | 7744.9 | 7752.5 | 7.6
GEN-2018-029 | 04 - Southeast | 514974 | DEEPFRK2 | 69 | 6519.1 | 6524.4 | 5.3
GEN-2018-029 | 04 - Southeast | 514933 | DRAPER 4 | 138 | 43020.3 | 43132.9 | 112.6
GEN-2018-029 | 04 - Southeast | 514934 | DRAPER 7 | 345 | 26206.4 | 26290.2 | 83.8
GEN-2018-029 | 04 - Southeast | 514884 | DUNJEE 4 | 138 | 21555.5 | 21680.9 | 125.4
GEN-2018-029 | 04 - Southeast | 514832 | EASTERN4 | 138 | 24883.3 | 25048.5 | 165.2
GEN-2018-029 | 04 - Southeast | 514830 | FITZGRD4 | 138 | 9194.7 | 9185.5 | -9.2
GEN-2018-029 | 04 - Southeast | 514959 | FOSTER 4 | 138 | 26426.3 | 26554.7 | 128.4
GEN-2018-029 | 04 - Southeast | 520917 | FRNKLNS4 | 138 | 30071.4 | 30109.4 | 38
GEN-2018-029 | 04 - Southeast | 515074 | FRSTHIL2 | 69 | 11179.5 | 11174.5 | -5
GEN-2018-029 | 04 - Southeast | 515075 | FRSTHIL4 | 138 | 14000 | 14006.6 | 6.6
GEN-2018-029 | 04 - Southeast | 515963 | GATEWAY4 | 138 | 21447.5 | 21591.2 | 143.7
GEN-2018-029 | 04 - Southeast | 587210 | GEN-2016-032 | 138 | 7982.5 | 8001.6 | 19.1
GEN-2018-029 | 04 - Southeast | 760032 | GEN-2017-132 | 345 | 6295.8 | 6298.8 | 3
GEN-2018-029 | 04 - Southeast | 762647 | GEN-2018-029 | 138 | 42309.7 | 42892.6 | 582.9
GEN-2018-029 | 04 - Southeast | 514986 | GLENDAL4 | 138 | 13711.4 | 13730.6 | 19.2
GEN-2018-029 | 04 - Southeast | 514961 | GM 4 | 138 | 20379.8 | 20419.8 | 40
GEN-2018-029 | 04 - Southeast | 520526 | GRDGVTP4 | 138 | 6931.3 | 6919.5 | -11.8
GEN-2018-029 | 04 - Southeast | 514971 | GRNPAST2 | 69 | 5844.7 | 5849.7 | 5
GEN-2018-029 | 04 - Southeast | 520951 | HAMMETT4 | 138 | 12616.6 | 12637.8 | 21.2
GEN-2018-029 | 04 - Southeast | 515046 | HAMMTAP4 | 138 | 16949.7 | 16994.1 | 44.4
GEN-2018-029 | 04 - Southeast | 514953 | HOLLYWD4 | 138 | 37414.9 | 37505.5 | 90.6
GEN-2018-029 | 04 - Southeast | 514941 | HSL 4 | 138 | 42323.2 | 42906.2 | 583
GEN-2018-029 | 04 - Southeast | 514927 | HSLEAST2 | 69 | 11428.1 | 11446.4 | 18.3
GEN-2018-029 | 04 - Southeast | 514937 | HSLWEST2 | 69 | 12070.7 | 12091.7 | 21
GEN-2018-029 | 04 - Southeast | 515060 | INGLEWD4 | 138 | 10285.5 | 10288.5 | 3
GEN-2018-029 | 04 - Southeast | 515051 | JACKTWN4 | 138 | 9728.4 | 9727.2 | -1.2
GEN-2018-029 | 04 - Southeast | 514906 | JNSKAMO4 | 138 | 21651.9 | 21714 | 62.1
GEN-2018-029 | 04 - Southeast | 515480 | JONESSB4 | 138 | 29582.4 | 29801.6 | 219.2
GEN-2018-029 | 04 - Southeast | 514501 | KELLYAV4 | 138 | 26555.2 | 26803.5 | 248.3
GEN-2018-029 | 04 - Southeast | 515373 | LBRTYLK4 | 138 | 14492.2 | 14516.7 | 24.5
GEN-2018-029 | 04 - Southeast | 515465 | LGARBER4 | 138 | 21885.8 | 21947.7 | 61.9
GEN-2018-029 | 04 - Southeast | 514923 | LIGHTCK4 | 138 | 25421.5 | 25601.6 | 180.1
GEN-2018-029 | 04 - Southeast | 515442 | LINCOLN4 | 138 | 15030.3 | 15039.7 | 9.4
GEN-2018-029 | 04 - Southeast | 515502 | LITLAXT2 | 69 | 3310.6 | 3308.8 | -1.8
GEN-2018-029 | 04 - Southeast | 514951 | LITTLAX2 | 69 | 3305.8 | 3304 | -1.8
GEN-2018-029 | 04 - Southeast | 514983 | LTLRLKT2 | 69 | 2770.6 | 2770.3 | -0.3
GEN-2018-029 | 04 - Southeast | 514956 | MACOCTP2 | 69 | 3260.3 | 3258.3 | -2
GEN-2018-029 | 04 - Southeast | 521006 | MARSHAL4 | 138 | 8237.2 | 8238.6 | 1.4
GEN-2018-029 | 04 - Southeast | 514733 | MARSHL 4 | 138 | 8237.2 | 8238.6 | 1.4
GEN-2018-029 | 04 - Southeast | 515497 | MATHWSN7 | 345 | 34955.7 | 35072.3 | 116.6
GEN-2018-029 | 04 - Southeast | 515055 | MAUD 4 | 138 | 20332.4 | 20329.3 | -3.1
GEN-2018-029 | 04 - Southeast | 515065 | MCLOUD 2 | 69 | 4866.1 | 4868.1 | 2
GEN-2018-029 | 04 - Southeast | 515504 | MCLOUDT2 | 69 | 4889.5 | 4891.4 | 1.9
GEN-2018-029 | 04 - Southeast | 520464 | MEEKER 4 | 138 | 8924.7 | 8915.6 | -9.1
GEN-2018-029 | 04 - Southeast | 520994 | MEEKRSW4 | 138 | 8189.4 | 8178.4 | -11
GEN-2018-029 | 04 - Southeast | 514835 | MEMRIAL4 | 138 | 37270.2 | 37758.6 | 488.4
GEN-2018-029 | 04 - Southeast | 514966 | MIDWAY 4 | 138 | 18551.6 | 18649.6 | 98
GEN-2018-029 | 04 - Southeast | 514946 | MIDWEST4 | 138 | 34939.1 | 35003.1 | 64
GEN-2018-029 | 04 - Southeast | 515057 | MOBIL 4 | 138 | 8467.2 | 8465.8 | -1.4
GEN-2018-029 | 04 - Southeast | 515224 | MUSKOGE7 | 345 | 27171 | 27664 | 493
GEN-2018-029 | 04 - Southeast | 514964 | NE10TH 4 | 138 | 18466.5 | 18554.3 | 87.8
GEN-2018-029 | 04 - Southeast | 514969 | NE30TH 2 | 69 | 9052.7 | 9062.8 | 10.1
GEN-2018-029 | 04 - Southeast | 515062 | NE45TAP4 | 138 | 8808.4 | 8808 | -0.4
GEN-2018-029 | 04 - Southeast | 515387 | NEWDOMI4 | 138 | 27126.5 | 27285.1 | 158.6
GEN-2018-029 | 04 - Southeast | 514879 | NORTWST4 | 138 | 46201.6 | 46520.6 | 319
GEN-2018-029 | 04 - Southeast | 514880 | NORTWST7 | 345 | 34437.5 | 34597.8 | 160.3
GEN-2018-029 | 04 - Southeast | 555234 | NSUB345 | 345 | 27439.2 | 27532.6 | 93.4
GEN-2018-029 | 04 - Southeast | 514930 | OAKTRET4 | 138 | 21787.3 | 21805.4 | 18.1
GEN-2018-029 | 04 - Southeast | 514875 | OUMED 4 | 138 | 22541.4 | 22711.7 | 170.3
GEN-2018-029 | 04 - Southeast | 514829 | PINE ST4 | 138 | 12526.5 | 12531.3 | 4.8
GEN-2018-029 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 14161.2 | 14118.5 | -42.7
GEN-2018-029 | 04 - Southeast | 509782 | R.S.S.-7 | 345 | 31623.7 | 31821.2 | 197.5
GEN-2018-029 | 04 - Southeast | 514909 | REDBUD 7 | 345 | 26648.4 | 26715.4 | 67
GEN-2018-029 | 04 - Southeast | 514972 | RENO 2 | 69 | 14190.4 | 14214.1 | 23.7
GEN-2018-029 | 04 - Southeast | 514973 | RENO 4 | 138 | 28491.8 | 28701 | 209.2
GEN-2018-029 | 04 - Southeast | 515461 | RNDBARN4 | 138 | 43869.8 | 44029.5 | 159.7
GEN-2018-029 | 04 - Southeast | 521107 | RSSVILE4 | 138 | 12329.9 | 12330.1 | 0.2
GEN-2018-029 | 04 - Southeast | 514993 | SE15TH 4 | 138 | 15681.3 | 15708.5 | 27.2
GEN-2018-029 | 04 - Southeast | 515044 | SEMINOL4 | 138 | 40748.6 | 40800.9 | 52.3
GEN-2018-029 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 28591.5 | 28664.8 | 73.3
GEN-2018-029 | 04 - Southeast | 515068 | SHAWNEE2 | 69 | 7952.8 | 7945.4 | -7.4
GEN-2018-029 | 04 - Southeast | 515072 | SINCPAN2 | 69 | 5767.1 | 5762.8 | -4.3
GEN-2018-029 | 04 - Southeast | 515642 | SINCPNT2 | 69 | 5800.2 | 5796 | -4.2
GEN-2018-029 | 04 - Southeast | 514850 | SKYLINE4 | 138 | 33460.9 | 33800.7 | 339.8
GEN-2018-029 | 04 - Southeast | 514949 | SOONRTP4 | 138 | 23210.4 | 23231.4 | 21
GEN-2018-029 | 04 - Southeast | 514881 | SPRNGCK7 | 345 | 24231.9 | 24289.2 | 57.3
GEN-2018-029 | 04 - Southeast | 515059 | SQUIRCK4 | 138 | 14098.4 | 14111.4 | 13
GEN-2018-029 | 04 - Southeast | 520449 | STERLNG4 | 138 | 11312.6 | 11317.6 | 5
GEN-2018-029 | 04 - Southeast | 515061 | STGREG 4 | 138 | 9109.5 | 9110 | 0.5
GEN-2018-029 | 04 - Southeast | 515286 | STRLGTP4 | 138 | 13940.4 | 13951 | 10.6
GEN-2018-029 | 04 - Southeast | 514980 | SUNNYLN2 | 69 | 11985.1 | 12001.1 | 16
GEN-2018-029 | 04 - Southeast | 514837 | TENESTP4 | 138 | 31728.4 | 32191.4 | 463
GEN-2018-029 | 04 - Southeast | 514981 | TINKER32 | 69 | 9037.6 | 9046.7 | 9.1
GEN-2018-029 | 04 - Southeast | 514994 | TINKER54 | 138 | 14322.7 | 14341.8 | 19.1
GEN-2018-029 | 04 - Southeast | 515806 | TINKER64 | 138 | 13870.6 | 13888.6 | 18
GEN-2018-029 | 04 - Southeast | 515959 | TINKER74 | 138 | 13440.1 | 13457.8 | 17.7
GEN-2018-029 | 04 - Southeast | 514963 | TROSPER4 | 138 | 28863.9 | 29060.5 | 196.6
GEN-2018-029 | 04 - Southeast | 515675 | TRYON 4 | 138 | 9020.7 | 9015.8 | -4.9
GEN-2018-029 | 04 - Southeast | 521073 | TWNLKSW4 | 138 | 10077.3 | 10142.9 | 65.6
GEN-2018-029 | 04 - Southeast | 514989 | TXPLSTE2 | 69 | 2999.9 | 2999.6 | -0.3
GEN-2018-029 | 04 - Southeast | 515516 | TXPLSTP2 | 69 | 3003.7 | 3003.4 | -0.3
GEN-2018-029 | 04 - Southeast | 514985 | TXSTELA2 | 69 | 3910.6 | 3910.5 | -0.1
GEN-2018-029 | 04 - Southeast | 515047 | WARWICK4 | 138 | 10333 | 10328.5 | -4.5
GEN-2018-029 | 04 - Southeast | 515156 | WASHPRK4 | 138 | 21675.6 | 21812.2 | 136.6
GEN-2018-029 | 04 - Southeast | 514831 | WATRLOO4 | 138 | 14907.1 | 14936.3 | 29.2
GEN-2018-029 | 04 - Southeast | 515366 | WFROSST4 | 138 | 12329.9 | 12330.1 | 0.2
GEN-2018-029 | 04 - Southeast | 515056 | WOLVERN4 | 138 | 8394.4 | 8392.9 | -1.5
GEN-2018-029 | 04 - Southeast | 515532 | WOLVRNT4 | 138 | 8465 | 8463.6 | -1.4
GEN-2018-029 | 04 - Southeast | 514714 | WOODRNG4 | 138 | 21390 | 21433.6 | 43.6
GEN-2018-029 | 04 - Southeast | 521097 | WREDHIL4 | 138 | 7118.5 | 7108 | -10.5
GEN-2018-048 | 04 - Southeast | 509753 | 116JENK4 | 138 | 42776.5 | 42944.1 | 167.6
GEN-2018-048 | 04 - Southeast | 509869 | 121LYNN4 | 138 | 17761.5 | 17781.3 | 19.8
GEN-2018-048 | 04 - Southeast | 509775 | 136YALE4 | 138 | 23569.4 | 23612.1 | 42.7
GEN-2018-048 | 04 - Southeast | 515308 | 3RDST 5 | 161 | 15744.2 | 15657.3 | -86.9
GEN-2018-048 | 04 - Southeast | 509814 | 52DELWT4 | 138 | 22872.5 | 22948.8 | 76.3
GEN-2018-048 | 04 - Southeast | 337912 | 5ANO% | 161 | 17603.9 | 17608.7 | 4.8
GEN-2018-048 | 04 - Southeast | 515227 | 5TRIBES2 | 69 | 12899.5 | 12896.9 | -2.6
GEN-2018-048 | 04 - Southeast | 515228 | 5TRIBES5 | 161 | 15692.5 | 15749.8 | 57.3
GEN-2018-048 | 04 - Southeast | 509888 | 72ELWOD4 | 138 | 23453.8 | 23576.1 | 122.3
GEN-2018-048 | 04 - Southeast | 337909 | 8ANO% | 500 | 18109.2 | 18113 | 3.8
GEN-2018-048 | 04 - Southeast | 337811 | 8HAPPYVALY% | 500 | 25549.8 | 25536.6 | -13.2
GEN-2018-048 | 04 - Southeast | 337922 | 8P.HILL% | 500 | 15676 | 15663 | -13
GEN-2018-048 | 04 - Southeast | 515229 | AGENCY 2 | 69 | 13209.6 | 13204.5 | -5.1
GEN-2018-048 | 04 - Southeast | 515230 | AGENCY 5 | 161 | 14256.4 | 14291.1 | 34.7
GEN-2018-048 | 04 - Southeast | 515117 | ARBUCKL4 | 138 | 16109.4 | 16069.1 | -40.3
GEN-2018-048 | 04 - Southeast | 514907 | ARCADIA4 | 138 | 46415.2 | 46590.2 | 175
GEN-2018-048 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 27716.6 | 27798.6 | 82
GEN-2018-048 | 04 - Southeast | 515306 | ARKOMA 5 | 161 | 16374.7 | 16281.3 | -93.4
GEN-2018-048 | 04 - Southeast | 509767 | B111---4 | 138 | 15994.7 | 16010.5 | 15.8
GEN-2018-048 | 04 - Southeast | 509721 | BA.NO-S4 | 138 | 12273.1 | 12272.6 | -0.5
GEN-2018-048 | 04 - Southeast | 509786 | BA.N-ST4 | 138 | 23890.4 | 23902.4 | 12
GEN-2018-048 | 04 - Southeast | 509891 | BA_71ST4 | 138 | 23300.6 | 23332.7 | 32.1
GEN-2018-048 | 04 - Southeast | 509737 | BA101 S4 | 138 | 18128.3 | 18146.4 | 18.1
GEN-2018-048 | 04 - Southeast | 509769 | BA101-N4 | 138 | 19699.3 | 19722.5 | 23.2
GEN-2018-048 | 04 - Southeast | 509768 | BA101ST4 | 138 | 18808.2 | 18827.9 | 19.7
GEN-2018-048 | 04 - Southeast | 509747 | BA81---4 | 138 | 18155.5 | 18176.2 | 20.7
GEN-2018-048 | 04 - Southeast | 509785 | BANNTAP4 | 138 | 18718.9 | 18744.9 | 26
GEN-2018-048 | 04 - Southeast | 515003 | BARNES 4 | 138 | 16533.4 | 16559 | 25.6
GEN-2018-048 | 04 - Southeast | 515247 | BEELINE4 | 138 | 22196.6 | 22233.3 | 36.7
GEN-2018-048 | 04 - Southeast | 515249 | BEGGS 4 | 138 | 5727.9 | 5724.9 | -3
GEN-2018-048 | 04 - Southeast | 515299 | BEVYTAP5 | 161 | 20792.5 | 20677.6 | -114.9
GEN-2018-048 | 04 - Southeast | 515239 | BIXBY 2 | 69 | 5859.7 | 5855.4 | -4.3
GEN-2018-048 | 04 - Southeast | 511508 | BLANCHD4 | 138 | 6630.7 | 6629.4 | -1.3
GEN-2018-048 | 04 - Southeast | 515242 | BLUEBEL4 | 138 | 17307.5 | 17322.6 | 15.1
GEN-2018-048 | 04 - Southeast | 515034 | BRISTOW2 | 69 | 5879 | 5875.6 | -3.4
GEN-2018-048 | 04 - Southeast | 515035 | BRISTOW4 | 138 | 10878.6 | 10876.4 | -2.2
GEN-2018-048 | 04 - Southeast | 506944 | CHAMSPR5 | 161 | 23530.6 | 23514.4 | -16.2
GEN-2018-048 | 04 - Southeast | 506945 | CHAMSPR7 | 345 | 10217.7 | 10195.8 | -21.9
GEN-2018-048 | 04 - Southeast | 515201 | CHECOTA2 | 69 | 3322.5 | 3314.2 | -8.3
GEN-2018-048 | 04 - Southeast | 515114 | CHIGLEY4 | 138 | 8279.9 | 8258.7 | -21.2
GEN-2018-048 | 04 - Southeast | 514901 | CIMARON7 | 345 | 36994.7 | 37158.1 | 163.4
GEN-2018-048 | 04 - Southeast | 509745 | CLARKSV7 | 345 | 20231.1 | 20321 | 89.9
GEN-2018-048 | 04 - Southeast | 512694 | CLEVLND7 | 345 | 15119.9 | 15104.6 | -15.3
GEN-2018-048 | 04 - Southeast | 509834 | COGENT 7 | 345 | 29350.1 | 29519.5 | 169.4
GEN-2018-048 | 04 - Southeast | 515345 | COLONY 5 | 161 | 18653.6 | 18543.5 | -110.1
GEN-2018-048 | 04 - Southeast | 510946 | C-RIVER4 | 138 | 13144 | 13112 | -32
GEN-2018-048 | 04 - Southeast | 515422 | C-RIVER7 | 345 | 10106.6 | 10121.1 | 14.5
GEN-2018-048 | 04 - Southeast | 514827 | CTNWOOD4 | 138 | 18657 | 18695.1 | 38.1
GEN-2018-048 | 04 - Southeast | 510379 | DELWARE4 | 138 | 11042.3 | 11016.6 | -25.7
GEN-2018-048 | 04 - Southeast | 510380 | DELWARE7 | 345 | 11721.1 | 11695.9 | -25.2
GEN-2018-048 | 04 - Southeast | 509896 | DENV_WTAP4 | 138 | 28036.2 | 28112.8 | 76.6
GEN-2018-048 | 04 - Southeast | 509748 | DENVR-W4 | 138 | 9607.8 | 9613.1 | 5.3
GEN-2018-048 | 04 - Southeast | 516006 | DMNDSPG7 | 345 | 8018.8 | 7995.2 | -23.6
GEN-2018-048 | 04 - Southeast | 514933 | DRAPER 4 | 138 | 43020.3 | 43132.9 | 112.6
GEN-2018-048 | 04 - Southeast | 514934 | DRAPER 7 | 345 | 26206.4 | 26290.2 | 83.8
GEN-2018-048 | 04 - Southeast | 509889 | E_121ST4 | 138 | 15864.6 | 15882.5 | 17.9
GEN-2018-048 | 04 - Southeast | 510948 | EARLSBORO 4 | 138 | 8422.8 | 8406.5 | -16.3
GEN-2018-048 | 04 - Southeast | 510923 | EC.HEN-4 | 138 | 8587 | 8573.1 | -13.9
GEN-2018-048 | 04 - Southeast | 515251 | EUCLID 5 | 161 | 13937.6 | 13959.6 | 22
GEN-2018-048 | 04 - Southeast | 510904 | EXP_OKM4 | 138 | 9882.5 | 9876.8 | -5.7
GEN-2018-048 | 04 - Southeast | 515473 | EXPGLNT4 | 138 | 24478 | 24524.6 | 46.6
GEN-2018-048 | 04 - Southeast | 515248 | EXPLGLN4 | 138 | 24041.7 | 24086.6 | 44.9
GEN-2018-048 | 04 - Southeast | 588839 | FIREWHL-TAP | 345 | 11256.3 | 11439.7 | 183.4
GEN-2018-048 | 04 - Southeast | 515075 | FRSTHIL4 | 138 | 14000 | 14006.6 | 6.6
GEN-2018-048 | 04 - Southeast | 515302 | FTSMITH7 | 345 | 10221.9 | 10123.2 | -98.7
GEN-2018-048 | 04 - Southeast | 515305 | FTSMITH8 | 500 | 8594 | 8544.8 | -49.2
GEN-2018-048 | 04 - Southeast | 515300 | FTSMTHE5 | 161 | 23536 | 23399.7 | -136.3
GEN-2018-048 | 04 - Southeast | 515301 | FTSMTHW5 | 161 | 23406.7 | 23269.8 | -136.9
GEN-2018-048 | 04 - Southeast | 560056 | G15-066T | 345 | 19544.5 | 19524.8 | -19.7
GEN-2018-048 | 04 - Southeast | 587804 | G16-119-TAP | 345 | 16400.5 | 16395.5 | -5
GEN-2018-048 | 04 - Southeast | 588040 | G16133_345GS | 345 | 17419.9 | 17471.9 | 52
GEN-2018-048 | 04 - Southeast | 588041 | G16133_765GS | 765 | 6192.6 | 6205.3 | 12.7
GEN-2018-048 | 04 - Southeast | 588043 | G16133_765MP | 765 | 3864.8 | 3867.9 | 3.1
GEN-2018-048 | 04 - Southeast | 588039 | G16133G16146 | 345 | 31623.7 | 31821.2 | 197.5
GEN-2018-048 | 04 - Southeast | 588838 | G17-092-SWYD | 345 | 11256.3 | 11439.7 | 183.4
GEN-2018-048 | 04 - Southeast | 760393 | G17-140-BUS | 345 | 1710.5 | 1710.4 | -0.1
GEN-2018-048 | 04 - Southeast | 762629 | G18-027-TAP | 138 | 38238.4 | 38755.2 | 516.8
GEN-2018-048 | 04 - Southeast | 560389 | GEN-2010-055 | 138 | 32596.1 | 32624.9 | 28.8
GEN-2018-048 | 04 - Southeast | 588810 | GEN-2017-040 | 345 | 11104.5 | 11282.4 | 177.9
GEN-2018-048 | 04 - Southeast | 589140 | GEN-2017-076 | 161 | 20925.8 | 20910.4 | -15.4
GEN-2018-048 | 04 - Southeast | 589300 | GEN-2017-092 | 345 | 9903.1 | 10040.7 | 137.6
GEN-2018-048 | 04 - Southeast | 760032 | GEN-2017-132 | 345 | 6295.8 | 6298.8 | 3
GEN-2018-048 | 04 - Southeast | 760389 | GEN-2017-140 | 345 | 1721.8 | 1721.7 | -0.1
GEN-2018-048 | 04 - Southeast | 760830 | GEN-2017-149 | 345 | 4100.4 | 4091.9 | -8.5
GEN-2018-048 | 04 - Southeast | 761334 | GEN-2017-155 | 345 | 12056.6 | 12148.8 | 92.2
GEN-2018-048 | 04 - Southeast | 760368 | GEN-2017-213 | 345 | 16334.7 | 16389.4 | 54.7
GEN-2018-048 | 04 - Southeast | 760158 | GEN-2017-240 | 138 | 4274.5 | 4273.4 | -1.1
GEN-2018-048 | 04 - Southeast | 762592 | GEN-2018-024 | 345 | 11044.2 | 11229 | 184.8
GEN-2018-048 | 04 - Southeast | 762823 | GEN-2018-048 | 345 | 15762.5 | 16386.3 | 623.8
GEN-2018-048 | 04 - Southeast | 514961 | GM 4 | 138 | 20379.8 | 20419.8 | 40
GEN-2018-048 | 04 - Southeast | 515417 | GRNWOOD4 | 138 | 8721 | 8718.5 | -2.5
GEN-2018-048 | 04 - Southeast | 515250 | HANCOK-5 | 161 | 14349.5 | 14381.9 | 32.4
GEN-2018-048 | 04 - Southeast | 515216 | HONORHT2 | 69 | 12909.2 | 12903.9 | -5.3
GEN-2018-048 | 04 - Southeast | 521157 | HUGO 7 | 345 | 11298.9 | 11219 | -79.9
GEN-2018-048 | 04 - Southeast | 513596 | IGLOOV 7 | 345 | 20039.7 | 20039.9 | 0.2
GEN-2018-048 | 04 - Southeast | 515240 | JAMESVL2 | 69 | 4413.9 | 4411.1 | -2.8
GEN-2018-048 | 04 - Southeast | 509759 | JENKS--4 | 138 | 25452.5 | 25521.5 | 69
GEN-2018-048 | 04 - Southeast | 514906 | JNSKAMO4 | 138 | 21651.9 | 21714 | 62.1
GEN-2018-048 | 04 - Southeast | 514808 | JOHNCO 4 | 138 | 15979.5 | 15916.1 | -63.4
GEN-2018-048 | 04 - Southeast | 514809 | JOHNCO 7 | 345 | 11293.7 | 11272.2 | -21.5
GEN-2018-048 | 04 - Southeast | 510931 | KELCO 4 | 138 | 10150.6 | 10141.2 | -9.4
GEN-2018-048 | 04 - Southeast | 505610 | KEYSTON4 | 138 | 22636.7 | 22640.8 | 4.1
GEN-2018-048 | 04 - Southeast | 515048 | KEYWEST4 | 138 | 5995.6 | 5991.6 | -4
GEN-2018-048 | 04 - Southeast | 509845 | KIMCLRK4 | 138 | 22361.5 | 22399.3 | 37.8
GEN-2018-048 | 04 - Southeast | 510925 | KIOWA 7 | 345 | 13907.6 | 13864.7 | -42.9
GEN-2018-048 | 04 - Southeast | 515465 | LGARBER4 | 138 | 21885.8 | 21947.7 | 61.9
GEN-2018-048 | 04 - Southeast | 515977 | LKKONWA4 | 138 | 39834.9 | 39884.3 | 49.4
GEN-2018-048 | 04 - Southeast | 509804 | LLANETP4 | 138 | 27181.2 | 27179.2 | -2
GEN-2018-048 | 04 - Southeast | 508298 | LYDIA 7 | 345 | 12551.3 | 12518.5 | -32.8
GEN-2018-048 | 04 - Southeast | 515497 | MATHWSN7 | 345 | 34955.7 | 35072.3 | 116.6
GEN-2018-048 | 04 - Southeast | 515054 | MAUD 2 | 69 | 10674.1 | 10661.1 | -13
GEN-2018-048 | 04 - Southeast | 515055 | MAUD 4 | 138 | 20332.4 | 20329.3 | -3.1
GEN-2018-048 | 04 - Southeast | 515124 | MAYSVIL4 | 138 | 6345.2 | 6328.9 | -16.3
GEN-2018-048 | 04 - Southeast | 514946 | MIDWEST4 | 138 | 34939.1 | 35003.1 | 64
GEN-2018-048 | 04 - Southeast | 514801 | MINCO 7 | 345 | 23878.2 | 23943 | 64.8
GEN-2018-048 | 04 - Southeast | 515184 | MSKPORT5 | 161 | 12856.4 | 12864 | 7.6
GEN-2018-048 | 04 - Southeast | 515232 | MSKPTAP5 | 161 | 15621.2 | 15640.6 | 19.4
GEN-2018-048 | 04 - Southeast | 515222 | MUSKOGE5 | 161 | 16315.6 | 16336.2 | 20.6
GEN-2018-048 | 04 - Southeast | 515224 | MUSKOGE7 | 345 | 27171 | 27664 | 493
GEN-2018-048 | 04 - Southeast | 510406 | N.E.S.-7 | 345 | 19054.5 | 19071.3 | 16.8
GEN-2018-048 | 04 - Southeast | 532793 | NEOSHO 7 | 345 | 17450.3 | 17395.3 | -55
GEN-2018-048 | 04 - Southeast | 514879 | NORTWST4 | 138 | 46201.6 | 46520.6 | 319
GEN-2018-048 | 04 - Southeast | 514880 | NORTWST7 | 345 | 34437.5 | 34597.8 | 160.3
GEN-2018-048 | 04 - Southeast | 555234 | NSUB345 | 345 | 27439.2 | 27532.6 | 93.4
GEN-2018-048 | 04 - Southeast | 508072 | NWTXARK7 | 345 | 13088.2 | 13159.5 | 71.3
GEN-2018-048 | 04 - Southeast | 509727 | OAKS W4 | 138 | 15639.3 | 15695.6 | 56.3
GEN-2018-048 | 04 - Southeast | 509846 | OAKS--E4 | 138 | 13941.5 | 14001.7 | 60.2
GEN-2018-048 | 04 - Southeast | 509850 | OAKSETP4 | 138 | 29489.8 | 29753.8 | 264
GEN-2018-048 | 04 - Southeast | 509848 | OAKSWTP4 | 138 | 25026.4 | 25171.3 | 144.9
GEN-2018-048 | 04 - Southeast | 509836 | OEC 7 | 345 | 28822.6 | 28933.7 | 111.1
GEN-2018-048 | 04 - Southeast | 510898 | OKMULGE4 | 138 | 11373.8 | 11365.5 | -8.3
GEN-2018-048 | 04 - Southeast | 509806 | ONETA--4 | 138 | 49079.3 | 49212.5 | 133.2
GEN-2018-048 | 04 - Southeast | 509807 | ONETA--7 | 345 | 29108.6 | 29222.2 | 113.6
GEN-2018-048 | 04 - Southeast | 509738 | ORU E4 | 138 | 24719 | 24773 | 54
GEN-2018-048 | 04 - Southeast | 509732 | ORU W4 | 138 | 23396.8 | 23445.7 | 48.9
GEN-2018-048 | 04 - Southeast | 509849 | ORU ETP4 | 138 | 34179.7 | 34283.1 | 103.4
GEN-2018-048 | 04 - Southeast | 509853 | ORU-WTP4 | 138 | 29947.4 | 30027.9 | 80.5
GEN-2018-048 | 04 - Southeast | 509851 | P&P WTP4 | 138 | 15290.1 | 15287.2 | -2.9
GEN-2018-048 | 04 - Southeast | 515099 | PALIOGE2 | 69 | 8734.2 | 8714.9 | -19.3
GEN-2018-048 | 04 - Southeast | 515100 | PAOLI- 4 | 138 | 10568 | 10551 | -17
GEN-2018-048 | 04 - Southeast | 515178 | PARKLN 4 | 138 | 16500.6 | 16477.6 | -23
GEN-2018-048 | 04 - Southeast | 515233 | PECANCK4 | 138 | 9818.7 | 9832.4 | 13.7
GEN-2018-048 | 04 - Southeast | 515234 | PECANCK5 | 161 | 21229.9 | 21391 | 161.1
GEN-2018-048 | 04 - Southeast | 515235 | PECANCK7 | 345 | 21209 | 21844.1 | 635.1
GEN-2018-048 | 04 - Southeast | 516010 | PINTAIL7 | 345 | 17551.1 | 17560.3 | 9.2
GEN-2018-048 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 14161.2 | 14118.5 | -42.7
GEN-2018-048 | 04 - Southeast | 514929 | PLVALLY4 | 138 | 46680 | 46818 | 138
GEN-2018-048 | 04 - Southeast | 515310 | QUANXTP5 | 161 | 17936 | 17832.7 | -103.3
GEN-2018-048 | 04 - Southeast | 509783 | R.S.S.-4 | 138 | 61175.5 | 61503.5 | 328
GEN-2018-048 | 04 - Southeast | 509782 | R.S.S.-7 | 345 | 31623.7 | 31821.2 | 197.5
GEN-2018-048 | 04 - Southeast | 515576 | RANCHRD7 | 345 | 14704.7 | 14664.9 | -39.8
GEN-2018-048 | 04 - Southeast | 514909 | REDBUD 7 | 345 | 26648.4 | 26715.4 | 67
GEN-2018-048 | 04 - Southeast | 515461 | RNDBARN4 | 138 | 43869.8 | 44029.5 | 159.7
GEN-2018-048 | 04 - Southeast | 509773 | RSS T1 4 | 138 | 50830.1 | 51049 | 218.9
GEN-2018-048 | 04 - Southeast | 509875 | RSS T2 4 | 138 | 51729.1 | 51956.4 | 227.3
GEN-2018-048 | 04 - Southeast | 509859 | S HILLW4 | 138 | 16792.1 | 16833.8 | 41.7
GEN-2018-048 | 04 - Southeast | 509815 | S.S.---4 | 138 | 28757.6 | 28838 | 80.4
GEN-2018-048 | 04 - Southeast | 509871 | SAPLPRD4 | 138 | 33107 | 33259 | 152
GEN-2018-048 | 04 - Southeast | 509870 | SAPLPRD7 | 345 | 22644.3 | 22719.1 | 74.8
GEN-2018-048 | 04 - Southeast | 515044 | SEMINOL4 | 138 | 40748.6 | 40800.9 | 52.3
GEN-2018-048 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 28591.5 | 28664.8 | 73.3
GEN-2018-048 | 04 - Southeast | 509812 | SHEFFD-4 | 138 | 25993.9 | 26052 | 58.1
GEN-2018-048 | 04 - Southeast | 509813 | SHILETP4 | 138 | 27970.3 | 28041 | 70.7
GEN-2018-048 | 04 - Southeast | 506948 | SILOAM 5 | 161 | 21990.2 | 21980.6 | -9.6
GEN-2018-048 | 04 - Southeast | 504202 | SILOAMSP 5 | 161 | 19637 | 19632.1 | -4.9
GEN-2018-048 | 04 - Southeast | 512726 | SILVCTYGR4 | 138 | 15688 | 15673.9 | -14.1
GEN-2018-048 | 04 - Southeast | 514802 | SOONER 4 | 138 | 32499.7 | 32507.6 | 7.9
GEN-2018-048 | 04 - Southeast | 514803 | SOONER 7 | 345 | 29241.4 | 29219.7 | -21.7
GEN-2018-048 | 04 - Southeast | 514949 | SOONRTP4 | 138 | 23210.4 | 23231.4 | 21
GEN-2018-048 | 04 - Southeast | 514881 | SPRNGCK7 | 345 | 24231.9 | 24289.2 | 57.3
GEN-2018-048 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12217.7 | 12233.9 | 16.2
GEN-2018-048 | 04 - Southeast | 509895 | T.NO.2-4 | 138 | 34856.9 | 34852.3 | -4.6
GEN-2018-048 | 04 - Southeast | 509852 | T.NO.--7 | 345 | 24027.3 | 24032.9 | 5.6
GEN-2018-048 | 04 - Southeast | 509788 | T.P.S.-4 | 138 | 39555.8 | 40019.8 | 464
GEN-2018-048 | 04 - Southeast | 510951 | TALAWANDA 4 | 138 | 9697.7 | 9662.6 | -35.1
GEN-2018-048 | 04 - Southeast | 515217 | TENYSON2 | 69 | 12045 | 12040.3 | -4.7
GEN-2018-048 | 04 - Southeast | 515640 | THRERVR5 | 161 | 14848.6 | 14868.7 | 20.1
GEN-2018-048 | 04 - Southeast | 515894 | THUNDER7 | 345 | 11830 | 11817.7 | -12.3
GEN-2018-048 | 04 - Southeast | 506957 | TONTITN5 | 161 | 23015.4 | 23014.2 | -1.2
GEN-2018-048 | 04 - Southeast | 506959 | TONTITN7 | 345 | 9204.3 | 9186.7 | -17.6
GEN-2018-048 | 04 - Southeast | 510918 | VALIANT4 | 138 | 14830.6 | 14735.6 | -95
GEN-2018-048 | 04 - Southeast | 510911 | VALIANT7 | 345 | 13306.9 | 13221.3 | -85.6
GEN-2018-048 | 04 - Southeast | 515174 | VANOSS 4 | 138 | 13394.2 | 13374.9 | -19.3
GEN-2018-048 | 04 - Southeast | 515531 | VANOSTP4 | 138 | 13523 | 13503.7 | -19.3
GEN-2018-048 | 04 - Southeast | 509858 | WARNTAP4 | 138 | 28822.3 | 28896.3 | 74
GEN-2018-048 | 04 - Southeast | 506992 | WEDINGTON | 161 | 16384 | 16370.4 | -13.6
GEN-2018-048 | 04 - Southeast | 509823 | WED-TAP4 | 138 | 19241.5 | 19262.1 | 20.6
GEN-2018-048 | 04 - Southeast | 509757 | WEKIWA-4 | 138 | 32596.1 | 32624.9 | 28.8
GEN-2018-048 | 04 - Southeast | 509755 | WEKIWA-7 | 345 | 22309.7 | 22339.1 | 29.4
GEN-2018-048 | 04 - Southeast | 515202 | WELLS 2 | 69 | 3171.2 | 3163.3 | -7.9
GEN-2018-048 | 04 - Southeast | 515097 | WLNUTCK4 | 138 | 9610.2 | 9600.9 | -9.3
GEN-2018-050 | 04 - Southeast | 337360 | 3ADA_LA | 115 | 5477 | 5478.4 | 1.4
GEN-2018-050 | 04 - Southeast | 337367 | 3ARCADIA | 115 | 5340.2 | 5337.4 | -2.8
GEN-2018-050 | 04 - Southeast | 337364 | 3CULLEN | 115 | 8436 | 8443 | 7
GEN-2018-050 | 04 - Southeast | 337539 | 3EL DORADO! | 115 | 28733.5 | 28726.8 | -6.7
GEN-2018-050 | 04 - Southeast | 337540 | 3ELD DONAN | 115 | 14829 | 14823.4 | -5.6
GEN-2018-050 | 04 - Southeast | 337560 | 3ELD QUINN | 115 | 27972.2 | 27965.7 | -6.5
GEN-2018-050 | 04 - Southeast | 337553 | 3ELDORADO.E! | 115 | 13464.7 | 13458.2 | -6.5
GEN-2018-050 | 04 - Southeast | 337526 | 3EMERSON! | 115 | 5878.8 | 5877.3 | -1.5
GEN-2018-050 | 04 - Southeast | 337366 | 3HAYNESVILLE | 115 | 5909 | 5910.3 | 1.3
GEN-2018-050 | 04 - Southeast | 337524 | 3KERLIN+ | 115 | 7209.8 | 7203.7 | -6.1
GEN-2018-050 | 04 - Southeast | 337362 | 3LA_ORD_PLNT | 115 | 4384.1 | 4384.9 | 0.8
GEN-2018-050 | 04 - Southeast | 337514 | 3MACEDONA | 115 | 6386 | 6383.2 | -2.8
GEN-2018-050 | 04 - Southeast | 337516 | 3MCNEIL! | 115 | 24774.5 | 24730.2 | -44.3
GEN-2018-050 | 04 - Southeast | 337361 | 3MINDEN_LA! | 115 | 6746.7 | 6747.9 | 1.2
GEN-2018-050 | 04 - Southeast | 303302 | 3MINDEN_LG | 115 | 5525.3 | 5524.9 | -0.4
GEN-2018-050 | 04 - Southeast | 337351 | 3SAILES! | 115 | 5996.4 | 5998.7 | 2.3
GEN-2018-050 | 04 - Southeast | 337363 | 3SAREPTA! | 115 | 19817.5 | 19835.4 | 17.9
GEN-2018-050 | 04 - Southeast | 337537 | 3SMACKOVER+ | 115 | 9271.8 | 9266.8 | -5
GEN-2018-050 | 04 - Southeast | 337365 | 3SPRINGHILL | 115 | 9713.2 | 9718.3 | 5.1
GEN-2018-050 | 04 - Southeast | 337415 | 3STERLING% | 115 | 35815.4 | 35813.5 | -1.9
GEN-2018-050 | 04 - Southeast | 337500 | 3TAYLOR | 115 | 7084.9 | 7085.5 | 0.6
GEN-2018-050 | 04 - Southeast | 500465 | 6LAYFLD | 230 | 15673.8 | 15632.4 | -41.4
GEN-2018-050 | 04 - Southeast | 337369 | 6MT_OLIVE% | 230 | 13701.6 | 13694.8 | -6.8
GEN-2018-050 | 04 - Southeast | 337562 | 7EL DORADO | 345 | 14086.3 | 14089.1 | 2.8
GEN-2018-050 | 04 - Southeast | 337376 | 7SAREPTA% | 345 | 9853.4 | 9859.3 | 5.9
GEN-2018-050 | 04 - Southeast | 337561 | 8EL DORADO% | 500 | 27617.3 | 27618.9 | 1.6
GEN-2018-050 | 04 - Southeast | 337754 | 8ETTA% | 500 | 18940.6 | 18941.7 | 1.1
GEN-2018-050 | 04 - Southeast | 337808 | 8MABELVALE% | 500 | 27500.4 | 27492.1 | -8.3
GEN-2018-050 | 04 - Southeast | 337763 | 8MAGNETCOVE% | 500 | 22444.9 | 22446.6 | 1.7
GEN-2018-050 | 04 - Southeast | 337515 | 8MCNEIL% | 500 | 14426.5 | 14425 | -1.5
GEN-2018-050 | 04 - Southeast | 337368 | 8MT_OLIVE% | 500 | 11823.7 | 11821.3 | -2.4
GEN-2018-050 | 04 - Southeast | 338440 | 8PANDA% | 500 | 27554.3 | 27556 | 1.7
GEN-2018-050 | 04 - Southeast | 337427 | 8PERRYVILLE% | 500 | 19660.9 | 19661.3 | 0.4
GEN-2018-050 | 04 - Southeast | 337643 | 8SHERIDAN% | 500 | 27851.8 | 27852 | 0.2
GEN-2018-050 | 04 - Southeast | 337420 | 8STERLING% | 500 | 19968.1 | 19968.4 | 0.3
GEN-2018-050 | 04 - Southeast | 337413 | 8STERLING2% | 500 | 19968.1 | 19968.4 | 0.3
GEN-2018-050 | 04 - Southeast | 337651 | 8WHT BLUFF% | 500 | 27657.1 | 27659.1 | 2
GEN-2018-050 | 04 - Southeast | 508050 | ANDRSNC4 | 138 | 7264.9 | 7514.8 | 249.9
GEN-2018-050 | 04 - Southeast | 507710 | ARSHILL2 | 69 | 28027.3 | 28019.8 | -7.5
GEN-2018-050 | 04 - Southeast | 507711 | ARSHILL4 | 138 | 24939.2 | 24944.2 | 5
GEN-2018-050 | 04 - Southeast | 508052 | ATLANTA2 | 69 | 5503.1 | 5494.6 | -8.5
GEN-2018-050 | 04 - Southeast | 509603 | BIGSAND4 | 138 | 7182.2 | 7178.7 | -3.5
GEN-2018-050 | 04 - Southeast | 508801 | BLANCH-2 | 69 | 6799.1 | 6788.4 | -10.7
GEN-2018-050 | 04 - Southeast | 508802 | BLANCHR2 | 69 | 7653.2 | 7644.6 | -8.6
GEN-2018-050 | 04 - Southeast | 507717 | BROOKS 2 | 69 | 20410.3 | 20402.1 | -8.2
GEN-2018-050 | 04 - Southeast | 508056 | BRYANML4 | 138 | 6946.8 | 7074.3 | 127.5
GEN-2018-050 | 04 - Southeast | 508286 | CAMPCOR4 | 138 | 8092.9 | 8092.1 | -0.8
GEN-2018-050 | 04 - Southeast | 500150 | CARROLL4 | 138 | 13075.1 | 13058.5 | -16.6
GEN-2018-050 | 04 - Southeast | 500140 | CARROLL6 | 230 | 13465.2 | 13440.4 | -24.8
GEN-2018-050 | 04 - Southeast | 508106 | CASSTP4 | 138 | 7376.7 | 7380.6 | 3.9
GEN-2018-050 | 04 - Southeast | 507771 | CEDARGR4 | 138 | 22083.7 | 22067.4 | -16.3
GEN-2018-050 | 04 - Southeast | 508337 | CHAPELH4 | 138 | 7415.1 | 7415.4 | 0.3
GEN-2018-050 | 04 - Southeast | 509664 | CHAPLHL4 | 138 | 7173.6 | 7173.6 | 0
GEN-2018-050 | 04 - Southeast | 5918 | DCEAST | 345 | 4476.9 | 4476.9 | 0
GEN-2018-050 | 04 - Southeast | 509607 | DIAN 4 | 138 | 11572.2 | 11559.6 | -12.6
GEN-2018-050 | 04 - Southeast | 508831 | DIANA 4 | 138 | 28842.5 | 28829.5 | -13
GEN-2018-050 | 04 - Southeast | 508832 | DIANA 7 | 345 | 18717.2 | 18714.6 | -2.6
GEN-2018-050 | 04 - Southeast | 509639 | DIANASW4 | 138 | 12045.1 | 12032.2 | -12.9
GEN-2018-050 | 04 - Southeast | 500260 | DOLHILL6 | 230 | 15089.5 | 15074.9 | -14.6
GEN-2018-050 | 04 - Southeast | 500250 | DOLHILL7 | 345 | 12305 | 12306.7 | 1.7
GEN-2018-050 | 04 - Southeast | 509645 | DUGLASV2 | 69 | 6382.3 | 6432 | 49.7
GEN-2018-050 | 04 - Southeast | 509666 | DUGLASV4 | 138 | 4959.5 | 5020.6 | 61.1
GEN-2018-050 | 04 - Southeast | 509092 | EASTON 4 | 138 | 24123.4 | 24129.8 | 6.4
GEN-2018-050 | 04 - Southeast | 508369 | EXXONM 4 | 138 | 6661.8 | 6659.4 | -2.4
GEN-2018-050 | 04 - Southeast | 507726 | FLOURNY2 | 69 | 14016.2 | 13994.6 | -21.6
GEN-2018-050 | 04 - Southeast | 507727 | FLOURNY4 | 138 | 16378.3 | 16354.9 | -23.4
GEN-2018-050 | 04 - Southeast | 507728 | FORBNGT2 | 69 | 17587.3 | 17570.1 | -17.2
GEN-2018-050 | 04 - Southeast | 507730 | FTHUMBG2 | 69 | 18089.4 | 18080.3 | -9.1
GEN-2018-050 | 04 - Southeast | 507731 | FTHUMBG4 | 138 | 19220 | 19214.8 | -5.2
GEN-2018-050 | 04 - Southeast | 588404 | G16-167-TAP | 138 | 9774.7 | 9762.1 | -12.6
GEN-2018-050 | 04 - Southeast | 588400 | GEN-2016-167 | 138 | 9675.5 | 9663 | -12.5
GEN-2018-050 | 04 - Southeast | 762845 | GEN-2018-050 | 345 | 11701.9 | 11740.3 | 38.4
GEN-2018-050 | 04 - Southeast | 507732 | GENMOTR4 | 138 | 17552.9 | 17527.4 | -25.5
GEN-2018-050 | 04 - Southeast | 508595 | HALLSVLS4 | 138 | 18600.8 | 18601.6 | 0.8
GEN-2018-050 | 04 - Southeast | 507735 | HARTSIS4 | 138 | 16163.3 | 16152.7 | -10.6
GEN-2018-050 | 04 - Southeast | 521157 | HUGO 7 | 345 | 11298.9 | 11219 | -79.9
GEN-2018-050 | 04 - Southeast | 500430 | IPAPER 4 | 138 | 5364.5 | 5354.8 | -9.7
GEN-2018-050 | 04 - Southeast | 508059 | IPC T 4 | 138 | 8019 | 8021.7 | 2.7
GEN-2018-050 | 04 - Southeast | 508833 | IPCJEFF4 | 138 | 12162.3 | 12164.2 | 1.9
GEN-2018-050 | 04 - Southeast | 508835 | JEFFRSN4 | 138 | 13428.9 | 13431.8 | 2.9
GEN-2018-050 | 04 - Southeast | 509050 | KEATCHI4 | 138 | 7854.7 | 7826.2 | -28.5
GEN-2018-050 | 04 - Southeast | 509623 | LAKEPIN2 | 69 | 7343.1 | 7341.7 | -1.4
GEN-2018-050 | 04 - Southeast | 509624 | LAKEPIN4 | 138 | 7396.9 | 7396.7 | -0.2
GEN-2018-050 | 04 - Southeast | 509366 | LAYFLD8 | 500 | 10182.8 | 10170.6 | -12.2
GEN-2018-050 | 04 - Southeast | 507794 | LEASIDE 2 | 69 | 12856.8 | 12832.4 | -24.4
GEN-2018-050 | 04 - Southeast | 507793 | LEASIDE 4 | 138 | 22127.7 | 22092.1 | -35.6
GEN-2018-050 | 04 - Southeast | 508572 | LEBROCK7 | 345 | 15766.4 | 15734.4 | -32
GEN-2018-050 | 04 - Southeast | 508805 | LIEBERM2 | 69 | 9063.7 | 9045.3 | -18.4
GEN-2018-050 | 04 - Southeast | 508806 | LIEBERM4 | 138 | 16587.9 | 16570.6 | -17.3
GEN-2018-050 | 04 - Southeast | 508062 | LINDEN 2 | 69 | 5865.7 | 5858.6 | -7.1
GEN-2018-050 | 04 - Southeast | 508807 | LINTNRD4 | 138 | 8787.3 | 8775.7 | -11.6
GEN-2018-050 | 04 - Southeast | 507738 | LINWOOD4 | 138 | 22207.1 | 22191.1 | -16
GEN-2018-050 | 04 - Southeast | 508552 | LLAMOND4 | 138 | 7063 | 7054.4 | -8.6
GEN-2018-050 | 04 - Southeast | 508808 | LONGWD 4 | 138 | 24405.6 | 24384.1 | -21.5
GEN-2018-050 | 04 - Southeast | 508809 | LONGWD 7 | 345 | 15356.6 | 15339.9 | -16.7
GEN-2018-050 | 04 - Southeast | 508320 | LONSTAR2 | 69 | 8208.2 | 8199.4 | -8.8
GEN-2018-050 | 04 - Southeast | 508295 | LSREC 2 | 69 | 7614.5 | 7605.7 | -8.8
GEN-2018-050 | 04 - Southeast | 508296 | LSSOUTH2 | 69 | 9786.9 | 9776.7 | -10.2
GEN-2018-050 | 04 - Southeast | 508297 | LSSOUTH4 | 138 | 17266.1 | 17273.3 | 7.2
GEN-2018-050 | 04 - Southeast | 508298 | LYDIA 7 | 345 | 12551.3 | 12518.5 | -32.8
GEN-2018-050 | 04 - Southeast | 500525 | MANCOMP 6 | 230 | 8605.7 | 8591.5 | -14.2
GEN-2018-050 | 04 - Southeast | 508576 | MARAUTO2 | 69 | 17757.9 | 17746.3 | -11.6
GEN-2018-050 | 04 - Southeast | 508557 | MARSHL-4 | 138 | 16604.4 | 16602.3 | -2.1
GEN-2018-050 | 04 - Southeast | 507742 | MCWILLI4 | 138 | 21055.9 | 21047.5 | -8.4
GEN-2018-050 | 04 - Southeast | 507788 | MINDEN-3 | 115 | 5438.1 | 5439 | 0.9
GEN-2018-050 | 04 - Southeast | 508064 | MUNZCTY4 | 138 | 7071 | 7187.9 | 116.9
GEN-2018-050 | 04 - Southeast | 508049 | NASH 4 | 138 | 19246.7 | 19415.7 | 169
GEN-2018-050 | 04 - Southeast | 508810 | NBENTON2 | 69 | 4138 | 4126.3 | -11.7
GEN-2018-050 | 04 - Southeast | 508811 | NBENTON4 | 138 | 9100.2 | 9088.1 | -12.1
GEN-2018-050 | 04 - Southeast | 508560 | NEWGLAD4 | 138 | 9523.5 | 9521.2 | -2.3
GEN-2018-050 | 04 - Southeast | 508827 | NGPL 4 | 138 | 10093.3 | 10082.4 | -10.9
GEN-2018-050 | 04 - Southeast | 508837 | NGPLTAP4 | 138 | 13374.9 | 13361.8 | -13.1
GEN-2018-050 | 04 - Southeast | 507745 | NMARKET2 | 69 | 16023 | 16013.9 | -9.1
GEN-2018-050 | 04 - Southeast | 509628 | NOONDAY4 | 138 | 5835.9 | 5828.3 | -7.6
GEN-2018-050 | 04 - Southeast | 507774 | NORAM 4 | 138 | 16982.3 | 16969.4 | -12.9
GEN-2018-050 | 04 - Southeast | 508070 | NWT-BNT4 | 138 | 23653.9 | 23957.4 | 303.5
GEN-2018-050 | 04 - Southeast | 508071 | NWTXARK4 | 138 | 24636.3 | 24941.4 | 305.1
GEN-2018-050 | 04 - Southeast | 508072 | NWTXARK7 | 345 | 13088.2 | 13159.5 | 71.3
GEN-2018-050 | 04 - Southeast | 508816 | OAKPH 4 | 138 | 19163.4 | 19143.6 | -19.8
GEN-2018-050 | 04 - Southeast | 508812 | OILCITY2 | 69 | 7265.5 | 7251 | -14.5
GEN-2018-050 | 04 - Southeast | 507431 | PATTERS4 | 138 | 12990.9 | 13154.3 | 163.4
GEN-2018-050 | 04 - Southeast | 508350 | PERDUE 2 | 69 | 13366.7 | 13360.2 | -6.5
GEN-2018-050 | 04 - Southeast | 508351 | PERDUE 4 | 138 | 10659.1 | 10655 | -4.1
GEN-2018-050 | 04 - Southeast | 508310 | PETTY 4 | 138 | 7891.3 | 7891.2 | -0.1
GEN-2018-050 | 04 - Southeast | 507746 | PIERMNT4 | 138 | 16209.7 | 16200.7 | -9
GEN-2018-050 | 04 - Southeast | 507747 | PINESRD2 | 69 | 10644.2 | 10631.5 | -12.7
GEN-2018-050 | 04 - Southeast | 508562 | PIRKEY 4 | 138 | 41252.5 | 41272.2 | 19.7
GEN-2018-050 | 04 - Southeast | 508563 | PIRKEY 7 | 345 | 16892.6 | 16866.5 | -26.1
GEN-2018-050 | 04 - Southeast | 508312 | PITTSB_2 | 69 | 8640.3 | 8638 | -2.3
GEN-2018-050 | 04 - Southeast | 508313 | PITTSB_4 | 138 | 8873.2 | 8872.3 | -0.9
GEN-2018-050 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 14161.2 | 14118.5 | -42.7
GEN-2018-050 | 04 - Southeast | 508564 | PLILER 4 | 138 | 12186.4 | 12177.2 | -9.2
GEN-2018-050 | 04 - Southeast | 507748 | POWELL 4 | 138 | 19263.1 | 19244.4 | -18.7
GEN-2018-050 | 04 - Southeast | 507782 | PROBSON4 | 138 | 8467.4 | 8456.2 | -11.2
GEN-2018-050 | 04 - Southeast | 507749 | RAINES 4 | 138 | 16204.2 | 16197.3 | -6.9
GEN-2018-050 | 04 - Southeast | 500255 | REDBAYOU_6 | 230 | 10540.3 | 10525.7 | -14.6
GEN-2018-050 | 04 - Southeast | 509668 | ROACH 2 | 69 | 6062.5 | 6075.2 | 12.7
GEN-2018-050 | 04 - Southeast | 509083 | ROKHILL4 | 138 | 11250.8 | 11215.4 | -35.4
GEN-2018-050 | 04 - Southeast | 507754 | S SHV 2 | 69 | 18355.6 | 18337.6 | -18
GEN-2018-050 | 04 - Southeast | 507755 | S SHV 4 | 138 | 22948.7 | 22927.6 | -21.1
GEN-2018-050 | 04 - Southeast | 508577 | SABINEM4 | 138 | 22239.7 | 22244.7 | 5
GEN-2018-050 | 04 - Southeast | 508566 | SABMINT4 | 138 | 33688.6 | 33700.5 | 11.9
GEN-2018-050 | 04 - Southeast | 508567 | SCOTTSV4 | 138 | 12079.8 | 12072.7 | -7.1
GEN-2018-050 | 04 - Southeast | 508368 | SCROGNSSW4 | 138 | 5818.7 | 5816.1 | -2.6
GEN-2018-050 | 04 - Southeast | 508569 | SEMRSHL4 | 138 | 13390.4 | 13385.7 | -4.7
GEN-2018-050 | 04 - Southeast | 507756 | SHEDRD 2 | 69 | 17204.4 | 17197.9 | -6.5
GEN-2018-050 | 04 - Southeast | 5921 | SPP-CAP1 | 345 | 20559.1 | 20616.3 | 57.2
GEN-2018-050 | 04 - Southeast | 5922 | SPP-CAP2 | 345 | 20559.1 | 20616.3 | 57.2
GEN-2018-050 | 04 - Southeast | 5923 | SPP-CAP3 | 345 | 20559.1 | 20616.3 | 57.2
GEN-2018-050 | 04 - Southeast | 5917 | SPPMAINBUS | 345 | 20559.1 | 20616.3 | 57.2
GEN-2018-050 | 04 - Southeast | 5924 | SPP-REAC1 | 345 | 20559.1 | 20616.3 | 57.2
GEN-2018-050 | 04 - Southeast | 508571 | SPRHILL4 | 138 | 8357.8 | 8347.3 | -10.5
GEN-2018-050 | 04 - Southeast | 507757 | SPRIDGE4 | 138 | 11108.2 | 11085.4 | -22.8
GEN-2018-050 | 04 - Southeast | 507789 | STLGENS4 | 138 | 24568.7 | 24576.8 | 8.1
GEN-2018-050 | 04 - Southeast | 509052 | STONWAL4 | 138 | 10280 | 10250.5 | -29.5
GEN-2018-050 | 04 - Southeast | 508080 | SUGARHL4 | 138 | 11967.8 | 12009.2 | 41.4
GEN-2018-050 | 04 - Southeast | 507758 | SUMMERG2 | 69 | 11129.3 | 11108.5 | -20.8
GEN-2018-050 | 04 - Southeast | 508815 | SUPEROR2 | 69 | 6738.1 | 6725.5 | -12.6
GEN-2018-050 | 04 - Southeast | 507759 | SW SHV 4 | 138 | 30658.4 | 30616.9 | -41.5
GEN-2018-050 | 04 - Southeast | 507760 | SW SHV 7 | 345 | 15625.4 | 15605.2 | -20.2
GEN-2018-050 | 04 - Southeast | 507762 | T70THST2 | 69 | 12690.2 | 12678.7 | -11.5
GEN-2018-050 | 04 - Southeast | 508585 | TENRUSK7 | 345 | 7698.2 | 7654.9 | -43.3
GEN-2018-050 | 04 - Southeast | 507763 | TRICHEL4 | 138 | 16084.4 | 16077.7 | -6.7
GEN-2018-050 | 04 - Southeast | 507454 | TURK 4 | 138 | 24085.5 | 24217.3 | 131.8
GEN-2018-050 | 04 - Southeast | 507455 | TURK 7 | 345 | 8898 | 8926.9 | 28.9
GEN-2018-050 | 04 - Southeast | 510918 | VALIANT4 | 138 | 14830.6 | 14735.6 | -95
GEN-2018-050 | 04 - Southeast | 510911 | VALIANT7 | 345 | 13306.9 | 13221.3 | -85.6
GEN-2018-050 | 04 - Southeast | 507764 | WALLAKE2 | 69 | 8744.6 | 8731.2 | -13.4
GEN-2018-050 | 04 - Southeast | 507765 | WALLAKE4 | 138 | 10535.2 | 10521.2 | -14
GEN-2018-050 | 04 - Southeast | 508839 | WASKOM 2 | 69 | 4490.7 | 4483.5 | -7.2
GEN-2018-050 | 04 - Southeast | 507766 | WATERWK2 | 69 | 16782.8 | 16772.5 | -10.3
GEN-2018-050 | 04 - Southeast | 508089 | WATLANT2 | 69 | 8060.1 | 8054.7 | -5.4
GEN-2018-050 | 04 - Southeast | 508090 | WATLANT4 | 138 | 7404.1 | 7407.4 | 3.3
GEN-2018-050 | 04 - Southeast | 508359 | WELSH 7 | 345 | 20559.1 | 20616.3 | 57.2
GEN-2018-050 | 04 - Southeast | 5919 | WELSHDC1 | 345 | 20559.1 | 20616.3 | 57.2
GEN-2018-050 | 04 - Southeast | 508355 | WELSHRE4 | 138 | 7404.2 | 7404.9 | 0.7
GEN-2018-050 | 04 - Southeast | 507767 | WESTELC4 | 138 | 20379.1 | 20348.6 | -30.5
GEN-2018-050 | 04 - Southeast | 508840 | WILKES 4 | 138 | 30098.2 | 30164.8 | 66.6
GEN-2018-050 | 04 - Southeast | 508841 | WILKES 7 | 345 | 15083.4 | 15105.6 | 22.2
GEN-2018-050 | 04 - Southeast | 509103 | WLNTSPRINGS4 | 138 | 8902.9 | 8876.9 | -26
GEN-2018-050 | 04 - Southeast | 507770 | WOOLWTP2 | 69 | 11639.6 | 11620.8 | -18.8
GEN-2018-055 | 04 - Southeast | 511488 | 112GORE4 | 138 | 12944.4 | 12962.6 | 18.2
GEN-2018-055 | 04 - Southeast | 514908 | ARCADIA7 | 345 | 27716.6 | 27798.6 | 82
GEN-2018-055 | 04 - Southeast | 515372 | ARDWEST4 | 138 | 13037.1 | 12980.4 | -56.7
GEN-2018-055 | 04 - Southeast | 511537 | ARTVLTP4 | 138 | 11920.8 | 11935.2 | 14.4
GEN-2018-055 | 04 - Southeast | 515150 | CANEYCK4 | 138 | 9349.1 | 9302.5 | -46.6
GEN-2018-055 | 04 - Southeast | 515138 | CARTER 4 | 138 | 13053.3 | 12998.4 | -54.9
GEN-2018-055 | 04 - Southeast | 515561 | CARTRCO4 | 138 | 10116.1 | 10076.2 | -39.9
GEN-2018-055 | 04 - Southeast | 521125 | CHEEK_4 | 138 | 8866.6 | 8819.3 | -47.3
GEN-2018-055 | 04 - Southeast | 515415 | CHEEKTP4 | 138 | 12864.7 | 12807.4 | -57.3
GEN-2018-055 | 04 - Southeast | 511436 | COMANC-2 | 69 | 9755.9 | 9761 | 5.1
GEN-2018-055 | 04 - Southeast | 511437 | COMANC-4 | 138 | 18598.6 | 18665.7 | 67.1
GEN-2018-055 | 04 - Southeast | 511494 | COMMTAP4 | 138 | 22235.4 | 22315.5 | 80.1
GEN-2018-055 | 04 - Southeast | 510946 | C-RIVER4 | 138 | 13144 | 13112 | -32
GEN-2018-055 | 04 - Southeast | 515422 | C-RIVER7 | 345 | 10106.6 | 10121.1 | 14.5
GEN-2018-055 | 04 - Southeast | 516006 | DMNDSPG7 | 345 | 8018.8 | 7995.2 | -23.6
GEN-2018-055 | 04 - Southeast | 514934 | DRAPER 7 | 345 | 26206.4 | 26290.2 | 83.8
GEN-2018-055 | 04 - Southeast | 515873 | DRPSPRG4 | 138 | 11261.6 | 11209.5 | -52.1
GEN-2018-055 | 04 - Southeast | 511487 | ELGINJT2 | 69 | 8685.6 | 8683.4 | -2.2
GEN-2018-055 | 04 - Southeast | 511486 | ELGINJT4 | 138 | 10220.4 | 10224.7 | 4.3
GEN-2018-055 | 04 - Southeast | 511563 | ELSWORTH 4 | 138 | 10145.7 | 10149.9 | 4.2
GEN-2018-055 | 04 - Southeast | 588839 | FIREWHL-TAP | 345 | 11256.3 | 11439.7 | 183.4
GEN-2018-055 | 04 - Southeast | 511423 | FLE TAP4 | 138 | 9022.4 | 9024.8 | 2.4
GEN-2018-055 | 04 - Southeast | 511422 | FLETCHR4 | 138 | 8228.7 | 8230.3 | 1.6
GEN-2018-055 | 04 - Southeast | 515162 | FNDTION4 | 138 | 12268 | 12215.2 | -52.8
GEN-2018-055 | 04 - Southeast | 515131 | FOX 4 | 138 | 7660.6 | 7626.2 | -34.4
GEN-2018-055 | 04 - Southeast | 560078 | G16-037-TAP | 345 | 10235.1 | 10357.7 | 122.6
GEN-2018-055 | 04 - Southeast | 560088 | G16-063-TAP | 345 | 8107.7 | 8046.2 | -61.5
GEN-2018-055 | 04 - Southeast | 587744 | G16-091-TAP | 345 | 16130 | 16201.1 | 71.1
GEN-2018-055 | 04 - Southeast | 587794 | G16-097-TAP | 138 | 11834.6 | 11839.4 | 4.8
GEN-2018-055 | 04 - Southeast | 762216 | G17-151TAP | 345 | 7736.5 | 7726.2 | -10.3
GEN-2018-055 | 04 - Southeast | 760938 | G17-171-TAP | 345 | 11452.1 | 11648.9 | 196.8
GEN-2018-055 | 04 - Southeast | 762467 | G18-015-TAP | 345 | 5062.4 | 5051.1 | -11.3
GEN-2018-055 | 04 - Southeast | 563259 | GEN-2015-092 | 345 | 6338.3 | 6696.8 | 358.5
GEN-2018-055 | 04 - Southeast | 563269 | GEN-2015-093 | 345 | 10728.5 | 10745.9 | 17.4
GEN-2018-055 | 04 - Southeast | 587430 | GEN-2016-063 | 345 | 8003.6 | 7942.5 | -61.1
GEN-2018-055 | 04 - Southeast | 587740 | GEN-2016-091 | 345 | 11095.8 | 11120.8 | 25
GEN-2018-055 | 04 - Southeast | 587770 | GEN-2016-095 | 345 | 11589.9 | 11617.3 | 27.4
GEN-2018-055 | 04 - Southeast | 588710 | GEN-2017-027 | 138 | 10066.2 | 10026.4 | -39.8
GEN-2018-055 | 04 - Southeast | 588760 | GEN-2017-033 | 345 | 3842.7 | 3832.8 | -9.9
GEN-2018-055 | 04 - Southeast | 589130 | GEN-2017-075 | 345 | 8096.4 | 8035 | -61.4
GEN-2018-055 | 04 - Southeast | 760830 | GEN-2017-149 | 345 | 4100.4 | 4091.9 | -8.5
GEN-2018-055 | 04 - Southeast | 762217 | GEN-2017-151 | 345 | 5775.2 | 5767.7 | -7.5
GEN-2018-055 | 04 - Southeast | 760851 | GEN-2017-154 | 345 | 3734.1 | 3726.7 | -7.4
GEN-2018-055 | 04 - Southeast | 761859 | GEN-2017-166 | 345 | 7277.9 | 7263.2 | -14.7
GEN-2018-055 | 04 - Southeast | 760939 | GEN-2017-171 | 345 | 11452.1 | 11648.9 | 196.8
GEN-2018-055 | 04 - Southeast | 762460 | GEN-2018-015 | 345 | 5053.7 | 5042.4 | -11.3
GEN-2018-055 | 04 - Southeast | 762900 | GEN-2018-055 | 345 | 4359.5 | 4776.9 | 417.4
GEN-2018-055 | 04 - Southeast | 515147 | GLASSES4 | 138 | 8530.9 | 8486.2 | -44.7
GEN-2018-055 | 04 - Southeast | 515802 | GRACMNT4 | 138 | 34054.9 | 34095.8 | 40.9
GEN-2018-055 | 04 - Southeast | 515800 | GRACMNT7 | 345 | 19727.6 | 19818.3 | 90.7
GEN-2018-055 | 04 - Southeast | 521122 | HOWE 4 | 138 | 11306.3 | 11259.1 | -47.2
GEN-2018-055 | 04 - Southeast | 521157 | HUGO 7 | 345 | 11298.9 | 11219 | -79.9
GEN-2018-055 | 04 - Southeast | 520948 | HUGO PP4 | 138 | 22755.6 | 22675.3 | -80.3
GEN-2018-055 | 04 - Southeast | 520560 | HUGOITC4 | 138 | 22434.8 | 22346.9 | -87.9
GEN-2018-055 | 04 - Southeast | 514808 | JOHNCO 4 | 138 | 15979.5 | 15916.1 | -63.4
GEN-2018-055 | 04 - Southeast | 514809 | JOHNCO 7 | 345 | 11293.7 | 11272.2 | -21.5
GEN-2018-055 | 04 - Southeast | 510925 | KIOWA 7 | 345 | 13907.6 | 13864.7 | -42.9
GEN-2018-055 | 04 - Southeast | 511466 | L.E.S.-2 | 69 | 16515.4 | 16524.7 | 9.3
GEN-2018-055 | 04 - Southeast | 511467 | L.E.S.-4 | 138 | 25561.1 | 25671.6 | 110.5
GEN-2018-055 | 04 - Southeast | 511468 | L.E.S.-7 | 345 | 13957.6 | 14097.6 | 140
GEN-2018-055 | 04 - Southeast | 511469 | LGORE-N2 | 69 | 8104.8 | 8103.2 | -1.6
GEN-2018-055 | 04 - Southeast | 511470 | LGORE-S2 | 69 | 7049.2 | 7047.4 | -1.8
GEN-2018-055 | 04 - Southeast | 515144 | LONEGRV4 | 138 | 14295.6 | 14236.2 | -59.4
GEN-2018-055 | 04 - Southeast | 515151 | LTLCITY4 | 138 | 7480.4 | 7442.4 | -38
GEN-2018-055 | 04 - Southeast | 511431 | LWS S4 | 138 | 11263 | 11274.8 | 11.8
GEN-2018-055 | 04 - Southeast | 511439 | LWSTAP 4 | 138 | 11752.4 | 11765.9 | 13.5
GEN-2018-055 | 04 - Southeast | 508298 | LYDIA 7 | 345 | 12551.3 | 12518.5 | -32.8
GEN-2018-055 | 04 - Southeast | 515149 | MADINDT4 | 138 | 8528.8 | 8484.1 | -44.7
GEN-2018-055 | 04 - Southeast | 520988 | MARIETA4 | 138 | 7485.2 | 7446.5 | -38.7
GEN-2018-055 | 04 - Southeast | 515121 | MILLCKT4 | 138 | 11254.7 | 11208.3 | -46.4
GEN-2018-055 | 04 - Southeast | 514801 | MINCO 7 | 345 | 23878.2 | 23943 | 64.8
GEN-2018-055 | 04 - Southeast | 515160 | MRIETA 2 | 138 | 7579.6 | 7540 | -39.6
GEN-2018-055 | 04 - Southeast | 515224 | MUSKOGE7 | 345 | 27171 | 27664 | 493
GEN-2018-055 | 04 - Southeast | 508072 | NWTXARK7 | 345 | 13088.2 | 13159.5 | 71.3
GEN-2018-055 | 04 - Southeast | 511456 | O.K.U.-7 | 345 | 5444.6 | 5435.5 | -9.1
GEN-2018-055 | 04 - Southeast | 599891 | OKLAUN 7 | 345 | 4262 | 4262 | 0
GEN-2018-055 | 04 - Southeast | 511565 | OKLAUN HVDC7 | 345 | 5428.8 | 5419.7 | -9.1
GEN-2018-055 | 04 - Southeast | 529304 | OMDUNCN4 | 138 | 6719 | 6710.5 | -8.5
GEN-2018-055 | 04 - Southeast | 515563 | ORIGINW4 | 138 | 5936.8 | 5908.7 | -28.1
GEN-2018-055 | 04 - Southeast | 510907 | PITTSB-7 | 345 | 14161.2 | 14118.5 | -42.7
GEN-2018-055 | 04 - Southeast | 515130 | POOLVIL4 | 138 | 9830.2 | 9790.9 | -39.3
GEN-2018-055 | 04 - Southeast | 515134 | PRARPNT4 | 138 | 5752.8 | 5732.2 | -20.6
GEN-2018-055 | 04 - Southeast | 515128 | RATLIFF2 | 69 | 5326.9 | 5301.3 | -25.6
GEN-2018-055 | 04 - Southeast | 515129 | RATLIFF4 | 138 | 7223.5 | 7194.7 | -28.8
GEN-2018-055 | 04 - Southeast | 515163 | ROCKYPT2 | 69 | 8046.7 | 7999.3 | -47.4
GEN-2018-055 | 04 - Southeast | 515164 | ROCKYPT4 | 138 | 12265.4 | 12209 | -56.4
GEN-2018-055 | 04 - Southeast | 511512 | RPPAPER4 | 138 | 12185.1 | 12200.3 | 15.2
GEN-2018-055 | 04 - Southeast | 511979 | RSHSPR1_MPT1 | 345 | 5806.8 | 5869.5 | 62.7
GEN-2018-055 | 04 - Southeast | 511571 | RUSHSPR7 | 345 | 6541.1 | 6927.5 | 386.4
GEN-2018-055 | 04 - Southeast | 515120 | RUSSET-4 | 138 | 11679.5 | 11621.9 | -57.6
GEN-2018-055 | 04 - Southeast | 521044 | RUSSETT4 | 138 | 11606.4 | 11549 | -57.4
GEN-2018-055 | 04 - Southeast | 515420 | SCMMRCT2 | 69 | 9256.9 | 9203.9 | -53
GEN-2018-055 | 04 - Southeast | 515044 | SEMINOL4 | 138 | 40748.6 | 40800.9 | 52.3
GEN-2018-055 | 04 - Southeast | 515045 | SEMINOL7 | 345 | 28591.5 | 28664.8 | 73.3
GEN-2018-055 | 04 - Southeast | 511474 | SHERID4 | 138 | 12563.9 | 12580.8 | 16.9
GEN-2018-055 | 04 - Southeast | 515172 | SPRNDAL4 | 138 | 12201.3 | 12147.6 | -53.7
GEN-2018-055 | 04 - Southeast | 515932 | STIRLNG4 | 138 | 10179.8 | 10129.9 | -49.9
GEN-2018-055 | 04 - Southeast | 515135 | SUNNYSD4 | 138 | 20303.9 | 20247.1 | -56.8
GEN-2018-055 | 04 - Southeast | 515136 | SUNNYSD7 | 345 | 12217.7 | 12233.9 | 16.2
GEN-2018-055 | 04 - Southeast | 515122 | SXMLCKT4 | 138 | 11416.4 | 11369 | -47.4
GEN-2018-055 | 04 - Southeast | 511568 | TERRYRD7 | 345 | 10464.2 | 10759.4 | 295.2
GEN-2018-055 | 04 - Southeast | 521067 | TEXOMAJ4 | 138 | 9256.3 | 9210 | -46.3
GEN-2018-055 | 04 - Southeast | 525832 | TUCO_INT 7 | 345 | 12494.6 | 12487.7 | -6.9
GEN-2018-055 | 04 - Southeast | 515137 | UNIROY 4 | 138 | 13236 | 13178.8 | -57.2
GEN-2018-055 | 04 - Southeast | 510918 | VALIANT4 | 138 | 14830.6 | 14735.6 | -95
GEN-2018-055 | 04 - Southeast | 510911 | VALIANT7 | 345 | 13306.9 | 13221.3 | -85.6
GEN-2018-055 | 04 - Southeast | 515143 | WOLFCRK4 | 138 | 10218.4 | 10167.8 | -50.6
GEN-2018-004 | 05 - Southwest | 528602 | ANDREWS 3 | 115 | 9689.4 | 9700.2 | 10.8
GEN-2018-004 | 05 - Southwest | 528604 | ANDREWS 6 | 230 | 6076.2 | 6085.3 | 9.1
GEN-2018-004 | 05 - Southwest | 528433 | BENSING 3 | 115 | 8067.9 | 8081.2 | 13.3
GEN-2018-004 | 05 - Southwest | 528385 | BUCKEYE 3 | 115 | 7473.3 | 7489.3 | 16
GEN-2018-004 | 05 - Southwest | 528348 | BUCKEYE_TP 3 | 115 | 8312.3 | 8332.3 | 20
GEN-2018-004 | 05 - Southwest | 528582 | BYRD 3 | 115 | 7386.1 | 7399.3 | 13.2
GEN-2018-004 | 05 - Southwest | 528581 | BYRD_TP 3 | 115 | 7988.4 | 8004 | 15.6
GEN-2018-004 | 05 - Southwest | 528554 | COOPER_RNCH3 | 115 | 6597.9 | 6606.9 | 9
GEN-2018-004 | 05 - Southwest | 527656 | CROSSROADS 7 | 345 | 10767.9 | 10789.2 | 21.3
GEN-2018-004 | 05 - Southwest | 527865 | CUNNIGHM_N 6 | 230 | 17244.3 | 17296 | 51.7
GEN-2018-004 | 05 - Southwest | 527867 | CUNNIGHM_S 6 | 230 | 17244.3 | 17296 | 51.7
GEN-2018-004 | 05 - Southwest | 527864 | CUNNINHAM 3 | 115 | 27243.7 | 27496.1 | 252.4
GEN-2018-004 | 05 - Southwest | 528423 | DCP_ZIA 3 | 115 | 6634.6 | 6640.2 | 5.6
GEN-2018-004 | 05 - Southwest | 528422 | DCP_ZIA TP 3 | 115 | 6997.6 | 7004 | 6.4
GEN-2018-004 | 05 - Southwest | 528589 | DRINKARD 3 | 115 | 7628.3 | 7638.4 | 10.1
GEN-2018-004 | 05 - Southwest | 528533 | DRINKARD_TP3 | 115 | 7531.3 | 7543 | 11.7
GEN-2018-004 | 05 - Southwest | 528470 | E_SANGER 3 | 115 | 12650.8 | 12714 | 63.2
GEN-2018-004 | 05 - Southwest | 527799 | EDDY_NORTH 6 | 230 | 9359.8 | 9374.3 | 14.5
GEN-2018-004 | 05 - Southwest | 528318 | ENRON 3 | 115 | 5892 | 5896.6 | 4.6
GEN-2018-004 | 05 - Southwest | 528317 | ENRON_TP 3 | 115 | 6779.5 | 6786.3 | 6.8
GEN-2018-004 | 05 - Southwest | 528512 | EUNICE 3 | 115 | 5906 | 5912.6 | 6.6
GEN-2018-004 | 05 - Southwest | 762442 | G18-004-TAP | 115 | 22569.1 | 22967.3 | 398.2
GEN-2018-004 | 05 - Southwest | 762438 | GEN-2018-004 | 115 | 22232.5 | 22631 | 398.5
GEN-2018-004 | 05 - Southwest | 527363 | HIGG 3 | 115 | 10345 | 10358.2 | 13.2
GEN-2018-004 | 05 - Southwest | 527286 | HIGGEAST 3 | 115 | 10170.7 | 10182.7 | 12
GEN-2018-004 | 05 - Southwest | 527891 | HOBBS_INT 3 | 115 | 31037.6 | 31357.4 | 319.8
GEN-2018-004 | 05 - Southwest | 527894 | HOBBS_INT 6 | 230 | 19039.2 | 19111.4 | 72.2
GEN-2018-004 | 05 - Southwest | 527896 | HOBBS_INT 7 | 345 | 11655.7 | 11689.6 | 33.9
GEN-2018-004 | 05 - Southwest | 527027 | INK_BASIN 3 | 115 | 13249.4 | 13261.8 | 12.4
GEN-2018-004 | 05 - Southwest | 527028 | INK_BASIN 6 | 230 | 10982.6 | 10998.3 | 15.7
GEN-2018-004 | 05 - Southwest | 527362 | JOHNSON_DRW3 | 115 | 10837.6 | 10860.9 | 23.3
GEN-2018-004 | 05 - Southwest | 527965 | KIOWA 7 | 345 | 8712.8 | 8733.6 | 20.8
GEN-2018-004 | 05 - Southwest | 528399 | LEA_NATIONL3 | 115 | 6819.7 | 6826.6 | 6.9
GEN-2018-004 | 05 - Southwest | 528618 | LE-LOVINTON2 | 69 | 6610 | 6613.2 | 3.2
GEN-2018-004 | 05 - Southwest | 528334 | LE-NRTH_INT3 | 115 | 9088.1 | 9100.8 | 12.7
GEN-2018-004 | 05 - Southwest | 528341 | LE-SANANDRS3 | 115 | 6483.7 | 6495 | 11.3
GEN-2018-004 | 05 - Southwest | 528792 | LE-TEXACO 3 | 115 | 6518.9 | 6530.5 | 11.6
GEN-2018-004 | 05 - Southwest | 528627 | LE-TXACO_TP3 | 115 | 7202 | 7216.4 | 14.4
GEN-2018-004 | 05 - Southwest | 528325 | LE-WAITS 3 | 115 | 9046.2 | 9055.6 | 9.4
GEN-2018-004 | 05 - Southwest | 528333 | LE-WEST_SUB3 | 115 | 9155.8 | 9168.8 | 13
GEN-2018-004 | 05 - Southwest | 528355 | MADDOX 3 | 115 | 26147.8 | 26537.7 | 389.9
GEN-2018-004 | 05 - Southwest | 528353 | MADDOXG23 3 | 115 | 26147.8 | 26537.7 | 389.9
GEN-2018-004 | 05 - Southwest | 528435 | MILLEN 3 | 115 | 11681.4 | 11731.6 | 50.2
GEN-2018-004 | 05 - Southwest | 528436 | MILLEN_TPE 3 | 115 | 11681.4 | 11731.6 | 50.2
GEN-2018-004 | 05 - Southwest | 528434 | MILLEN_TPW 3 | 115 | 11681.4 | 11731.6 | 50.2
GEN-2018-004 | 05 - Southwest | 528491 | MONUMENT 3 | 115 | 15398.2 | 15516.4 | 118.2
GEN-2018-004 | 05 - Southwest | 528568 | MONUMNT_TP 3 | 115 | 10260 | 10289.4 | 29.4
GEN-2018-004 | 05 - Southwest | 528456 | N_HOBBS 3 | 115 | 9054 | 9101.7 | 47.7
GEN-2018-004 | 05 - Southwest | 528442 | NE_HOBBS 3 | 115 | 11937.5 | 11991.3 | 53.8
GEN-2018-004 | 05 - Southwest | 528574 | OXY_NHU_RCF3 | 115 | 15104 | 15245.6 | 141.6
GEN-2018-004 | 05 - Southwest | 528480 | OXY_S_HOBBS3 | 115 | 10559 | 10601.7 | 42.7
GEN-2018-004 | 05 - Southwest | 528575 | OXYPERMIAN 3 | 115 | 15296.5 | 15443.5 | 147
GEN-2018-004 | 05 - Southwest | 527930 | PCA 3 | 115 | 11972.5 | 11988.1 | 15.6
GEN-2018-004 | 05 - Southwest | 528392 | PEARLE 3 | 115 | 6365.6 | 6377.4 | 11.8
GEN-2018-004 | 05 - Southwest | 527963 | POTASH_JCT 6 | 230 | 7469.9 | 7479.5 | 9.6
GEN-2018-004 | 05 - Southwest | 528394 | QUAHADA 3 | 115 | 8076.6 | 8085.9 | 9.3
GEN-2018-004 | 05 - Southwest | 528027 | RDRUNNER 7 | 345 | 8598.6 | 8620.1 | 21.5
GEN-2018-004 | 05 - Southwest | 527284 | RUSSELL 3 | 115 | 9204.2 | 9214.4 | 10.2
GEN-2018-004 | 05 - Southwest | 528477 | S_HOBBS 3 | 115 | 10432.3 | 10474 | 41.7
GEN-2018-004 | 05 - Southwest | 528463 | SANGER_SW 3 | 115 | 15910.2 | 16074.8 | 164.6
GEN-2018-004 | 05 - Southwest | 528404 | SUMMIT_3 | 115 | 5645.5 | 5649.6 | 4.1
GEN-2018-004 | 05 - Southwest | 528484 | SW_4J44 3 | 115 | 11135.5 | 11183.4 | 47.9
GEN-2018-004 | 05 - Southwest | 528413 | TAYLOR 3 | 115 | 14482.1 | 14566.3 | 84.2
GEN-2018-004 | 05 - Southwest | 528449 | W_BENDER 3 | 115 | 14792 | 14925 | 133
GEN-2018-004 | 05 - Southwest | 528498 | W_HOBBS 3 | 115 | 11671.2 | 11724.2 | 53
GEN-2018-004 | 05 - Southwest | 528396 | XTO_BIGEDDY3 | 115 | 8843.2 | 8852.5 | 9.3
GEN-2018-004 | 05 - Southwest | 526935 | YOAKUM 6 | 230 | 18373.5 | 18399 | 25.5
GEN-2018-004 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 9701.4 | 9719.3 | 17.9
GEN-2018-004 | 05 - Southwest | 528420 | ZIA 3 | 115 | 6536 | 6541.4 | 5.4
GEN-2018-015 | 05 - Southwest | 511488 | 112GORE4 | 138 | 12675.8 | 12670.6 | -5.2
GEN-2018-015 | 05 - Southwest | 524415 | AMA_SOUTH 6 | 230 | 13282.4 | 13284 | 1.6
GEN-2018-015 | 05 - Southwest | 526460 | AMOCO_SS 6 | 230 | 9649 | 9654.4 | 5.4
GEN-2018-015 | 05 - Southwest | 525840 | ANTELOPE_1 6 | 230 | 21704.6 | 21825.4 | 120.8
GEN-2018-015 | 05 - Southwest | 511537 | ARTVLTP4 | 138 | 11691.4 | 11682.1 | -9.3
GEN-2018-015 | 05 - Southwest | 515458 | BORDER 7 | 345 | 7451.8 | 7394.3 | -57.5
GEN-2018-015 | 05 - Southwest | 527009 | BRU_SUB 6 | 230 | 14543.8 | 14558.4 | 14.6
GEN-2018-015 | 05 - Southwest | 526160 | CARLISLE 3 | 115 | 13992.5 | 14001.5 | 9
GEN-2018-015 | 05 - Southwest | 526161 | CARLISLE 6 | 230 | 10637.9 | 10651.7 | 13.8
GEN-2018-015 | 05 - Southwest | 511553 | CHISHOLM7 | 345 | 10267.5 | 10202.4 | -65.1
GEN-2018-015 | 05 - Southwest | 511436 | COMANC-2 | 69 | 9708.7 | 9712.2 | 3.5
GEN-2018-015 | 05 - Southwest | 511437 | COMANC-4 | 138 | 18057.8 | 18101 | 43.2
GEN-2018-015 | 05 - Southwest | 511494 | COMMTAP4 | 138 | 21396.7 | 21410.7 | 14
GEN-2018-015 | 05 - Southwest | 527656 | CROSSROADS 7 | 345 | 10767.9 | 10789.2 | 21.3
GEN-2018-015 | 05 - Southwest | 527802 | EDDY_CNTY 7 | 345 | 7254.9 | 7269.6 | 14.7
GEN-2018-015 | 05 - Southwest | 511487 | ELGINJT2 | 69 | 8637.5 | 8627.2 | -10.3
GEN-2018-015 | 05 - Southwest | 511486 | ELGINJT4 | 138 | 10075.4 | 10067.2 | -8.2
GEN-2018-015 | 05 - Southwest | 525850 | ELK_CT1 | 345 | 12479.1 | 12587.3 | 108.2
GEN-2018-015 | 05 - Southwest | 511563 | ELSWORTH 4 | 138 | 10003.7 | 9995.7 | -8
GEN-2018-015 | 05 - Southwest | 511423 | FLE TAP4 | 138 | 8665.3 | 8658.7 | -6.6
GEN-2018-015 | 05 - Southwest | 511422 | FLETCHR4 | 138 | 7931.1 | 7924.6 | -6.5
GEN-2018-015 | 05 - Southwest | 525780 | FLOYD_CNTY 3 | 115 | 6732 | 6729.3 | -2.7
GEN-2018-015 | 05 - Southwest | 560078 | G16-037-TAP | 345 | 8926.7 | 8879.8 | -46.9
GEN-2018-015 | 05 - Southwest | 587744 | G16-091-TAP | 345 | 14015.2 | 13982.1 | -33.1
GEN-2018-015 | 05 - Southwest | 587794 | G16-097-TAP | 138 | 10871.9 | 10869.7 | -2.2
GEN-2018-015 | 05 - Southwest | 762216 | G17-151TAP | 345 | 7657.7 | 7804.2 | 146.5
GEN-2018-015 | 05 - Southwest | 760938 | G17-171-TAP | 345 | 10623.5 | 10594.1 | -29.4
GEN-2018-015 | 05 - Southwest | 762467 | G18-015-TAP | 345 | 4717.6 | 5087.6 | 370
GEN-2018-015 | 05 - Southwest | 563269 | GEN-2015-093 | 345 | 9685.6 | 9652.8 | -32.8
GEN-2018-015 | 05 - Southwest | 587740 | GEN-2016-091 | 345 | 9857.4 | 9823.6 | -33.8
GEN-2018-015 | 05 - Southwest | 587770 | GEN-2016-095 | 345 | 10192.4 | 10158.3 | -34.1
GEN-2018-015 | 05 - Southwest | 588760 | GEN-2017-033 | 345 | 4039.4 | 4077.9 | 38.5
GEN-2018-015 | 05 - Southwest | 762217 | GEN-2017-151 | 345 | 5731.4 | 5802.5 | 71.1
GEN-2018-015 | 05 - Southwest | 762132 | GEN-2017-158 | 230 | 12421.3 | 12424.3 | 3
GEN-2018-015 | 05 - Southwest | 760939 | GEN-2017-171 | 345 | 10623.5 | 10594.1 | -29.4
GEN-2018-015 | 05 - Southwest | 762460 | GEN-2018-015 | 345 | 4708.4 | 5078.7 | 370.3
GEN-2018-015 | 05 - Southwest | 515802 | GRACMNT4 | 138 | 32787.2 | 32781.9 | -5.3
GEN-2018-015 | 05 - Southwest | 515800 | GRACMNT7 | 345 | 17157.3 | 17118 | -39.3
GEN-2018-015 | 05 - Southwest | 526677 | GRASSLAND 6 | 230 | 6298.4 | 6300.7 | 2.3
GEN-2018-015 | 05 - Southwest | 525454 | HALE_CNTY 3 | 115 | 10061.8 | 10055.4 | -6.4
GEN-2018-015 | 05 - Southwest | 525957 | HALE_WNDCL16 | 230 | 11860 | 11883.7 | 23.7
GEN-2018-015 | 05 - Southwest | 527894 | HOBBS_INT 6 | 230 | 19039.2 | 19111.4 | 72.2
GEN-2018-015 | 05 - Southwest | 527896 | HOBBS_INT 7 | 345 | 11655.7 | 11689.6 | 33.9
GEN-2018-015 | 05 - Southwest | 527028 | INK_BASIN 6 | 230 | 10982.6 | 10998.3 | 15.7
GEN-2018-015 | 05 - Southwest | 526337 | JONES 6 | 230 | 17645 | 17664.6 | 19.6
GEN-2018-015 | 05 - Southwest | 527965 | KIOWA 7 | 345 | 8712.8 | 8733.6 | 20.8
GEN-2018-015 | 05 - Southwest | 511466 | L.E.S.-2 | 69 | 16334.7 | 16321 | -13.7
GEN-2018-015 | 05 - Southwest | 511467 | L.E.S.-4 | 138 | 24447.9 | 24465.5 | 17.6
GEN-2018-015 | 05 - Southwest | 511468 | L.E.S.-7 | 345 | 12899.9 | 12898 | -1.9
GEN-2018-015 | 05 - Southwest | 525637 | LAMB_CNTY 6 | 230 | 5419.1 | 5419.7 | 0.6
GEN-2018-015 | 05 - Southwest | 511469 | LGORE-N2 | 69 | 8066.3 | 8055.6 | -10.7
GEN-2018-015 | 05 - Southwest | 511470 | LGORE-S2 | 69 | 7022.1 | 7012.3 | -9.8
GEN-2018-015 | 05 - Southwest | 526298 | LUBBCK_EST 3 | 115 | 14966.2 | 14975.2 | 9
GEN-2018-015 | 05 - Southwest | 526299 | LUBBCK_EST 6 | 230 | 11551.7 | 11560.1 | 8.4
GEN-2018-015 | 05 - Southwest | 526269 | LUBBCK_STH 6 | 230 | 15719.6 | 15736.5 | 16.9
GEN-2018-015 | 05 - Southwest | 511431 | LWS S4 | 138 | 11058.9 | 11050 | -8.9
GEN-2018-015 | 05 - Southwest | 511439 | LWSTAP 4 | 138 | 11530.1 | 11521.5 | -8.6
GEN-2018-015 | 05 - Southwest | 514801 | MINCO 7 | 345 | 20902.1 | 20861.6 | -40.5
GEN-2018-015 | 05 - Southwest | 527149 | MUSTANG 6 | 230 | 15728.4 | 15743.7 | 15.3
GEN-2018-015 | 05 - Southwest | 525586 | NEEDMORE 6 | 230 | 10573.1 | 10576.8 | 3.7
GEN-2018-015 | 05 - Southwest | 525461 | NEWHART 6 | 230 | 10619.2 | 10615.1 | -4.1
GEN-2018-015 | 05 - Southwest | 511456 | O.K.U.-7 | 345 | 5460.8 | 5564.1 | 103.3
GEN-2018-015 | 05 - Southwest | 599891 | OKLAUN 7 | 345 | 4262 | 4262 | 0
GEN-2018-015 | 05 - Southwest | 511565 | OKLAUN HVDC7 | 345 | 5445.1 | 5547.5 | 102.4
GEN-2018-015 | 05 - Southwest | 590003 | OKLEHV14 | 138 | 5160.8 | 5160.8 | 0
GEN-2018-015 | 05 - Southwest | 590001 | OKLEHV24 | 138 | 5048.9 | 5048.9 | 0
GEN-2018-015 | 05 - Southwest | 529304 | OMDUNCN4 | 138 | 6535 | 6516.5 | -18.5
GEN-2018-015 | 05 - Southwest | 525481 | PLANT_X 6 | 230 | 22379.1 | 22385 | 5.9
GEN-2018-015 | 05 - Southwest | 528027 | RDRUNNER 7 | 345 | 8598.6 | 8620.1 | 21.5
GEN-2018-015 | 05 - Southwest | 524909 | ROOSEVELT 6 | 230 | 8909.1 | 8913.7 | 4.6
GEN-2018-015 | 05 - Southwest | 511512 | RPPAPER4 | 138 | 11946.6 | 11939.5 | -7.1
GEN-2018-015 | 05 - Southwest | 511979 | RSHSPR1_MPT1 | 345 | 5557.5 | 5525.1 | -32.4
GEN-2018-015 | 05 - Southwest | 527655 | RSVLT_CC_E 7 | 345 | 9472 | 9489.6 | 17.6
GEN-2018-015 | 05 - Southwest | 511571 | RUSHSPR7 | 345 | 5988.8 | 5959.8 | -29
GEN-2018-015 | 05 - Southwest | 527610 | SAGA_SCOL 7 | 345 | 9692.6 | 9710.4 | 17.8
GEN-2018-015 | 05 - Southwest | 511474 | SHERID4 | 138 | 12308.4 | 12298.4 | -10
GEN-2018-015 | 05 - Southwest | 526076 | STANTON_W 3 | 115 | 9343.3 | 9347.5 | 4.2
GEN-2018-015 | 05 - Southwest | 515136 | SUNNYSD7 | 345 | 10760.4 | 10705.1 | -55.3
GEN-2018-015 | 05 - Southwest | 525212 | SWISHER 3 | 115 | 11383.7 | 11375.1 | -8.6
GEN-2018-015 | 05 - Southwest | 525213 | SWISHER 6 | 230 | 10308.7 | 10307.6 | -1.1
GEN-2018-015 | 05 - Southwest | 511568 | TERRYRD7 | 345 | 9603.5 | 9562.4 | -41.1
GEN-2018-015 | 05 - Southwest | 525531 | TOLK 6 | 230 | 27581.8 | 27597.6 | 15.8
GEN-2018-015 | 05 - Southwest | 525549 | TOLK 7 | 345 | 11176 | 11183.7 | 7.7
GEN-2018-015 | 05 - Southwest | 525826 | TUCO_INT 2 | 69 | 7939.5 | 7940.1 | 0.6
GEN-2018-015 | 05 - Southwest | 525828 | TUCO_INT 3 | 115 | 19804.1 | 19833.1 | 29
GEN-2018-015 | 05 - Southwest | 525830 | TUCO_INT 6 | 230 | 21884.7 | 22007.7 | 123
GEN-2018-015 | 05 - Southwest | 525832 | TUCO_INT 7 | 345 | 12600.8 | 12711.4 | 110.6
GEN-2018-015 | 05 - Southwest | 525816 | TUCO_INT2 2 | 69 | 4688 | 4687.6 | -0.4
GEN-2018-015 | 05 - Southwest | 526525 | WOLFFORTH 6 | 230 | 12742.2 | 12756.7 | 14.5
GEN-2018-015 | 05 - Southwest | 755000 | WWDBORDT | 345 | 10252.2 | 10186.9 | -65.3
GEN-2018-015 | 05 - Southwest | 515375 | WWRDEHV7 | 345 | 19296.9 | 19236 | -60.9
GEN-2018-015 | 05 - Southwest | 526934 | YOAKUM 3 | 115 | 18441.1 | 18452.2 | 11.1
GEN-2018-015 | 05 - Southwest | 526935 | YOAKUM 6 | 230 | 18373.5 | 18399 | 25.5
GEN-2018-015 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 9701.4 | 9719.3 | 17.9
GEN-2018-052 | 05 - Southwest | 528095 | 7-RIVERS 6 | 230 | 6396.3 | 6403.9 | 7.6
GEN-2018-052 | 05 - Southwest | 528195 | AGAVE_PDURO3 | 115 | 8071.7 | 8081 | 9.3
GEN-2018-052 | 05 - Southwest | 528231 | AGAVE_RHIL23 | 115 | 11752.9 | 11756.7 | 3.8
GEN-2018-052 | 05 - Southwest | 528230 | AGAVE_RHILL3 | 115 | 12455.3 | 12459.8 | 4.5
GEN-2018-052 | 05 - Southwest | 526460 | AMOCO_SS 6 | 230 | 9649 | 9654.4 | 5.4
GEN-2018-052 | 05 - Southwest | 528602 | ANDREWS 3 | 115 | 9689.4 | 9700.2 | 10.8
GEN-2018-052 | 05 - Southwest | 528604 | ANDREWS 6 | 230 | 6076.2 | 6085.3 | 9.1
GEN-2018-052 | 05 - Southwest | 528040 | BATTLE_AXE 3 | 115 | 3284.1 | 3283.3 | -0.8
GEN-2018-052 | 05 - Southwest | 528433 | BENSING 3 | 115 | 8067.9 | 8081.2 | 13.3
GEN-2018-052 | 05 - Southwest | 528193 | BLACKRIVER 3 | 115 | 10356 | 10368.9 | 12.9
GEN-2018-052 | 05 - Southwest | 528206 | BLCKRVR_DST3 | 115 | 8182.5 | 8191.9 | 9.4
GEN-2018-052 | 05 - Southwest | 528020 | BOPCO_PKRLK3 | 115 | 12871.7 | 12885.8 | 14.1
GEN-2018-052 | 05 - Southwest | 515458 | BORDER 7 | 345 | 7451.8 | 7394.3 | -57.5
GEN-2018-052 | 05 - Southwest | 527009 | BRU_SUB 6 | 230 | 14543.8 | 14558.4 | 14.6
GEN-2018-052 | 05 - Southwest | 528596 | CARDINAL 3 | 115 | 7692.9 | 7698.1 | 5.2
GEN-2018-052 | 05 - Southwest | 528160 | CARLSBAD 3 | 115 | 11373.5 | 11386.3 | 12.8
GEN-2018-052 | 05 - Southwest | 528225 | CD_SVC_HV 3 | 115 | 11210.4 | 11224.9 | 14.5
GEN-2018-052 | 05 - Southwest | 527483 | CHAVES_CNTY6 | 230 | 4282.6 | 4287.1 | 4.5
GEN-2018-052 | 05 - Southwest | 528222 | CHINA_DRAW 3 | 115 | 11210.4 | 11224.9 | 14.5
GEN-2018-052 | 05 - Southwest | 528223 | CHINA_DRAW 7 | 345 | 5887.6 | 5898.1 | 10.5
GEN-2018-052 | 05 - Southwest | 528252 | CHVRN_EDDYS3 | 115 | 7424.4 | 7432.6 | 8.2
GEN-2018-052 | 05 - Southwest | 527656 | CROSSROADS 7 | 345 | 10767.9 | 10789.2 | 21.3
GEN-2018-052 | 05 - Southwest | 527865 | CUNNIGHM_N 6 | 230 | 17244.3 | 17296 | 51.7
GEN-2018-052 | 05 - Southwest | 527867 | CUNNIGHM_S 6 | 230 | 17244.3 | 17296 | 51.7
GEN-2018-052 | 05 - Southwest | 527864 | CUNNINHAM 3 | 115 | 27243.7 | 27496.1 | 252.4
GEN-2018-052 | 05 - Southwest | 528239 | CUSTERMTN 3 | 115 | 7716 | 7719.5 | 3.5
GEN-2018-052 | 05 - Southwest | 528561 | DOLLARHIDE 3 | 115 | 5038.9 | 5039.8 | 0.9
GEN-2018-052 | 05 - Southwest | 527802 | EDDY_CNTY 7 | 345 | 7254.9 | 7269.6 | 14.7
GEN-2018-052 | 05 - Southwest | 527799 | EDDY_NORTH 6 | 230 | 9359.8 | 9374.3 | 14.5
GEN-2018-052 | 05 - Southwest | 527798 | EDDY_NTH 3 | 115 | 11896.2 | 11908.9 | 12.7
GEN-2018-052 | 05 - Southwest | 527793 | EDDY_STH 3 | 115 | 11896.2 | 11908.9 | 12.7
GEN-2018-052 | 05 - Southwest | 525850 | ELK_CT1 | 345 | 12479.1 | 12587.3 | 108.2
GEN-2018-052 | 05 - Southwest | 599960 | EPTNP-D6 | 230 | 9359.8 | 9374.3 | 14.5
GEN-2018-052 | 05 - Southwest | 762216 | G17-151TAP | 345 | 7657.7 | 7804.2 | 146.5
GEN-2018-052 | 05 - Southwest | 587990 | GEN-2016-121 | 115 | 13669.7 | 13676.5 | 6.8
GEN-2018-052 | 05 - Southwest | 527891 | HOBBS_INT 3 | 115 | 31037.6 | 31357.4 | 319.8
GEN-2018-052 | 05 - Southwest | 527894 | HOBBS_INT 6 | 230 | 19039.2 | 19111.4 | 72.2
GEN-2018-052 | 05 - Southwest | 527896 | HOBBS_INT 7 | 345 | 11655.7 | 11689.6 | 33.9
GEN-2018-052 | 05 - Southwest | 528226 | HOPI_SUB 3 | 115 | 7350.2 | 7357.3 | 7.1
GEN-2018-052 | 05 - Southwest | 527027 | INK_BASIN 3 | 115 | 13249.4 | 13261.8 | 12.4
GEN-2018-052 | 05 - Southwest | 527028 | INK_BASIN 6 | 230 | 10982.6 | 10998.3 | 15.7
GEN-2018-052 | 05 - Southwest | 527999 | INTREPDW_TP3 | 115 | 13934.2 | 13952.3 | 18.1
GEN-2018-052 | 05 - Southwest | 527966 | KIOWA 3 | 115 | 17087.9 | 17114.7 | 26.8
GEN-2018-052 | 05 - Southwest | 527965 | KIOWA 7 | 345 | 8712.8 | 8733.6 | 20.8
GEN-2018-052 | 05 - Southwest | 528505 | LEA_ROAD 3 | 115 | 5828.4 | 5833.8 | 5.4
GEN-2018-052 | 05 - Southwest | 528333 | LE-WEST_SUB3 | 115 | 9155.8 | 9168.8 | 13
GEN-2018-052 | 05 - Southwest | 527953 | LIVSTNRIDGE3 | 115 | 7715.6 | 7719 | 3.4
GEN-2018-052 | 05 - Southwest | 528355 | MADDOX 3 | 115 | 26147.8 | 26537.7 | 389.9
GEN-2018-052 | 05 - Southwest | 528194 | MALAGABEND 3 | 115 | 7963.7 | 7971.4 | 7.7
GEN-2018-052 | 05 - Southwest | 527954 | MEDANOS 3 | 115 | 5579.9 | 5581.3 | 1.4
GEN-2018-052 | 05 - Southwest | 528434 | MILLEN_TPW 3 | 115 | 11681.4 | 11731.6 | 50.2
GEN-2018-052 | 05 - Southwest | 527149 | MUSTANG 6 | 230 | 15728.4 | 15743.7 | 15.3
GEN-2018-052 | 05 - Southwest | 528185 | N_LOVING 7 | 345 | 6608.8 | 6621.6 | 12.8
GEN-2018-052 | 05 - Southwest | 525586 | NEEDMORE 6 | 230 | 10573.1 | 10576.8 | 3.7
GEN-2018-052 | 05 - Southwest | 528182 | NORTH_LOVNG3 | 115 | 12346.9 | 12363.7 | 16.8
GEN-2018-052 | 05 - Southwest | 528232 | OCHOA 3 | 115 | 11773 | 11776.8 | 3.8
GEN-2018-052 | 05 - Southwest | 528552 | OIL_CENTER 3 | 115 | 6077.8 | 6084.5 | 6.7
GEN-2018-052 | 05 - Southwest | 527930 | PCA 3 | 115 | 11972.5 | 11988.1 | 15.6
GEN-2018-052 | 05 - Southwest | 528013 | PHANTOM 3 | 115 | 13064.7 | 13079.4 | 14.7
GEN-2018-052 | 05 - Southwest | 528015 | PHANTOM 7 | 345 | 5767.2 | 5777.3 | 10.1
GEN-2018-052 | 05 - Southwest | 528240 | PONDEROSA 3 | 115 | 4084.4 | 4084.7 | 0.3
GEN-2018-052 | 05 - Southwest | 527961 | POTASH_JCT 2 | 69 | 9721.9 | 9728.6 | 6.7
GEN-2018-052 | 05 - Southwest | 527962 | POTASH_JCT 3 | 115 | 17090 | 17116.7 | 26.7
GEN-2018-052 | 05 - Southwest | 527963 | POTASH_JCT 6 | 230 | 7469.9 | 7479.5 | 9.6
GEN-2018-052 | 05 - Southwest | 528025 | RDRUNNER 3 | 115 | 13897.7 | 13904 | 6.3
GEN-2018-052 | 05 - Southwest | 528027 | RDRUNNER 7 | 345 | 8598.6 | 8620.1 | 21.5
GEN-2018-052 | 05 - Southwest | 528018 | RED_BLUFF 3 | 115 | 10264.1 | 10266 | 1.9
GEN-2018-052 | 05 - Southwest | 528024 | RR_SVC_HV 3 | 115 | 13897.7 | 13904 | 6.3
GEN-2018-052 | 05 - Southwest | 527655 | RSVLT_CC_E 7 | 345 | 9472 | 9489.6 | 17.6
GEN-2018-052 | 05 - Southwest | 527654 | RSVLT_CC_W 7 | 345 | 8392.4 | 8407.2 | 14.8
GEN-2018-052 | 05 - Southwest | 528547 | S_JAL 3 | 115 | 6571.1 | 6573.5 | 2.4
GEN-2018-052 | 05 - Southwest | 527610 | SAGA_SCOL 7 | 345 | 9692.6 | 9710.4 | 17.8
GEN-2018-052 | 05 - Southwest | 527599 | SAGA_SDCOL 7 | 345 | 9692.6 | 9710.4 | 17.8
GEN-2018-052 | 05 - Southwest | 528016 | SAND_DUNES 3 | 115 | 7488.1 | 7489.7 | 1.6
GEN-2018-052 | 05 - Southwest | 528192 | SOUTH_LOVNG3 | 115 | 9409.5 | 9420.6 | 11.1
GEN-2018-052 | 05 - Southwest | 528526 | TEAGUE 3 | 115 | 6445.3 | 6448.2 | 2.9
GEN-2018-052 | 05 - Southwest | 525531 | TOLK 6 | 230 | 27581.8 | 27597.6 | 15.8
GEN-2018-052 | 05 - Southwest | 525549 | TOLK 7 | 345 | 11176 | 11183.7 | 7.7
GEN-2018-052 | 05 - Southwest | 525830 | TUCO_INT 6 | 230 | 21884.7 | 22007.7 | 123
GEN-2018-052 | 05 - Southwest | 525832 | TUCO_INT 7 | 345 | 12600.8 | 12711.4 | 110.6
GEN-2018-052 | 05 - Southwest | 528519 | WARD 3 | 115 | 5780.2 | 5784.1 | 3.9
GEN-2018-052 | 05 - Southwest | 528540 | WHITTEN 3 | 115 | 7650.7 | 7655.2 | 4.5
GEN-2018-052 | 05 - Southwest | 528009 | WIPP 3 | 115 | 7339.1 | 7341.6 | 2.5
GEN-2018-052 | 05 - Southwest | 528236 | WOLFCAMP 3 | 115 | 11295.9 | 11306.4 | 10.5
GEN-2018-052 | 05 - Southwest | 528235 | WOLFCAMP_TP3 | 115 | 12201.4 | 12213.4 | 12
GEN-2018-052 | 05 - Southwest | 528228 | WOOD_DRAW 3 | 115 | 8272.5 | 8280.6 | 8.1
GEN-2018-052 | 05 - Southwest | 528064 | XTO_DI9_TP 3 | 115 | 8117.4 | 8122.6 | 5.2
GEN-2018-052 | 05 - Southwest | 526934 | YOAKUM 3 | 115 | 18441.1 | 18452.2 | 11.1
GEN-2018-052 | 05 - Southwest | 526935 | YOAKUM 6 | 230 | 18373.5 | 18399 | 25.5
GEN-2018-052 | 05 - Southwest | 526936 | YOAKUM_345 | 345 | 9701.4 | 9719.3 | 17.9

## SCRCCT
Study | Case Type | Region Name | Season Year | Season | Contingency Type | Contingency Definition | SCR | Critical_Clearing_Time | POI Bus | Stability Margin | Pg Out | Pg Rated
1801 | TC | North | 23 | SP0 | contingency131 | 659160-659423 | 4.4286 | 0.8272 | GEN-2018-008 | 727.206 | 124.32 | 142
1801 | TC | North | 23 | SP0 | contingency131 | 659160-659423 | 4.4286 | 0.8259 | GEN-2018-008 | 725.8566 | 127.68 | 142
1801 | TC | North | 26 | SP0 | contingency131 | 659160-659423 | 4.4358 | 0.8264 | GEN-2018-008 | 726.3573 | 124.32 | 142
1801 | TC | North | 26 | SP0 | contingency131 | 659160-659423 | 4.4358 | 0.825 | GEN-2018-008 | 725.0105 | 127.68 | 142
1801 | TC | North | 26 | L0 | contingency131 | 659160-659423 | 4.3242 | 0.8256 | GEN-2018-008 | 725.5777 | 124.32 | 142
1801 | TC | North | 26 | L0 | contingency131 | 659160-659423 | 4.3242 | 0.8242 | GEN-2018-008 | 724.2273 | 127.68 | 142
1801 | TC | North | 26 | WP0 | contingency131 | 659160-659423 | 4.4483 | 0.8244 | GEN-2018-008 | 724.3961 | 124.32 | 142
1801 | TC | North | 26 | WP0 | contingency131 | 659160-659423 | 4.4483 | 0.8231 | GEN-2018-008 | 723.0551 | 127.68 | 142
1801 | TC | Nebraska | 26 | SP0 | contingency157 | 653571-653871 | 17.9696 | 0.0263 | GEN-2018-056 | -73.6527 | 102.6 | 114
1801 | TC | Nebraska | 26 | WP0 | contingency157 | 653571-653871 | 17.9746 | 0.0264 | GEN-2018-056 | -73.5927 | 102.6 | 114
1801 | TC | Central | 23 | SP0 | base | N/A | 4.3415 | 0.3394 | GEN-2018-013 | 239.4406 | 74.1 | 90
1801 | TC | Central | 23 | SP0 | base | N/A | 13.013 | 0.0609 | GEN-2018-022 | -39.1019 | 148.5 | 179.6
1801 | TC | Central | 23 | SP0 | base | N/A | 13.013 | 0.0643 | GEN-2018-022 | -35.6517 | 148.5 | 179.6
1801 | TC | Central | 23 | SP0 | contingency36 | 523853-531449 | 3.4144 | 6.8919 | GEN-2018-030 | 6791.8506 | 200 | 239
1801 | TC | Central | 26 | L0 | base | N/A | 3.937 | 0.3492 | GEN-2018-013 | 249.245 | 74.1 | 90
1801 | TC | Central | 26 | L0 | contingency33 | 523106-539672 | 5.8737 | 0.1519 | GEN-2018-009 | 51.9021 | 150 | 168
1801 | TC | Central | 26 | L0 | contingency36 | 523823-531512 | 5.1436 | 0.1523 | GEN-2018-009 | 52.3402 | 150 | 168
1801 | TC | Central | 26 | L0 | contingency42 | 531374-531467 | 5.2726 | 0.1524 | GEN-2018-009 | 52.3989 | 150 | 168
1801 | TC | Central | 26 | L0 | contingency46 | 531405-531510 | 5.1436 | 0.1523 | GEN-2018-009 | 52.3394 | 150 | 168
1801 | TC | Central | 26 | L0 | contingency48 | 531467-539749 | 5.2725 | 0.1524 | GEN-2018-009 | 52.4088 | 150 | 168
1801 | TC | Central | 26 | L0 | contingency57 | 531510-531512-531511 | 5.1435 | 0.1523 | GEN-2018-009 | 52.3442 | 150 | 168
1801 | TC | Central | 26 | L0 | contingency176 | 539646-539652 | 5.6751 | 0.1531 | GEN-2018-009 | 53.1011 | 150 | 168
1801 | TC | Central | 26 | L0 | contingency177 | 539646-539659 | 5.6765 | 0.1531 | GEN-2018-009 | 53.0715 | 150 | 168
1801 | TC | Central | 26 | SP0 | base | N/A | 4.3636 | 0.3378 | GEN-2018-013 | 237.8304 | 74.1 | 90
1801 | TC | Central | 26 | SP0 | base | N/A | 12.9976 | 0.061 | GEN-2018-022 | -39.0011 | 148.5 | 179.6
1801 | TC | Central | 26 | SP0 | base | N/A | 12.9976 | 0.0645 | GEN-2018-022 | -35.5417 | 148.5 | 179.6
1801 | TC | Central | 26 | SP0 | contingency36 | 523853-531449 | 3.4233 | 6.8911 | GEN-2018-030 | 6791.107 | 200 | 239
1801 | TC | Central | 26 | WP0 | base | N/A | 4.3113 | 0.3448 | GEN-2018-013 | 244.7664 | 74.1 | 90
1801 | TC | Central | 26 | WP0 | base | N/A | 12.8228 | 0.0618 | GEN-2018-022 | -38.1824 | 148.5 | 179.6
1801 | TC | Central | 26 | WP0 | base | N/A | 12.8228 | 0.0653 | GEN-2018-022 | -34.6566 | 148.5 | 179.6
1801 | TC | Central | 26 | WP0 | contingency36 | 523853-531449 | 3.3157 | 6.2501 | GEN-2018-030 | 6150.0722 | 200 | 239
1801 | TC | Southeast | 23 | SP0 | base | N/A | 47.5172 | 0 | GEN-2018-021 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 13.4037 | 0 | GEN-2018-003 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 26.1751 | 0 | GEN-2018-011 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 51.5407 | 0 | GEN-2018-021 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 62.0539 | 0 | GEN-2018-024 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 58.2155 | 0 | GEN-2018-026 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 54.784 | 0 | GEN-2018-027 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 28.4047 | 0 | GEN-2018-028 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 55.215 | 0 | GEN-2018-029 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 23.9414 | 0 | GEN-2018-048 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 23.9414 | 0 | GEN-2018-048 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 32.4474 | 0 | GEN-2018-050 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 9.9165 | 0 | GEN-2018-003 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 25.1577 | 0 | GEN-2018-011 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 44.8306 | 0 | GEN-2018-021 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 48.8221 | 0 | GEN-2018-024 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 52.4751 | 0 | GEN-2018-026 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 48.3606 | 0 | GEN-2018-027 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 25.7881 | 0 | GEN-2018-028 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 49.9259 | 0 | GEN-2018-029 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 19.0116 | 0 | GEN-2018-048 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 19.0116 | 0 | GEN-2018-048 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 24.631 | 0 | GEN-2018-050 | 0 | 0 | 0
1801 | TC | Southeast | 26 | SP0 | base | N/A | 65.0176 | 0 | GEN-2018-021 | 0 | 0 | 0
1801 | TC | Southeast | 26 | WP0 | base | N/A | 63.7889 | 0 | GEN-2018-021 | 0 | 0 | 0
1801 | TC | Southwest | 23 | SP0 | contingency3 | 511456-511468 | 5.3633 | 0 | GEN-2018-015 | 0 | 0 | 0
1801 | TC | Southwest | 23 | SP0 | contingency3 | 511456-511468 | 5.3633 | 0 | GEN-2018-015 | 0 | 0 | 0
1801 | TC | Southwest | 26 | L0 | contingency3 | 511456-511468 | 4.8034 | 0 | GEN-2018-015 | 0 | 0 | 0
1801 | TC | Southwest | 26 | L0 | contingency3 | 511456-511468 | 4.8034 | 0 | GEN-2018-015 | 0 | 0 | 0
1801 | TC | Southwest | 26 | SP0 | contingency3 | 511456-511468 | 5.432 | 0 | GEN-2018-015 | 0 | 0 | 0
1801 | TC | Southwest | 26 | SP0 | contingency3 | 511456-511468 | 5.432 | 0 | GEN-2018-015 | 0 | 0 | 0
1801 | TC | Southwest | 26 | WP0 | contingency3 | 511456-511468 | 4.9956 | 0 | GEN-2018-015 | 0 | 0 | 0
1801 | TC | Southwest | 26 | WP0 | contingency3 | 511456-511468 | 4.9956 | 0 | GEN-2018-015 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency200 | 511456-511468 | 10.3609 | 0 | GEN-2018-055 | 0 | 0 | 0
1801 | TC | Southeast | 26 | L0 | contingency333 | 515458-755000 | 9.7734 | 0 | GEN-2018-055 | 0 | 0 | 0

## WSCR
Study | Case Type | Region | Season Year | Season | Contingency Type | Contingency Definition | WSCR Group | WSCR Value | Bus 1 | Bus 2 | Bus 3 | Bus 4 | Bus 5 | Bus 6 | Bus 7 | Bus 8
1801 | TC | 1 | 23 | SP0 | contingency131 | 659160-659423 | 01-23S-2 | 2.7142 | Bus 1: GEN-2017-048,GEN-2018-010; Bus 2: GEN-2018-008; Bus 3: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236
1801 | TC | 1 | 26 | SP0 | contingency131 | 659160-659423 | 01-26S-2 | 2.7233 | Bus 1: GEN-2017-048,GEN-2018-010; Bus 2: GEN-2018-008; Bus 3: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236
1801 | TC | 1 | 26 | WP0 | contingency131 | 659160-659423 | 01-26W-2 | 2.73 | Bus 1: GEN-2017-048,GEN-2018-010; Bus 2: GEN-2018-008; Bus 3: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236
1801 | TC | 1 | 26 | SP0 | contingency3 | 620125-620325 | 01-26S-3 | 2.7458 | Bus 1: GEN-2018-039; Bus 2: GEN-2017-048,GEN-2018-010; Bus 3: GEN-2018-008; Bus 4: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236
1801 | TC | 1 | 26 | L0 | contingency38 | 652435-652444 | 01-26L-1 | 4.7987 | Bus 1: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236; Bus 2: GEN-2017-048,GEN-2018-010
1801 | TC | 1 | 26 | L0 | contingency60 | 652514-652530 | 01-26L-1 | 4.8016 | Bus 1: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236; Bus 2: GEN-2017-048,GEN-2018-010
1801 | TC | 1 | 26 | L0 | contingency65 | 652530-652614 | 01-26L-1 | 4.8016 | Bus 1: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236; Bus 2: GEN-2017-048,GEN-2018-010
1801 | TC | 1 | 26 | L0 | contingency61 | 652514-652614 | 01-26L-1 | 4.8018 | Bus 1: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236; Bus 2: GEN-2017-048,GEN-2018-010
1801 | TC | 1 | 26 | L0 | contingency78 | 655058-655069 | 01-26L-1 | 4.802 | Bus 1: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236; Bus 2: GEN-2017-048,GEN-2018-010
1801 | TC | 1 | 26 | L0 | contingency5 | 620159-620160 | 01-26L-1 | 4.802 | Bus 1: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236; Bus 2: GEN-2017-048,GEN-2018-010
1801 | TC | 1 | 26 | L0 | contingency134 | 659280-659326 | 01-26L-1 | 4.8021 | Bus 1: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236; Bus 2: GEN-2017-048,GEN-2018-010
1801 | TC | 1 | 23 | SP0 | base | N/A | 01-23S-1 | 5.1541 | Bus 1: GEN-2017-048,GEN-2018-010; Bus 2: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236
1801 | TC | 1 | 26 | SP0 | base | N/A | 01-26S-1 | 5.1714 | Bus 1: GEN-2017-048,GEN-2018-010; Bus 2: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236
1801 | TC | 1 | 26 | WP0 | base | N/A | 01-26W-1 | 5.1815 | Bus 1: GEN-2017-048,GEN-2018-010; Bus 2: GEN-2017-214,GEN-2017-215,GEN-2017-216,GEN-2017-235,GEN-2017-236
1801 | TC | 2 | 26 | L0 | contingency157 | 653571-653871 | 02-26L-1 | 5.4368 | Bus 1: GEN-2007-017IS,GEN-2007-18IS,GEN-2016-075; Bus 2: GEN-2015-023,GEN-2017-144
1801 | TC | 2 | 26 | SP0 | contingency157 | 653571-653871 | 02-26S-1 | 5.871 | Bus 1: GEN-2007-017S,GEN-2007-018IS,GEN-2016-075; Bus 2: GEN-2015-023,GEN-2017-144
1801 | TC | 2 | 26 | WP0 | contingency157 | 653571-653871 | 02-26W-1 | 5.8786 | Bus 1: GEN-2007-017IS,GEN-2007-018IS, GEN-2016-075; Bus 2: GEN-2015-023, GEN-2017-144
1801 | TC | 3 | 23 | SP0 | contingency198 | 541201-541500 | 03-23S-1 | 4.2869 | Bus 1: GEN-2018-022; Bus 2: GEN-2014-021,GEN-2016-115,GEN-2017-115,GEN-2018-014
1801 | TC | 3 | 26 | SP0 | contingency198 | 541201-541500 | 03-26S-1 | 4.2516 | Bus 1: GEN-2018-022; Bus 2: GEN-2014-021,GEN-2016-115,GEN-2017-115,GEN-2018-014
1801 | TC | 3 | 26 | WP0 | contingency198 | 541201-541500 | 03-26W-1 | 4.2228 | Bus 1: GEN-2018-022; Bus 2: GEN-2014-021,GEN-2016-115,GEN-2017-115,GEN-2018-014
1801 | TC | 4 | 23 | SP0 | contingency201 | 511468-760938 | 04-23S-1 | 3.4324 | Bus 1: GEN-2014-057,GEN-2015-045,GEN-2015-092; Bus 2: GEN-2017-171,GEN-2017-172, GEN-2017-173
1801 | TC | 4 | 26 | L0 | contingency201 | 511468-760938 | 04-26L-1 | 3.229 | Bus 1: GEN-2014-057,GEN-2015-045,GEN-2015-092; Bus 2: GEN-2017-171,GEN-2017-172, GEN-2017-173
1801 | TC | 4 | 26 | SP0 | contingency201 | 511468-760938 | 04-26S-1 | 3.4385 | Bus 1: GEN-2014-057,GEN-2015-045,GEN-2015-092; Bus 2: GEN-2017-171,GEN-2017-172, GEN-2017-173
1801 | TC | 5 | 26 | SP0 | base | N/A | 05-26S-2 | 3.2752 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 26 | SP0 | base | N/A | 05-26S-6 | 3.6429 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2017-158
1801 | TC | 5 | 26 | SP0 | contingency10 | 525824-525832-525830 | 05-26S-13 | 5.925 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 26 | SP0 | contingency11 | 525825-525832-525830 | 05-26S-13 | 5.9846 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 26 | SP0 | contingency12 | 525832-525850 | 05-26S-13 | 5.721 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 26 | SP0 | contingency13 | 525832-526936 | 05-26S-13 | 5.8751 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 26 | SP0 | contingency3 | 511456-511468 | 05-26S-1 | 2.5821 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-146
1801 | TC | 5 | 26 | SP0 | contingency7 | 511468-760938 | 05-26S-1 | 3.634 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2017-146
1801 | TC | 5 | 26 | SP0 | contingency7 | 511468-760938 | 05-26S-12 | 2.8313 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-015 | GEN-2018-004
1801 | TC | 5 | 26 | SP0 | contingency8 | 515458-525832 | 05-26S-1 | 3.5969 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2017-146
1801 | TC | 5 | 26 | SP0 | contingency8 | 515458-525832 | 05-26S-10 | 2.8098 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-239
1801 | TC | 5 | 26 | SP0 | contingency8 | 515458-525832 | 05-26S-13 | 3.5041 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015
1801 | TC | 5 | 26 | SP0 | contingency9 | 515458-755000 | 05-26S-1 | 3.5929 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2017-146
1801 | TC | 5 | 26 | SP0 | contingency9 | 515458-755000 | 05-26S-10 | 2.8074 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-239
1801 | TC | 5 | 26 | SP0 | contingency9 | 515458-755000 | 05-26S-13 | 3.0526 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015
1801 | TC | 5 | 26 | WP0 | base | N/A | 05-26W-1 | 4.6728 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2017-146
1801 | TC | 5 | 26 | WP0 | base | N/A | 05-26W-10 | 3.3557 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2017-239
1801 | TC | 5 | 26 | WP0 | base | N/A | 05-26W-13 | 5.5673 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 26 | WP0 | base | N/A | 05-26W-2 | 3.0138 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 26 | WP0 | contingency3 | 511456-511468 | 05-26W-1 | 2.3612 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-146
1801 | TC | 5 | 26 | WP0 | contingency7 | 511468-760938 | 05-26W-12 | 2.6143 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-015 | GEN-2018-004
1801 | TC | 5 | 26 | WP0 | contingency8 | 515458-525832 | 05-26W-1 | 3.2902 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2017-146
1801 | TC | 5 | 26 | WP0 | contingency8 | 515458-525832 | 05-26W-10 | 2.5788 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-239
1801 | TC | 5 | 26 | WP0 | contingency8 | 515458-525832 | 05-26W-13 | 3.1307 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015
1801 | TC | 5 | 26 | WP0 | contingency9 | 515458-755000 | 05-26W-1 | 3.2818 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2017-146
1801 | TC | 5 | 26 | WP0 | contingency9 | 515458-755000 | 05-26W-10 | 2.5731 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-239
1801 | TC | 5 | 26 | WP0 | contingency9 | 515458-755000 | 05-26W-13 | 2.7232 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015
1801 | TC | 5 | 23 | SP0 | base | N/A | 05-23S-1 | 5.0368 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2017-146
1801 | TC | 5 | 23 | SP0 | base | N/A | 05-23S-10 | 3.6536 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2017-239
1801 | TC | 5 | 23 | SP0 | base | N/A | 05-23S-2 | 3.279 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 23 | SP0 | contingency10 | 525825-525832-525830 | 05-23SP-13 | 5.8942 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 23 | SP0 | contingency11 | 525832-525850 | 05-23SP-13 | 5.5949 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 23 | SP0 | contingency11 | 525832-525850 | 05-23SP-2 | 2.7602 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 23 | SP0 | contingency12 | 525832-526936 | 05-23SP-13 | 5.7586 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 23 | SP0 | contingency23 | 527864-528348 | 05-23SP-2 | 3.079 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 23 | SP0 | contingency3 | 511456-511468 | 05-23SP-1 | 2.5861 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-146
1801 | TC | 5 | 23 | SP0 | contingency6 | 511468-587744 | 05-23SP-13 | 5.93 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 23 | SP0 | contingency7 | 511468-760938 | 05-23SP-12 | 2.8351 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-015 | GEN-2018-004
1801 | TC | 5 | 23 | SP0 | contingency8 | 515458-525832 | 05-23SP-10 | 2.8166 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-239
1801 | TC | 5 | 23 | SP0 | contingency8 | 515458-525832 | 05-23SP-13 | 3.0244 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015
1801 | TC | 5 | 23 | SP0 | contingency9 | 525824-525832-525830 | 05-23SP-13 | 5.8376 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 26 | L0 | base | N/A | 05-26L-1 | 4.1712 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2017-146
1801 | TC | 5 | 26 | L0 | base | N/A | 05-26L-10 | 2.9689 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2017-239
1801 | TC | 5 | 26 | L0 | base | N/A | 05-26L-13 | 4.8837 | Bus 1: GEN-2017-151; Bus 2: GEN-2018-015
1801 | TC | 5 | 26 | L0 | base | N/A | 05-26L-2 | 2.6702 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 26 | L0 | contingency10 | 525824-525832-525830 | 05-26L-2 | 2.428 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 26 | L0 | contingency11 | 525825-525832-525830 | 05-26L-2 | 2.4377 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 26 | L0 | contingency13 | 525832-526936 | 05-26L-2 | 2.9233 | Bus 1: GEN-2017-187; Bus 2: GEN-2018-004; Bus 3: GEN-2018-015; Bus 4: GEN-2017-151
1801 | TC | 5 | 26 | L0 | contingency14 | 526936-527896 | 05-26L-2 | 2.3904 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 26 | L0 | contingency3 | 511456-511468 | 05-26L-1 | 2.0922 | GEN-2017-158 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-146
1801 | TC | 5 | 26 | L0 | contingency37 | 527894-527896-527895 | 05-26L-2 | 2.4631 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 26 | L0 | contingency71 | 528540-528547 | 05-26L-2 | 2.4704 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2018-004 | GEN-2018-015 | GEN-2017-151
1801 | TC | 5 | 26 | L0 | contingency8 | 515458-525832 | 05-26L-10 | 2.2744 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-239
1801 | TC | 5 | 26 | L0 | contingency8 | 515458-525832 | 05-26L-13 | 2.3852 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015
1801 | TC | 5 | 26 | L0 | contingency9 | 515458-755000 | 05-26L-10 | 2.2639 | GEN-2017-158 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-146 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015 | GEN-2017-239
1801 | TC | 5 | 26 | L0 | contingency9 | 515458-755000 | 05-26L-13 | 2.3793 | GEN-2017-239 | GEN-2017-187 | GEN-2016-121,GEN-2018-052 | GEN-2017-151 | GEN-2018-004 | GEN-2018-015