## Executive Summary
Executive Summary: DISIS-2018-001 Phase 2 Restudy of Power Flow, Stability, and Short-Circuit
Pursuant to the Southwest Power Pool (SPP) Open Access Transmission Tariff (OATT), SPP has conducted this Definitive Interconnection System Impact Study (DISIS) for generation interconnection requests received during the DISIS Queue Cluster Window which closed on March 31, 2018. The primary objective of this DISIS is to identify the system constraints, transient instabilities, and over-dutied equipment associated with connecting the generation to the area transmission system. The Impact Study and other subsequent Interconnection Studies are designed to identify required Transmission Owner Interconnection Facilities, Network Upgrades and other Direct Assignment Facilities needed to inject power into the grid at each specific point of interconnection. The study analysis for the generation interconnection requests included in this DISIS are displayed in this workbook. This workbook provides a convenient method to sort and analyze required study data. The DISIS Manual Version 2.0 posted on http://opsportal.spp.org/Studies/Gen contains details about the DISIS process, methodology, definitions, and useful links. Please review the DISIS Manual or contact gistudies@spp.org for more information about the study process. DISIS-2018-001 Phase 2 Restudy includes study requests in the following cluster groups: ( 01 - North, 02 - Nebraska, 03 - Central, 04 - Southeast, 05 - Southwest ) NOTE: per SPP Tariff Attachment V; section 8.4.2 DISIS Phase Two will consist of a power flow analysis, a stability analysis, and a short-circuit analysis.
DISIS Manual Version 2.0
https://opsportal.spp.org/documents/studies/GI%20MANUAL%20BUSINESS%20PRACTICE_7250_20230915.pdf
This DISIS analyzes the impact of interconnecting new generation for total of:
5,445.09 MW
The minimum cost of interconnecting all requests included in this DISIS is estimated at:
Total Network Upgrade $338,708,005.58 Steady State Network Upgrade $84,397,665.58 Stability Network Upgrade $58,065,092.80 Interconnection Costs: $229,596,240.00
Models Used in Steady State Study
2021 ITP Series
Winter: 2026
Summer: 2023, 2026
Light: 2026
Models Used in Stability Study
2020 MDWG
Winter: 2025, Summer: 2025
By: SPP Generator Interconnection Department
Published: 12/22/2023
Costs for Solar/Battery Requests were allocated using the 26SP (summer peak) model.
Costs for Wind Requests were allocated using the 26L (light load) model.
Assigned Upgrade Costs include the new cumulative impact criteria from BP7250.

## Revision History
Revision History
Date | Author | Change Description
4518400% | SPP | Final Draft Posting
4528200% | SPP | Final Draft Reposting

## Revision Details
Revision Date | Update Type | Tab Order | Results Data Tab | Update Details
4528200% | Cost Correction | 6 | Assigned Upgrade Cost | Identified '36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild' as a contingent upgrade and updated cost per TO. Upgrade ID changed to 'NTC 210708'. Removed allocated cost to GEN-2018-027 associated with this contingent upgrade.
4528200% | Cost Correction | 7 | Upgrade Summary | Identified '36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild' as a contingent upgrade and updated cost per TO. Upgrade ID changed to 'NTC 210708'.
4528200% | LOIS Correction | 4 | Requests | Updated Current Study Projects to reflect updated LOIS amounts and constraints.
4528200% | Constraint Results | 5 | Constraints Summary | Updated Constraints Summary to reflect updated mitigations and model corrections.
4528200% | Total Costs | 1 | Executive Summary | Updated Total Network Costs and Steady State Costs to Reflect Contingent Upgrades, Mitigation Alternatives, and Model Corrections
4528200% | Cost Correction | 6 | Assigned Upgrade Cost | Removed North St. to Northview 115 kV Ckt 1 and 2 Rebuilds and North St. to Salina Main 115 kV Ckt 1 and 2 Rebuilds due to corrected ratings and topology at the North Street 115 kV Substation. Removed allocated cost to GEN-2018-013 associated with this model correction.
4528200% | Cost Correction | 7 | Upgrade Summary | Removed North St. to Northview 115 kV Ckt 1 and 2 Rebuilds and North St. to Salina Main 115 kV Ckt 1 and 2 Rebuilds due to corrected ratings and topology at the North Street 115 kV Substation.
4528200% | Constraint Correction | 5 | Constraints Summary | Removed constraints assigned GEN-2018-013 associated with North St. to Northview 115 kV Ckt 1 and 2 Rebuilds and North St. to Salina Main 115 kV Ckt 1 and 2 Rebuilds.
4528200% | LOIS Correction | 4 | Requests | Removed LOIS assigned GEN-2018-013 associated with North St. to Northview 115 kV Ckt 1 and 2 Rebuilds and North St. to Salina Main 115 kV Ckt 1 and 2 Rebuilds.
4528200% | Cost Correction | 6 | Assigned Upgrade Cost | Removed Wolforth to Terry County 115 kV Rebuild due to corrected ratings. Removed allocated cost to GEN-2018-015 associated with this model correction.
4528200% | Cost Correction | 7 | Upgrade Summary | Removed Wolforth to Terry County 115 kV Rebuild due to corrected ratings.
4528200% | Constraint Correction | 5 | Constraints Summary | Removed constraints assigned GEN-2018-015 associated with Wolforth to Terry County 115 kV Rebuild.
4528200% | LOIS Correction | 4 | Requests | Removed LOIS assigned GEN-2018-015 associated with Wolforth to Terry County 115 kV Rebuild.
4528200% | Cost Correction | 6 | Assigned Upgrade Cost | Removed Carlisle to LP-Doud_TP 115 kV Rebuild due to corrected ratings. Removed allocated cost to GEN-2018-015 associated with this model correction.
4528200% | Cost Correction | 7 | Upgrade Summary | Removed Carlisle to LP-Doud_TP 115 kV Rebuild due to corrected ratings.
4528200% | Constraint Correction | 5 | Constraints Summary | Removed constraints assigned GEN-2018-015 associated with Carlisle to LP-Doud_TP 115 kV Rebuild.
4528200% | LOIS Correction | 4 | Requests | Removed LOIS assigned GEN-2018-015 associated with Carlisle to LP-Doud_TP 115 kV Rebuild.
4528200% | Cost Correction | 6 | Assigned Upgrade Cost | Removed Summit to Watertown 115 kV Rebuild due to corrected ratings. Removed allocated costs to GEN-2018-009 and GEN-2018-039 associated with this model correction.
4528200% | Cost Correction | 7 | Upgrade Summary | Removed Summit to Watertown 115 kV Rebuild due to corrected ratings.
4528200% | Constraint Correction | 5 | Constraints Summary | Removed constraints assigned GEN-2018-009 and GEN-2018-039 associated with Summit to Watertown 115 kV Rebuild.
4528200% | Cost/Upgrade Update | 6 | Assigned Upgrade Cost | Replaced Build Atchison to GEN-2016-115 New 345 kV Line with Build New Holt to Atchison 345 kV Line due to ownership issues. Updated allocated costs for each project previously associated with Atchison to GEN-2016-115 New 345 kV Line to reflect the alternative mitigation's cost.
4528200% | Cost Update | 7 | Upgrade Summary | Replaced Build Atchison to GEN-2016-115 New 345 kV Line with Build New Holt to Atchison 345 kV Line due to ownership issues.
4528200% | Constraint Update | 5 | Constraints Summary | Updated Constraints Summary to reflect the Build New Holt to Atchison 345 kV Line.
4528200% | Cost/Upgrade Update | 6 | Assigned Upgrade Cost | Replaced Upgrade Potter 345/230 kV Transformer with Potter County 345/230 kV Circuit 1 Transformer Switch Replacement. Updated allocated costs for each project previously associated with Upgrade Potter 345/230 kV Transformer to reflect the alternative mitigation's cost.
4528200% | Cost/Upgrade Update | 7 | Upgrade Summary | Replaced Upgrade Potter 345/230 kV Transformer with Potter County 345/230 kV Circuit 1 Transformer Switch Replacement.
4528200% | LOIS Correction | 4 | Requests | The LOIS for GEN-2018-030 was adjusted due to a stability limiting element.
4528200% | Cost/Upgrade Update | 6 | Assigned Upgrade Cost | With updated network upgrades, adjustments due to costs not specifically mentioned above due to PTDF changes.

## Requests
Gen Number | Group | Queue Order | Queue | Fuel Type | MW Amount | LOIS Amount | Limiting Element | Reactive Compensation Requirements (MVAR) | Service | Area | POI | Status
ASGI-2017-013 | 01 - North | 20 | DIS-18-1 | Wind | 40 | 40 | None | -0.46 | ER | WAPA | Wolsey 69kV Substation | DISIS STAGE
GEN-2018-008 | 01 - North | 20 | DIS-18-1 | Wind | 252 | 64.05 | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | -5 | ER/NR | BEPC-SPP | Groton-Leland Olds 345kV Line | DISIS STAGE
GEN-2018-010 | 01 - North | 20 | DIS-18-1 | Storage | 74.1 | 74.1 | None | -0.06 | ER/NR | BEPC-SPP | Neset 230kV Substation | DISIS STAGE
GEN-2018-012 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 74.1 | 74.1 | None | -11.04 | ER/NR | NPPD | Antelope 345kV Substation | DISIS STAGE
GEN-2018-039 | 01 - North | 20 | DIS-18-1 | Solar | 72 | 67.63 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1 | -1.35 | ER/NR | WAPA | Edgeley 115kV substation | DISIS STAGE
GEN-2018-025 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 | 200 | None | -0.31 | ER | OPPD | Fort Calhoun 345kV Substation | DISIS STAGE
GEN-2018-033 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 200 | 200 | None | -110.5 | ER | OPPD | Cass County 345kV Substation | DISIS STAGE
GEN-2018-037 | 02 - Nebraska | 20 | DIS-18-1 | Storage | 100 | 100 | None | -0.05 | ER | OPPD | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV | DISIS STAGE
GEN-2018-043 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 500 | 500 | None | -10.68 | ER | OPPD | Ft. Calhoun - Raun 345 kV Line Break | DISIS STAGE
GEN-2018-056 | 02 - Nebraska | 20 | DIS-18-1 | Solar | 102.6 | 0 | Non-converged/Stability | -4.37 | ER/NR | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | DISIS STAGE
GEN-2018-060 | 02 - Nebraska | 20 | DIS-18-1 | Wind | 50 | 0 | Non-converged/Stability | 0 | ER/NR | NPPD | Axtell-Post Rock 345 kV | DISIS STAGE
ASGI-2018-003 | 03 - Central | 20 | DIS-18-1 | Solar | 20 | 0 | Non-converged/Stability | -0.46 | ER | KCPL | AP City 69kV Substation | DISIS STAGE
ASGI-2018-006 | 03 - Central | 20 | DIS-18-1 | Solar | 20 | 0 | Non-converged/Stability | -8.27 | ER | KCPL | Metz 69kV Substation | DISIS STAGE
ASGI-2018-007 | 03 - Central | 20 | DIS-18-1 | Solar | 20 | 0 | Non-converged/Stability | -55.1 | ER | KCPL | Salisbury 161kV Substation | DISIS STAGE
ASGI-2018-010 | 03 - Central | 20 | DIS-18-1 | Solar | 35 | 0 | Non-converged/Stability | -51.6 | ER | KCPL | Pleasant Valley 161kV Substation | DISIS STAGE
ASGI-2018-011 | 03 - Central | 20 | DIS-18-1 | Solar | 35 | 0 | Non-converged/Stability | -51.6 | ER | KCPL | South Ottawa 161kV Substation | DISIS STAGE
GEN-2018-009 | 03 - Central | 20 | DIS-18-1 | Wind | 150 | 0 | 523959 POTTER_CO 6 230 997752 WAUK 90343-A 230 1 | -12.3 | ER | SUNC | Cimarron 115kV Substation | DISIS STAGE
GEN-2018-013 | 03 - Central | 20 | DIS-18-1 | Wind | 74.1 | 74.1 | None | -2.13 | ER | WERE | Abilene Energy Center-Northview 115kV Line | DISIS STAGE
GEN-2018-022 | 03 - Central | 20 | DIS-18-1 | Solar | 300 | 0 | Non-converged/Stability | -14.27 | ER/NR | KCPL | Mullen Creek 345kV Substation | DISIS STAGE
GEN-2018-030 | 03 - Central | 20 | DIS-18-1 | Storage | 200 | 0 | GROUP3_FAULT_342 (See Stability Analysis Results Tab) | -3.37 | ER | SPS | Lamar-Finney 345kV Substation | DISIS STAGE
GEN-2018-031 | 03 - Central | 20 | DIS-18-1 | Storage | 50 | 0 | Non-converged/Stability | -23.63 | ER | KCPL | Blue Valley 161kV Substation | DISIS STAGE
GEN-2018-032 | 03 - Central | 20 | DIS-18-1 | Wind | 310 | 0 | Non-converged/Stability | -25.78 | ER | WERE | Neosho 345kV Substation | DISIS STAGE
GEN-2018-049 | 03 - Central | 20 | DIS-18-1 | Solar | 120 | 120 | None | -31.23 | ER | SUNC | Thistle 345kV Substation | DISIS STAGE
GEN-2018-054 | 03 - Central | 20 | DIS-18-1 | Solar | 120 | 0 | Non-converged/Stability | -1.9 | ER | KCPL | KC South - N. Raymore 161kV Line | DISIS STAGE
GEN-2018-057 | 03 - Central | 20 | DIS-18-1 | Solar | 203.4 | 203.4 | None | -2.85 | ER/NR | WERE | Gordon Evans 138kV | DISIS STAGE
GEN-2018-062 | 03 - Central | 20 | DIS-18-1 | Solar | 75.6 | 0 | Non-converged/Stability | -1.48 | ER/NR | KACY | Nearman 161kV substation | DISIS STAGE
GEN-2018-003 | 04 - Southeast | 20 | DIS-18-1 | Solar | 150 | 126.31 | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 (ftlo) 508054 BANN 4 138 508075 REDSPRG4 138 1 | -0.01 | ER/NR | AEPW | North Boston-Bann 138kV Line | DISIS STAGE
GEN-2018-011 | 04 - Southeast | 20 | DIS-18-1 | Storage | 74.1 | 74.1 | None | -0.62 | ER/NR | WFEC | Dover 138 kV Switching Station | DISIS STAGE
GEN-2018-021 | 04 - Southeast | 20 | DIS-18-1 | Solar | 74.1 | 74.1 | None | -3.74 | ER/NR | AEPW | Chisholm-Gracemont 345kV Line | DISIS STAGE
GEN-2018-024 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 | 100 | None | -0.19 | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | DISIS STAGE
GEN-2018-026 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 | 100 | None | -0.24 | ER | OKGE | Mustang 138kV Substation | DISIS STAGE
GEN-2018-027 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 | 11.2 | 509776 52DELTP4 138 509800 36LEWIS4 138 1 (ftlo) 509783 R.S.S.-4 138 509849 ORU ETP4 138 1 | -0.07 | ER | AEPW | Tulsa Power Station 138kV Substation | DISIS STAGE
GEN-2018-028 | 04 - Southeast | 20 | DIS-18-1 | Storage | 200 | 200 | None | -28.7 | ER | OKGE | Tulsa North 138kV Substation | DISIS STAGE
GEN-2018-029 | 04 - Southeast | 20 | DIS-18-1 | Storage | 100 | 100 | None | -16.47 | ER | OKGE | Horseshoe Lake 138kV Substation | DISIS STAGE
GEN-2018-048 | 04 - Southeast | 20 | DIS-18-1 | Solar | 300 | 300 | None | -2.5 | ER | OKGE | Pecan Creek 345kV Substation | DISIS STAGE
GEN-2018-050 | 04 - Southeast | 20 | DIS-18-1 | Solar | 200 | 200 | None | -6.26 | ER | AEPW | Longwood 345kV Substation | DISIS STAGE
GEN-2018-055 | 04 - Southeast | 20 | DIS-18-1 | Solar | 252 | 252 | None | -23.99 | ER/NR | AEPW | Terry Road 345kV station (shared with Rush Springs Windfarm on a common gentie) | DISIS STAGE
GEN-2018-004 | 05 - Southwest | 20 | DIS-18-1 | Solar | 74.99 | 74.99 | None | -132.2 | ER | SPS | T14 Circuit 115kV line | DISIS STAGE
GEN-2018-015 | 05 - Southwest | 20 | DIS-18-1 | Solar | 252 | 252 | None | -4.48 | ER/NR | SPS | Tuco-Oklaunion 345kV Line | DISIS STAGE
GEN-2018-052 | 05 - Southwest | 20 | DIS-18-1 | Storage | 70 | 70 | None | -1.12 | ER | SPS | Roadrunner 115kV Substation | DISIS STAGE
J1040 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER/NR | MDU | Wishek Junction 230 kV Substation | IA PENDING
J1045 | 01 - North | 19.5 | DIS-18-1-PQ | Storage | 20 |  |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line Tap | IA PENDING
J1072 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | XEL | Adams 345 kV Substation | IA PENDING
J1092 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Three Lakes 115 kV Substation | IA PENDING
J1124 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Byron 345kV Substation | IA PENDING
J1164 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER | ALTW | Magnolia 161 kV Substation | IA PENDING
J1169 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | XEL | Grant 115 kV Substation | IA PENDING
J1181 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER | ALTW | Hazleton - Mitchell county 345 kV line | IA PENDING
J1221 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | GRE | Wing River- Riverton 230kV line | IA PENDING
J1312 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | XEL | Grant 115 kV Substation | IA PENDING
J1314 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | DPC | Apple River 161 kV Substation | IA PENDING
J1325 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | ALTW | Magnolia 161 kV substation | IA PENDING
J1426 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Benton County 115kV Substation | IA PENDING
J1445 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Mayhew Lake 115kV Substation | IA PENDING
J1474 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  |  | ER/NR | XEL | Pine Lake - Eagle Point 115kV Line | IA PENDING
J1485 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER | OTP | Astoria 345 kV Substation (J493/J510) | IA PENDING
J1503 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Huntley 345 kV | Not Started
J1504 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Huntley 345 kV | Not Started
J1534 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | XEL | Byron 345kV | Not Started
J1566 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | ALTW | Rutland Substation 161kV | Not Started
J1572 | 01 - North | 19.5 | DIS-18-1-PQ | Solar/Storage | 150 |  |  |  | ER/NR | XEL | Huntley to Blue Earth 161kV | Not Started
J1575 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 70 |  |  |  | ER/NR | OTP | 115 kV transmission line from Warsaw to Donaldson owned by Otter Tail Power Company | Not Started
J1581 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | XEL | Nobles County 345 kV Substation | Not Started
J1588 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | XEL | Bison 345kV | Not Started
J1605 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | XEL | Sherburne 345kV | Not Started
J1611 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 120 |  |  |  | ER/NR | XEL | Langola 115kV Tap | Not Started
J1620 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER | XEL | Pipestone to Split Rock 115kV | Not Started
J1657 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER | XEL | Pine Lake to Apple River 161 kV | Not Started
J1730 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | XEL | Eau Claire to AS King 345 kV | Not Started
J1769 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 80 |  |  |  | ER | DPC | Beaver Creek to Rice 161 kV line tap (same POI as J898) | Not Started
J1808 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 148 |  |  |  | ER | DPC | Barron 161 kV | Not Started
J1826 | 01 - North | 19.5 | DIS-18-1-PQ | Hydro | 4 |  |  |  | ER | XEL | Cannon Falls Transmission 69 kV | Not Started
J967 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 150 |  |  |  | ER | XEL | Adams 345kV Substation | IA PENDING
IR39 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 151.88 |  |  |  | ER/NR | ALTW | Dundee 161 kV Substation
MPC03600 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03700 | 01 - North | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | OTP | Frontier-Wahpeton 230 kV Line | IA PENDING
MPC03800 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 250 |  |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC03900 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 151.2 |  |  |  | ER/NR | OTP | Center-Prairie 345 kV Line
MPC04000 | 01 - North | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  |  | ER/NR | OTP | Square Butte 230 kV Substation
J1050 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 225 |  |  |  | ER/NR | ALTW | Doud Tap 161 kV Substation | IA PENDING
J1132 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | ALTW | Creston East 69 kV Substation | IA PENDING
J1174 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV Line Tap | IA PENDING
J1175 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 165 |  |  |  | ER | ALTW | Ledyard - Colby 345kV Line Tap | IA PENDING
J1270 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER | MEC | Kossuth - O'Brien 345 kV Line Tap | IA PENDING
J1313 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | ALTW | 161kV bus at Karma substation | IA PENDING
J1359 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Combustion Turbine | 95 |  |  |  | ER/NR | ALTW | Oakridge 69 kV Substation | IA PENDING
J1365 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 169.4 |  |  |  | ER | ALTW | Traer 161-kV Substation | IA PENDING
J1444 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | ALTW | Duane Arnold 345kV Substation | IA PENDING
J1520 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | ALTW | Ledyard - Colby 345 kV | Not Started
J1529 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | MEC | Tap Carroll (635320) - Auburn (635328) 69 kV line at about midpoint | Not Started
J1530 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | MEC | Tap Hastings (635033) - Macedonia (635069) 69 kV line at about midpoint | Not Started
J1532 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | MEC | Clarinda-Coburg 69 kV | Not Started
J1590 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 200 |  |  |  | ER/NR | MEC | O'Brien - Raun 345 kV | Not Started
J982 | 02 - Nebraska | 19.5 | DIS-18-1-PQ | Wind | 300 |  |  |  | ER | MEC | Obrien County - Kossuth 345 kV Line Tap | IA PENDING
GIA-96 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 101.32 |  |  |  | ER | AECI | Stroud 138kV | IA PENDING
J1025 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 290 |  |  |  | ER/NR | AMMO | Zachary - Maywood 345 kV Line Tap | IA PENDING
J1026 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 380 |  |  |  | ER/NR | AMMO | Maywood - Spencer Creek 345 kV Line Tap | IA PENDING
J1145 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | AMMO | Overton - (McCrede) - Montgomery 345 kV Line Tap | IA PENDING
J1182 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | AMMO | Zachary Substation 345 kV Bus | IA PENDING
J1191 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 64 |  |  |  | ER/NR | CWLD | Bolstad 69 kV Substation | IA PENDING
J1202 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar/Storage | 68 |  |  |  | ER/NR | AMIL | Baldwin Plant 345kV Switchyard - Baldwin Unit 2 | IA PENDING
J1208 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1209 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 80 |  |  |  | ER/NR | AMIL | Muddy - Crab Orchard 138kV Line | IA PENDING
J1213 | 03 - Central | 19.5 | DIS-18-1-PQ | Hydro | 60 |  |  |  | ER/NR | AMMO | Taum Sauk 138kV Switchyard, Bus 1 & 2 | IA PENDING
J1216 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 185 |  |  |  | ER/NR | AMIL | Ashley 138 kV Substation | IA PENDING
J1241 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER/NR | AMIL | West Mt Vernon - Xenia 345kV Line | IA PENDING
J1268 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | AMMO | Pike - Troy 161kV Line | IA PENDING
J1303 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  |  | ER/NR | SIPC | Campbell Hill - Jackson 161kV Line | IA PENDING
J1306 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMIL | Commodore-Jordan 345kV Line | IA PENDING
J1311 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | AMIL | Fayetteville Bee Hollow Road 138 kV Substation | IA PENDING
J1352 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Spencer Creek - Montgomery 345kV Line | IA PENDING
J1488 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 500 |  |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J1490 | 03 - Central | 19.5 | DIS-18-1-PQ | Wind | 1000 |  |  |  | ER/NR | AMMO | McCredie - Montgomery 345 kV Line Tap | IA PENDING
J956 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Spencer Creek 345kV Substation | IA PENDING
J976 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | AMMO | Montgomery - Enon 345kV Line Tap | IA PENDING
J987 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Montgomery 161kV Substation | IA PENDING
J994 | 03 - Central | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | AMMO | Guthrie 161 kV Substation | IA PENDING
J1007 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 180 |  |  |  | ER/NR | EES-EAI | Marion - Marked Tree 161 kV | IA PENDING
J1030 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | EES | Poco - Menard 138 kV | IA PENDING
J1034 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 225 |  |  |  | ER/NR | AMMO | Stoddard - Morley 161kV Line Tap | IA PENDING
J1060 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 450 |  |  |  | ER/NR | EES-EAI | West Memphis - Keo 500 kV | IA PENDING
J1087 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Miner - Kelso 161 kV Line Tap | IA PENDING
J1107 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | AMMO | Kelso - Lutesville 345 kV Line Tap | IA PENDING
J1125 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | EES-EAI | Wynne South - Wynne East AECC 161 kV | IA PENDING
J1155 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | EES-EAI | Driver 230 kV | IA PENDING
J1205 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER | CLEC | Centennial - West Bay 138 kV | IA PENDING
J1215 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 155 |  |  |  | ER/NR | EES-EAI | Stuttgart Ricuskey - Woodward 230 kV | IA PENDING
J1231 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 125 |  |  |  | ER/NR | BREC | Barkley - Caldwell 161kV Line | IA PENDING
J1239 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER | EES | Rilla 115 kV | IA PENDING
J1258 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 50 |  |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1281 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 75 |  |  |  | ER/NR | EES-EAI | Crossett - Monticello East 115 kV | IA PENDING
J1299 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 149 |  |  |  | ER/NR | AMMO | Miner - Kelso 161kV Line | IA PENDING
J1373 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 95 |  |  |  | ER/NR | EES-EAI | Griffithville - Searcy Price 115 kV Line Tap | IA PENDING
J1402 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 0 |  |  |  | ER/NR | EES-EAI | Cash - Newport AB161kV Line | IA PENDING
J1415 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 250 |  |  |  | ER/NR | EES-EAI | KEO EHV 500 kV Substation | IA PENDING
J1424 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER | CLEC | Cooper - Penton Road 230 kV | IA PENDING
J1434 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | J907 230kV Sub, Brinkley East - Aubrey 230 kV Line | IA PENDING
J1436 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER | EES | Oak Ridge 115 kV | IA PENDING
J1437 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 180 |  |  |  | ER/NR | EES-EAI | AECC Dry Creek 161 kV | IA PENDING
J1442 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 105 |  |  |  | ER | EES | Rich (SHECO) - Livingston 138 kV | IA PENDING
J1509 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EMI | Greenwood - Pickens 115 kV | Not Started
J1514 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | Driver 230kV | Not Started
J1558 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | EES-EAI | Moreland - St. Vincent 161kV line | Not Started
J1559 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | EES-EAI | Morrilton East Substation (161kV bus) | Not Started
J1562 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | EES-EAI | Blytheville I-55 to AECC Blytheville North 161kV | Not Started
J1577 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | Hardin West SS to Sheridan 115 kV | Not Started
J1598 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 325.02 |  |  |  | ER | EES | Solac - Chalkley 230kV | Not Started
J1602 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 25 |  |  |  | ER/NR | EES | Rilla 115kV substation (Same as J1239) | Not Started
J1612 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | El Dorado East - Sterlington 115 kV | Not Started
J1669 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 165 |  |  |  | ER | EES | LC Bulk to Henning 138kV Line (Circuit 28) | Not Started
J1670 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | EES-EAI | Crooked Lake 161kV at J586 POI | Not Started
J1671 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER | EES | Rocky Creek to Lewis Creek 230kV | Not Started
J1672 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 150 |  |  |  | ER/NR | EES-EMI | Tinnin Road 230kV | Not Started
J1673 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 200 |  |  |  | ER/NR | CLEC | Fisher to Mansfield Compressor 230 kV | Not Started
J1709 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 100 |  |  |  | ER | EES | 138 kV Grimes | Not Started
J1710 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 300 |  |  |  | ER/NR | EES-EAI | Entergy Keo-Memphis 500kV Line Tap | Not Started
J1723 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Storage | 10 |  |  |  | ER/NR | EES-EAI | Wynne East to Wynne South 161kV line (J1125 sub) | Not Started
J1747 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 50 |  |  |  | ER/NR | EES-EMI | J830 POI | Not Started
J1748 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EMI | Twinkletown 230 kV | Not Started
J1760 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 205 |  |  |  | ER/NR | EES | Timberland 230kV | Not Started
J1816 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 135 |  |  |  | ER/NR | EES-EAI | Fisher (Endpoint A) to Cherry Valley (Endpoint B) 161 kV line | Not Started
J1820 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 100 |  |  |  | ER/NR | EES-EAI | Entergy Keo-West Memphis 500kV Line Tap | Not Started
J1827 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Solar | 90 |  |  |  | ER/NR | EES | Bastrop tap point | Not Started
J1834 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Combustion Turbine | 126 |  |  |  | ER/NR | EES | Sabine 138/230 kV Substation | Not Started
J1842 | 04 - Southeast | 19.5 | DIS-18-1-PQ | Wind | 135 |  |  |  | ER | EES-EAI | Forrest City to Wynne S 161 KV | Not Started
GEN-2017-175 | 01 - North | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER | WAPA | Vfodnes-Utica Jct. 230kV | DISIS STAGE
GEN-2017-214 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-215 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-216 | 01 - North | 19 | DIS-17-2 | Wind | 100 |  |  |  | ER/NR | BEPC-SPP | Logan 230kV Substation | DISIS STAGE
GEN-2017-222 | 01 - North | 19 | DIS-17-2 | Wind | 180 |  |  |  | ER | WAPA | Denison 230kV Substation | DISIS STAGE
GEN-2017-105 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 75 |  |  |  | ER/NR | OPPD | Tekamah - Raun 161 kV Line | DISIS STAGE
GEN-2017-144 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER | WAPA | Holt County 345kV | DISIS STAGE
GEN-2017-181 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-182 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 128 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | DISIS STAGE
GEN-2017-198 | 02 - Nebraska | 19 | DIS-17-2 | Storage | 11.64 |  |  |  | ER | OPPD | Jones St. No 1201 69kV substation | DISIS STAGE
GEN-2017-201 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 250 |  |  |  | ER/NR | NPPD | Hoskins 345kV Substation | DISIS STAGE
GEN-2017-210 | 02 - Nebraska | 19 | DIS-17-2 | Solar/Storage | 310 |  |  |  | ER | NPPD | McCool 345kV Substation | DISIS STAGE
GEN-2017-234 | 02 - Nebraska | 19 | DIS-17-2 | Wind | 115 |  |  |  | ER | NPPD | Spalding to North Loup 115kV | DISIS STAGE
GEN-2017-108 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  |  | ER/NR | KCPL | Stillwell - Clinton 161kV Line | DISIS STAGE
GEN-2017-111 | 03 - Central | 19 | DIS-17-2 | Solar | 152 |  |  |  | ER | KCPL | Clinton â€“ Stilwell 161 kV Line Tap | DISIS STAGE
GEN-2017-115 | 03 - Central | 19 | DIS-17-2 | Wind | 244 |  |  |  | ER | KCPL | Holt County 345 kV | DISIS STAGE
GEN-2017-119 | 03 - Central | 19 | DIS-17-2 | Wind | 180 |  |  |  | ER | SUNC | Elm Creek 345kV substation | DISIS STAGE
GEN-2017-120 | 03 - Central | 19 | DIS-17-2 | Wind | 260 |  |  |  | ER | WERE | Abilene Energy Center-Northview 115kV | DISIS STAGE
GEN-2017-121 | 03 - Central | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER/NR | WERE | Sumner 138kV | DISIS STAGE
GEN-2017-125 | 03 - Central | 19 | DIS-17-2 | Wind | 252 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-128 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-131 | 03 - Central | 19 | DIS-17-2 | Storage | 29.6 |  |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | DISIS STAGE
GEN-2017-148 | 03 - Central | 19 | DIS-17-2 | Wind | 202 |  |  |  | ER/NR | EMDE | Joplin 161kV sub | DISIS STAGE
GEN-2017-179 | 03 - Central | 19 | DIS-17-2 | Wind | 222 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-183 | 03 - Central | 19 | DIS-17-2 | Wind | 400 |  |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-184 | 03 - Central | 19 | DIS-17-2 | Solar | 400 |  |  |  | ER/NR | KCPL | Nashua-St. Joe 345kV | DISIS STAGE
GEN-2017-188 | 03 - Central | 19 | DIS-17-2 | Solar | 130 |  |  |  | ER | EMDE | Asbury 161 kV | DISIS STAGE
GEN-2017-191 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-192 | 03 - Central | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | WERE | Swissvale 345kV | DISIS STAGE
GEN-2017-195 | 03 - Central | 19 | DIS-17-2 | Solar | 500.4 |  |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-196 | 03 - Central | 19 | DIS-17-2 | Storage | 128 |  |  |  | ER/NR | KCPL | West Gardner 345kV | DISIS STAGE
GEN-2017-202 | 03 - Central | 19 | DIS-17-2 | Solar | 200 |  |  |  | ER/NR | SWPA | New Madrid - Sikeston 161kV | DISIS STAGE
GEN-2017-209 | 03 - Central | 19 | DIS-17-2 | Solar/Storage | 300 |  |  |  | ER | KCPL | LaCygne - Neosho 345kV | DISIS STAGE
GEN-2017-220 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-221 | 03 - Central | 19 | DIS-17-2 | Storage | 152 |  |  |  | ER/NR | WERE | Buffalo Flats 345kV Substation | DISIS STAGE
GEN-2017-226 | 03 - Central | 19 | DIS-17-2 | Solar | 201.6 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-227 | 03 - Central | 19 | DIS-17-2 | Storage | 201.6 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | DISIS STAGE
GEN-2017-229 | 03 - Central | 19 | DIS-17-2 | Storage | 76 |  |  |  | ER/NR | KCPL | Stilwell 345kV Substation | DISIS STAGE
GEN-2017-117 | 04 - Southeast | 19 | DIS-17-2 | Storage | 19.8 |  |  |  | ER/NR | WFEC | El Reno SW 138kV | DISIS STAGE
GEN-2017-132 | 04 - Southeast | 19 | DIS-17-2 | Wind | 400 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-133 | 04 - Southeast | 19 | DIS-17-2 | Wind | 200 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-134 | 04 - Southeast | 19 | DIS-17-2 | Wind | 250 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-137 | 04 - Southeast | 19 | DIS-17-2 | Wind | 295 |  |  |  | ER/NR | OKGE | Arcadia 345kV | DISIS STAGE
GEN-2017-140 | 04 - Southeast | 19 | DIS-17-2 | Solar | 160 |  |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-141 | 04 - Southeast | 19 | DIS-17-2 | Solar | 241.7 |  |  |  | ER/NR | AEPW | Clarksville 345kV Switching Station | DISIS STAGE
GEN-2017-149 | 04 - Southeast | 19 | DIS-17-2 | Wind | 258 |  |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-150 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-152 | 04 - Southeast | 19 | DIS-17-2 | Wind | 252 |  |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-154 | 04 - Southeast | 19 | DIS-17-2 | Wind | 255 |  |  |  | ER/NR | OKGE | Johnson County 345kV Substation | DISIS STAGE
GEN-2017-155 | 04 - Southeast | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER/NR | OKGE | Muskogee 345kV Substation | DISIS STAGE
GEN-2017-164 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-166 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-167 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | OKGE | Sunnyside 345kV | DISIS STAGE
GEN-2017-168 | 04 - Southeast | 19 | DIS-17-2 | Solar | 250 |  |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-169 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | OKGE | McClain 138kV | DISIS STAGE
GEN-2017-171 | 04 - Southeast | 19 | DIS-17-2 | Solar | 150 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-172 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-173 | 04 - Southeast | 19 | DIS-17-2 | Solar | 50 |  |  |  | ER/NR | AEPW | Lawton Eastside - Terry Road 345kV | DISIS STAGE
GEN-2017-178 | 04 - Southeast | 19 | DIS-17-2 | Storage | 52 |  |  |  | ER/NR | OKGE | Woodring 345kV Substation | DISIS STAGE
GEN-2017-203 | 04 - Southeast | 19 | DIS-17-2 | Solar/Storage | 210 |  |  |  | ER | OKGE | Renfrow 345kV Substation | DISIS STAGE
GEN-2017-230 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  |  | ER/NR | OKGE | Tryon 138kV Substation | DISIS STAGE
GEN-2017-231 | 04 - Southeast | 19 | DIS-17-2 | Solar | 72.5 |  |  |  | ER/NR | OKGE | Branch 161kV Substation | DISIS STAGE
GEN-2017-232 | 04 - Southeast | 19 | DIS-17-2 | Solar | 52.2 |  |  |  | ER/NR | OKGE | Brown 138kV Substation | DISIS STAGE
GEN-2017-233 | 04 - Southeast | 19 | DIS-17-2 | Wind | 215 |  |  |  | ER/NR | OKGE | Minco 345kV | DISIS STAGE
GEN-2017-240 | 04 - Southeast | 19 | DIS-17-2 | Solar | 202 |  |  |  | ER/NR | OKGE | Bristow 138kV Substation | DISIS STAGE
GEN-2017-146 | 05 - Southwest | 19 | DIS-17-2 | Wind | 151.8 |  |  |  | ER | SPS | Deaf Smith-Plant X 230kV | DISIS STAGE
GEN-2017-151 | 05 - Southwest | 19 | DIS-17-2 | Wind | 300 |  |  |  | ER | SPS | Tuco-Oklaunion 345kV Line | DISIS STAGE
GEN-2017-158 | 05 - Southwest | 19 | DIS-17-2 | Wind | 265 |  |  |  | ER | SPS | Tolk 230kV Substation | DISIS STAGE
GEN-2017-187 | 05 - Southwest | 19 | DIS-17-2 | Solar | 150 |  |  |  | ER | SPS | Sulphur Springs 115kV Substation | DISIS STAGE
GEN-2017-239 | 05 - Southwest | 19 | DIS-17-2 | Solar | 300 |  |  |  | ER | SPS | Mahoney 230kV Substation | DISIS STAGE
J545 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 110 |  |  |  | ER | XEL | Buffalo 115kV Substation
J722 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  |  | ER | OTP | Big Stone South 230kV Substation
J801 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 74 |  |  |  | ER | DPC | Crystal Cave-Rock Elm 161kV line tap | DISIS STAGE
J874 | 01 - North | 18.5 | DIS-17-2-PQ | Solar | 150 |  |  |  | ER/NR | XEL | Fenton - Chanarambie 115kV Line | DISIS STAGE
J897 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 190 |  |  |  | ER | GRE | Prairie - Ramsey 230 kV line
J898 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 100 |  |  |  | ER | DPC | Rice - Beaver Creek 161kV line tap
J926 | 01 - North | 18.5 | DIS-17-2-PQ | Wind | 101.28 |  |  |  | ER | XEL | Pine Lake - Apple River 161 kV Line
IR24 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  |  | ER/NR | ALTW | New 69kV substation near Prescott REC
IR32 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 56 |  |  |  | ER/NR | ALTW | Murray Junction 69 kV substation
J836 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Wind | 200 |  |  |  | ER | ALTW | Ledyard 345kV Substation
J877 | 02 - Nebraska | 18.5 | DIS-17-2-PQ | Solar | 250 |  |  |  | ER/NR | MEC | Obrien - Kossuth 345kV Line (J529 & J590 New Substation) | DISIS STAGE
GIA-83 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 1031 |  |  |  | ER/NR | AECI | McCredie 345 kV
GIA-86 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 103.68 |  |  |  | ER/NR | AECI | Thomas Hill 69 kV
GIA-90 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 108 |  |  |  | ER/NR | AECI | Montgomery City 161 kV
GIA-91 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 104.4 |  |  |  | ER/NR | AECI | Sedalia 69 kV
GIA-93 | 03 - Central | 18.5 | DIS-17-2-PQ | Solar | 100 |  |  |  | ER/NR | AECI | Palmyra 161 kV
GIA-95 | 03 - Central | 18.5 | DIS-17-2-PQ | Wind | 252 |  |  |  | ER/NR | AECI | Jasper-Morgan 345 kV
GEN-2017-010 | 01 - North | 18 | DIS-17-1 | Wind | 200.1 |  |  |  | ER | WAPA | Rhame 230 kV Sub | FACILITY STUDY STAGE
GEN-2017-014 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | WAPA | Philip Tap 230 kV | FACILITY STUDY STAGE
GEN-2017-048 | 01 - North | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | BEPC-SPP | Neset 230 kV Substation | FACILITY STUDY STAGE
GEN-2017-094 | 01 - North | 18 | DIS-17-1 | Wind | 200 |  |  |  | ER | WAPA | Fort Thompson-Huron 230 kV | FACILITY STUDY STAGE
GEN-2017-097 | 01 - North | 18 | DIS-17-1 | Solar | 128 |  |  |  | ER | WAPA | Underwood 115 kV Sub | FACILITY STUDY STAGE
GEN-2017-004 | 03 - Central | 18 | DIS-17-1 | Wind | 201.6 |  |  |  | ER | SUNC | Elm Creek - Summit 345 kV | FACILITY STUDY STAGE
GEN-2017-005 | 03 - Central | 18 | DIS-17-1 | Wind | 190 |  |  |  | ER | WERE | Marmaton - Litchfield 161 kV | FACILITY STUDY STAGE
GEN-2017-018 | 03 - Central | 18 | DIS-17-1 | Solar | 189 |  |  |  | ER/NR | SUNC | Thistle 345 kV sub | FACILITY STUDY STAGE
GEN-2017-022 | 03 - Central | 18 | DIS-17-1 | Solar | 65 |  |  |  | ER/NR | WERE | Altoona- NE Parson 138kV | FACILITY STUDY STAGE
GEN-2017-068 | 03 - Central | 18 | DIS-17-1 | Solar | 103.5 |  |  |  | ER/NR | WERE | Gordon Evans 138kV Substation | FACILITY STUDY STAGE
GEN-2017-086 | 03 - Central | 18 | DIS-17-1 | Wind | 150 |  |  |  | ER | WERE | Viola 345kV | FACILITY STUDY STAGE
GEN-2016-037 | 04 - Southeast | 18 | DIS-17-1 | Wind | 300 |  |  |  | ER | AEPW | Chisholm-Gracemont 345kV Line | FACILITY STUDY STAGE
GEN-2017-011 | 04 - Southeast | 18 | DIS-17-1 | Solar | 151.8 |  |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | FACILITY STUDY STAGE
GEN-2017-023 | 04 - Southeast | 18 | DIS-17-1 | Solar | 85 |  |  |  | ER/NR | WFEC | Hugo Power Plant 138 kV Sub | FACILITY STUDY STAGE
GEN-2017-027 | 04 - Southeast | 18 | DIS-17-1 | Wind | 140 |  |  |  | ER | OKGE | Pooleville-Ratliff (Carter County) 138kV | FACILITY STUDY STAGE
GEN-2017-036 | 04 - Southeast | 18 | DIS-17-1 | Solar | 100 |  |  |  | ER | WFEC | Snyder - Cache 138 kV | FACILITY STUDY STAGE
GEN-2017-040 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200.1 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-057 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | AEPW | Hosston 69kV | FACILITY STUDY STAGE
GEN-2017-061 | 04 - Southeast | 18 | DIS-17-1 | Solar | 101.5 |  |  |  | ER/NR | GRDA | GRDA1 to CLARMR 5 161kV line | FACILITY STUDY STAGE
GEN-2017-071 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-072 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  |  | ER | OKGE | Greenwood 138kV sub | FACILITY STUDY STAGE
GEN-2017-073 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | GRDA | Dry Gulch 161kV sub | FACILITY STUDY STAGE
GEN-2017-074 | 04 - Southeast | 18 | DIS-17-1 | Solar | 72.5 |  |  |  | ER | AEPW | Pryor Junction 138kV sub | FACILITY STUDY STAGE
GEN-2017-075 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  |  | ER | OKGE | Hugo-Sunnyside 345 kV | FACILITY STUDY STAGE
GEN-2017-076 | 04 - Southeast | 18 | DIS-17-1 | Solar | 52.2 |  |  |  | ER | AEPW | Chamber Springs 161kV sub | FACILITY STUDY STAGE
GEN-2017-077 | 04 - Southeast | 18 | DIS-17-1 | Solar | 124.7 |  |  |  | ER | AEPW | Explorer Claremore Tap EXCLART4 | FACILITY STUDY STAGE
GEN-2017-092 | 04 - Southeast | 18 | DIS-17-1 | Solar | 200 |  |  |  | ER | OKGE | Canadian River-Muskogee and Muskogee-Seminole 345kV | FACILITY STUDY STAGE
GEN-2017-033 | 05 - Southwest | 18 | DIS-17-1 | Wind | 200 |  |  |  | ER/NR | AEPW | Oklaunion 345 kV sub | FACILITY STUDY STAGE
GEN-2017-047 | 05 - Southwest | 18 | DIS-17-1 | Wind | 102 |  |  |  | ER/NR | SPS | Cole 115kV | FACILITY STUDY STAGE
GEN-2017-100 | 05 - Southwest | 18 | DIS-17-1 | Solar | 102.6 |  |  |  | ER/NR | SPS | Texas County 115kV | FACILITY STUDY STAGE
BEPCNDPW1 | 01 - North | 17.5 | DIS-17-1-PQ | Wind | 5 |  |  |  | ER | BEPC-SPP | NELSON 7
GEN-2016-036 | 01 - North | 17 | DIS-16-2 | Wind | 44.6 |  |  |  | ER | WAPA | Granite Falls 115kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-087 | 01 - North | 17 | DIS-16-2 | Wind | 98.9 |  |  |  | ER | WAPA | Bismark-Glenham 230 kV line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-094 | 01 - North | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER | WAPA | Tap Ft Thompson - Oahe 230kV Line (Single Circuit) | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-130 | 01 - North | 17 | DIS-16-2 | Wind | 202 |  |  |  | ER | WAPA | Leland Olds 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-074 | 02 - Nebraska | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER | NPPD | Sweetwater 345kV | IA PENDING
GEN-2016-147 | 02 - Nebraska | 17 | DIS-16-2 | Solar | 40 |  |  |  | ER | NPPD | Sidney 115 kV Sub | IA PENDING
GEN-2016-111 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Reno - Summit 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-115 | 03 - Central | 17 | DIS-16-2 | Wind | 300 |  |  |  | ER | KCPL | Nebraska City-Mullen Creek (Holt County MO) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-149 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-150 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-153 | 03 - Central | 17 | DIS-16-2 | Wind | 134 |  |  |  | ER | WERE | Viola 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-157 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-158 | 03 - Central | 17 | DIS-16-2 | Wind | 252 |  |  |  | ER | KCPL | West Gardner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-160 | 03 - Central | 17 | DIS-16-2 | Storage | 20 |  |  |  | ER/NR | MIDW | Post Rock 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-174 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-176 | 03 - Central | 17 | DIS-16-2 | Wind | 302 |  |  |  | ER | WERE | Stranger Creek 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-091 | 04 - Southeast | 17 | DIS-16-2 | Wind | 303.6 |  |  |  | ER | AEPW | Gracemont-Lawton East Side 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-095 | 04 - Southeast | 17 | DIS-16-2 | Wind | 200 |  |  |  | ER/NR | AEPW | Gracemont-Lawton East Side 345kV | IA PENDING
GEN-2016-097 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  |  | ER/NR | AEPW | Tap Southwestern-Fletcher Tap 138kV | IA PENDING
GEN-2016-102 | 04 - Southeast | 17 | DIS-16-2 | Wind | 150.9 |  |  |  | ER/NR | OKGE | Blue River 138kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-118 | 04 - Southeast | 17 | DIS-16-2 | Wind | 288 |  |  |  | ER | WFEC | Dover Switchyard 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-119 | 04 - Southeast | 17 | DIS-16-2 | Wind | 600 |  |  |  | ER | OKGE | Spring Creek-Sooner 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-126 | 04 - Southeast | 17 | DIS-16-2 | Wind | 172.5 |  |  |  | ER/NR | OKGE | Arbuckle 138kV substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-128 | 04 - Southeast | 17 | DIS-16-2 | Wind | 176 |  |  |  | ER | OKGE | Woodring 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-131 | 04 - Southeast | 17 | DIS-16-2 | Wind | 2.5 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-132 | 04 - Southeast | 17 | DIS-16-2 | Wind | 6.12 |  |  |  | ER | AEPW | Sweetwater 230kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-133 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-134 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-137 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-138 | 04 - Southeast | 17 | DIS-16-2 | Wind | 187.5 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-139 | 04 - Southeast | 17 | DIS-16-2 | Wind | 100 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-141 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-142 | 04 - Southeast | 17 | DIS-16-2 | Wind | 350 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-145 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-146 | 04 - Southeast | 17 | DIS-16-2 | Wind | 175 |  |  |  | ER | AEPW | Riverside 345kV Substation | IA PENDING
GEN-2016-167 | 04 - Southeast | 17 | DIS-16-2 | Solar | 73.5 |  |  |  | ER/NR | AEPW | Lieberman - North Benton 138 kV Line | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2016-010 | 05 - Southwest | 17 | DIS-16-2 | Wind | 90 |  |  |  | ER | SPS | TEXAS_CNTY 3
GEN-2016-121 | 05 - Southwest | 17 | DIS-16-2 | Solar | 110 |  |  |  | ER | SPS | Roadrunner 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-177 | 05 - Southwest | 17 | DIS-16-2 | Combustion Turbine | 17 |  |  |  | ER | SPS | XTO-Cornell 115 kV station | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2017-006GIA-53 | 03 - Central | 16.5 | DIS-16-2-PQ | Wind | 238 |  |  |  | ER/NR | AECI | 5MARYVL
GEN-2016-004 | 01 - North | 16 | DIS-16-1 | Wind | 202 |  |  |  | ER/NR | WAPA | Basin Electric 230 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-007 | 01 - North | 16 | DIS-16-1 | Wind | 100.05 |  |  |  | ER | WAPA | Valley City 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-021 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 300 |  |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-043 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 230 |  |  |  | ER | NPPD | Hoskins 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-050 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 250.7 |  |  |  | ER | NPPD | Axtell-Post Rock 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-075 | 02 - Nebraska | 16 | DIS-16-1 | Wind | 50 |  |  |  | ER | WAPA | Fort Thompson-Grand Island (Grand Prairie) 345kV | IA PENDING
GEN-2016-009 | 03 - Central | 16 | DIS-16-1 | Combustion Turbine | 29 |  |  |  | ER | OKGE | Osage 69 kV Sub | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-016 | 03 - Central | 16 | DIS-16-1 | Wind | 78.2 |  |  |  | ER | MIDW | North Kinsley 115 kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2016-046 | 03 - Central | 16 | DIS-16-1 | Wind | 299 |  |  |  | ER | SUNC | Clark County-Ironwood 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-073 | 03 - Central | 16 | DIS-16-1 | Wind | 220 |  |  |  | ER | WERE | Thistle-Wichita Dbl Ckt (Buffalo Flats) 345kV | IA FULLY EXECUTED/ON SUSPENSION
GEN-2015-036 | 04 - Southeast | 16 | DIS-16-1 | Wind | 303.6 |  |  |  | ER | OKGE | Johnston County 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-095 | 04 - Southeast | 16 | DIS-16-1 | Wind | 176 |  |  |  | ER | WFEC | Tap Mooreland - Knob Hill 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-003 | 04 - Southeast | 16 | DIS-16-1 | Wind | 248.4 |  |  |  | ER | OKGE | Badger-Woodward EHV Dbl Ckt 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-020 | 04 - Southeast | 16 | DIS-16-1 | Wind | 150 |  |  |  | ER | WFEC | Moreland 138kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-030 | 04 - Southeast | 16 | DIS-16-1 | Solar | 100 |  |  |  | ER/NR | OKGE | Brown 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-031 | 04 - Southeast | 16 | DIS-16-1 | Wind | 1.5 |  |  |  | ER | OKGE | Rose Hill (Open Sky)-Sooner (Ranch Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-032 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER/NR | OKGE | Crescent Substation 138 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-045 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-051 | 04 - Southeast | 16 | DIS-16-1 | Wind | 9.8 |  |  |  | ER | AEPW | Clinton Junction-Weatherford Southeast 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-057 | 04 - Southeast | 16 | DIS-16-1 | Wind | 499.1 |  |  |  | ER | OKGE | Mathewson 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-061 | 04 - Southeast | 16 | DIS-16-1 | Wind | 250.7 |  |  |  | ER | OKGE | Sooner-Woodring 345 kV line | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-063 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER/NR | OKGE | Hugo-Sunnyside 345 kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2016-071 | 04 - Southeast | 16 | DIS-16-1 | Wind | 200.1 |  |  |  | ER | OKGE | Middleton Tap 138kV Substation | IA FULLY EXECUTED/ON SUSPENSION
PQOKGEMustang | 04 - Southeast | 16 | DIS-16-1 | Combustion Turbine | 287 |  |  |  | ER | OKGE | MUSTANG4
ASGI-2016-004 | 05 - Southwest | 16 | DIS-16-1 | Wind | 10 |  |  |  | ER | SPS | Palo Duro 115kV
GEN-2015-082 | 05 - Southwest | 16 | DIS-16-1 | Wind | 200 |  |  |  | ER | OKGE | Beaver County - Woodward EHV Dbl Ckt (Badger) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2016-070 | 05 - Southwest | 16 | DIS-16-1 | Wind | 5.3 |  |  |  | ER | SPS | Martin 115 kV Substation | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-088 | 02 - Nebraska | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER/NR | NPPD | Tobias 345kV Substation | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-052 | 03 - Central | 15 | DIS-15-2 | Wind | 300 |  |  |  | ER | WERE | Open Sky-Rose Hill 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-045 | 04 - Southeast | 15 | DIS-15-2 | Storage | 20 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-048 | 04 - Southeast | 15 | DIS-15-2 | Wind | 200 |  |  |  | ER | OKGE | Cleo Corner 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-062 | 04 - Southeast | 15 | DIS-15-2 | Wind | 4.5 |  |  |  | ER | OKGE | Breckinridge 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-066 | 04 - Southeast | 15 | DIS-15-2 | Wind | 248.4 |  |  |  | ER | OKGE | Sooner - Cleveland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-092 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2015-093 | 04 - Southeast | 15 | DIS-15-2 | Wind | 250 |  |  |  | ER | OKGE | Gracemont 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2002-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 40.5 |  |  |  | ER/NR | BEPC-SPP | Edgeley 115kV [Pomona 115kV]
GEN-2006-006IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 10 |  |  |  | ER/NR | XEL | Marshall 115kV
GEN-2007-020IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 16 |  |  |  | ER/NR | BEPC-SPP | Nelson 115kV
GEN-2008-008IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 5 |  |  |  | ER/NR | WAPA | Nelson 115kV
GEN-2010-003IS | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 34 |  |  |  | ER/NR | BEPC-SPP | Wessington Springs 230kV
MPC02100 | 01 - North | 14.5 | DIS-15-2-PQ | Wind | 0.75 |  |  |  | ER | OTP | Center - Mandan 230 kV
GEN-2007-017IS | 02 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 202 |  |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2007-018IS | 02 - Nebraska | 14.5 | DIS-15-2-PQ | Wind | 198 |  |  |  | ER/NR | OPPD | Ft Thompson-Grand Island 345kV
GEN-2015-023 | 02 - Nebraska | 14 | DIS-15-1 | Wind | 300.72 |  |  |  | ER/NR | NPPD | Grand Prairie-Grand Island (Holt County NE) 345kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2015-001 | 03 - Central | 14 | DIS-15-1 | Combustion Turbine | 6.13 |  |  |  | ER | SUNC | Ninnescah 115kV
GEN-2015-005 | 03 - Central | 14 | DIS-15-1 | Wind | 200.11 |  |  |  | ER | KCPL | Mullen Creek-Sibley (Ketchum) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2015-013 | 04 - Southeast | 14 | DIS-15-1 | Solar | 120 |  |  |  | ER/NR | WFEC | Snyder 138kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-032 | 02 - Nebraska | 13 | DIS-14-2 | Wind | 10.22 |  |  |  | ER/NR | NPPD | Meadow Grove 230kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-025 | 03 - Central | 13 | DIS-14-2 | Wind | 2.42 |  |  |  | ER | MIDW | Tap Nekoma - Bazine (Walnut Creek) 69kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-057 | 04 - Southeast | 13 | DIS-14-2 | Wind | 249.9 |  |  |  | ER | AEPW | Lawton East Side-Sunnyside (Terry Road) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-035 | 05 - Southwest | 13 | DIS-14-2 | Solar | 30 |  |  |  | ER | SPS | Chaves County 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-004 | 02 - Nebraska | 12 | DIS-14-1 | Wind | 3.96 |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-001 | 03 - Central | 12 | DIS-14-1 | Wind | 200.6 |  |  |  | ER | WERE | Tap Wichita - Emporia Energy Center 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2014-002 | 04 - Southeast | 12 | DIS-14-1 | Wind | 10.53 |  |  |  | ER | OKGE | Tatonga 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2014-005 | 04 - Southeast | 12 | DIS-14-1 | Wind | 5.67 |  |  |  | ER | OKGE | Minco 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2013-019 | 02 - Nebraska | 11 | DIS-13-2 | Wind | 73.6 |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
ASGI-2013-005 | 05 - Southwest | 11 | DIS-13-2 | Wind | 1.65 |  |  |  | ER | SPS | FE Clovis 115kV
GEN-2013-002 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 50.6 |  |  |  | ER/NR | NPPD | Monolith 115kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2013-008 | 02 - Nebraska | 10 | DIS-13-1 | Wind | 1.2 |  |  |  | ER | NPPD | Steele City 115kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
ASGI-2013-002 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  |  | ER | SPS | FE Tucumcari 115kV
ASGI-2013-003 | 05 - Southwest | 10 | DIS-13-1 | Wind | 18.4 |  |  |  | ER | SPS | FE Clovis 115kV
ASGI-2012-002 | 05 - Southwest | 9 | DIS-12-2 | Wind | 18.15 |  |  |  | ER | SPS | FE-Clovis Interchange 115kV
NPPDBuffaloCountySolar | 02 - Nebraska | 8 | PQ | Solar | 10 |  |  |  | ER | NPPD | Kearney Northeast
NPPDBurtCountyWind | 02 - Nebraska | 8 | PQ | Wind | 20 |  |  |  | ER | NPPD | Tekamah & Oakland 115kV
ASGI-2012-006 | 03 - Central | 8 | DIS-12-1 | Waste Heat | 22.5 |  |  |  | ER | SUNC | Tap Hugoton - Rolla 69kV
ASGI-2010-006GIA-27 | 04 - Southeast | 8 | PQ | Wind | 150 |  |  |  | ER | AECI | Remington 138kV
GEN-2012-004 | 04 - Southeast | 8 | DIS-12-1 | Wind | 40.8 |  |  |  | ER/NR | OKGE | Pooleville-Ratliff (Carter County) 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-037 | 04 - Southeast | 7 | DIS-11-2 | Wind | 6.6 |  |  |  | ER | WFEC | Blue Canyon 5 138kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2011-019 | 04 - Southeast | 6 | DIS-11-1 | Wind | 175 |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-020 | 04 - Southeast | 6 | DIS-11-1 | Wind | 165.6 |  |  |  | ER/NR | OKGE | Woodward EHV 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2011-022 | 05 - Southwest | 6 | DIS-11-1 | Wind | 299 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2010-014 | 05 - Southwest | 4 | DIS-10-1 | Wind | 358.8 |  |  |  | ER | SPS | Hitchland 345kV | IA FULLY EXECUTED/ON SCHEDULE
GEN-2008-124 | 03 - Central | 3 | DIS-09-1 | Wind | 200.1 |  |  |  | ER | SUNC | Clark County-Spearville Ckt 1 (Ironwood) 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION
GEN-2008-018 | 03 - Central | 2 | ICS1 | Wind | 250 |  |  |  | ER | SPS | Finney 345kV | IA FULLY EXECUTED/COMMERCIAL OPERATION

## Constraints Summary
Group | Service Type | Constraint Type | Constraints | Seasons | Most Severe Contingency | MVA Rate A | MVA Rate B | BC Loading % | TC Loading % | TC Voltage | VMIN | VMAX | Upgrade Name
01ALL | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
01ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
01ALL | ERIS | Thermal | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 23SP, 26SP | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1 |  | 120 | 83.9 | 106.17 |  |  |  | Groton to Bristol 115 kV Rebuild
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 26L | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1 |  | 73 | 95.67 | 124.2 |  |  |  | Summit to Bristol 115 kV Rebuild
01ALL | ERIS | Thermal | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 23SP | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1 |  | 120 | 80.9 | 103.9 |  |  |  | Summit to Bristol 115 kV Rebuild
01ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV: | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV: | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV: | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV: | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV: | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | Non-Converge | 23SP | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 | [7 empty] | Gentleman to Cherry County and Cherry County to Holt new 345 kV line
02ALL | ERIS | Non-Converge | None | 26L, 26SP, 26WP | None | [7 empty] | None
02ALL | ERIS | Stability | Low Voltages, Controller Oscillations | 25S, 25W | Multiple Contingencies (See Stability Analysis Results Tab) | [7 empty] | Build a 50 MVAR STATCOM at GR PRAIRIE 345 kV
02ALL | ERIS | Thermal | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 26SP | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1 |  | 842 | 94.07 | 100.18 |  |  |  | Raise Spans on Holt Co to Grand Island 345 kV
02ALL | ERIS | Thermal | None | 23SP, 26L, 26WP | None | [7 empty] | None
02ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1 | [7 empty] | Build New Holt to Atchison 345 kV Line
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV: | [7 empty] | Build New Holt to Atchison 345 kV Line
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P12:345:GMO-OPPD:S3458-HOLT:::EHV: | [7 empty] | Build New Holt to Atchison 345 kV Line
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P14:345:GMO-OPPD:S3458 REACTOR:::EHV: | [7 empty] | Build New Holt to Atchison 345 kV Line
03ALL | ERIS | Non-Converge | Non-Converge | 23SP, 26L, 26SP, 26WP | P45:345:OPPD:S3455-S3761&T3:::EHV: | [7 empty] | Build New Holt to Atchison 345 kV Line
03ALL | ERIS | Stability | Low Voltages, Controller Oscillations | 25S | GROUP3_FAULT_655,GROUP3_FAULT_656 (See Stability Analysis Results Tab) | [7 empty] | Build New Holt to Atchison 345 kV Line
03ALL | ERIS | Stability | Low Voltages, Controller Oscillations | 25S, 25W | GROUP3_FAULT_342 (See Stability Analysis Results Tab) | [7 empty] | Build a second circuit from Holcomb 345 kV to Finney 345 kV
03ALL | ERIS | Thermal | None | 23SP, 26SP, 26WP | None | [7 empty] | None
03ALL | ERIS | Thermal | 523959 POTTER_CO 6 230 997752 WAUK 90343-A 230 1 | 26L | System Intact | 516 |  | 96.1 | 103.39 |  |  |  | Potter County 345/230 kV Circuit 1 Transformer Switch Replacement
03ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
04ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
04ALL | ERIS | Thermal | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 | 23SP | 508054 BANN 4 138 508075 REDSPRG4 138 1 |  | 153 | 62.28 | 107.13 |  |  |  | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001)
04ALL | ERIS | Thermal | 509776 52DELTP4 138 509800 36LEWIS4 138 1 | 23SP, 26SP | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1 |  | 278 | 109.6 | 118.8 |  |  |  | 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild
04ALL | ERIS | Thermal | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 | 23SP, 26SP | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1 |  | 278 | 96.65 | 105.9 |  |  |  | Delaware Tap to T.S.E. 138 kV Rebuild (DISIS-2018-001)
04ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | ERIS | Non-Converge | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | ERIS | Stability | None | 25S, 25W | None | [7 empty] | None
05ALL | ERIS | Thermal | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
05ALL | ERIS | Voltage | None | 23SP, 26L, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Non-Converge | None | 23SP, 26SP, 26WP | None | [7 empty] | None
00NR | NRIS | Thermal | None | 23SP, 26SP | None | [7 empty] | None
00NR | NRIS | Thermal | 652433 EDGELEY8 69.0 996753 ED KY6A _1 69.0 1 | 26WP | 652432 EDGELEY7 115 652445 JAMESTN7 115 1 |  | 37.5 | 52.4 | 102.75 |  |  |  | Edgeley 115/69 kV Transformer Replacement
00NR | NRIS | Voltage | None | 23SP, 26SP, 26WP | None | [7 empty] | None
01NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
01NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
01NR | NRIS | Voltage | None | 26L | None | [7 empty] | None
02NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
02NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
02NR | NRIS | Voltage | None | 26L | None | [7 empty] | None
03NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
03NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
03NR | NRIS | Voltage | None | 26L | None | [7 empty] | None
04NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
04NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
04NR | NRIS | Voltage | None | 26L | None | [7 empty] | None
05NR | NRIS | Non-Converge | None | 26L | None | [7 empty] | None
05NR | NRIS | Thermal | None | 26L | None | [7 empty] | None
05NR | NRIS | Voltage | None | 26L | None | [7 empty] | None

## Assigned Upgrade Costs
Gen Number | Group | Upgrade ID | Service Type | Upgrade Name | Upgrade Type | Upgrade Details | Allocated Cost | % Allocated | Total Upgrade Cost | PTDF
GEN-2018-039 | 00NR | 158552 | NRIS | Edgeley 115/69 kV Transformer Replacement | Current Study | Replace the existing 115/69 kV transformer at Edgeley to a minimum rating of 42 MVA | 2777743 | 100% | 2777743 | 0.0995
GEN-2018-008 | 01 - North | 158559 | ERIS | Groton to Bristol 115 kV Rebuild | Current Study | Rebuild the existing Groton to Bristol 115 kV 21.3 miles line with a minimum summer emergency rating of 139 MVA | 13158503.5293 | 86.91% | 15140892 | 0.03994
GEN-2018-039 | 01 - North | 158559 | ERIS | Groton to Bristol 115 kV Rebuild | Current Study | Rebuild the existing Groton to Bristol 115 kV 21.3 mile line with a minimum summer emergency rating of 139 MVA | 1982388.4707 | 13.09% | 15140892 | 0.02106
GEN-2018-008 | 01 - North | 158560 | ERIS | Summit to Bristol 115 kV Rebuild | Current Study | Rebuild the existing Summit to Bristol 115 kV 32.56 mile line with a minimum summer emergency rating of 136 MVA | 20114595.0663 | 86.91% | 23144950.4 | 0.03994
GEN-2018-039 | 01 - North | 158560 | ERIS | Summit to Bristol 115 kV Rebuild | Current Study | Rebuild the existing Summit to Bristol 115 kV 32.56 mile line with a minimum summer emergency rating of 136 MVA | 3030355.3337 | 13.09% | 23144950.4 | 0.02106
GEN-2018-056 | 02 - Nebraska | 158561 | ERIS | Raise Spans on Holt Co to Grand Island 345 kV | Current Study | Raise spans on the existing Holt Co to Grand Island 345 kV 82.3 mile line with a minimum summer emergency rating of 844 MVA | 6000000 | 100% | 6000000 | 0.43365
GEN-2018-056 | 02 - Nebraska | 158562 | ERIS | Build a 50 MVAR STATCOM at GR PRAIRIE 345 kV | Current Study | Install a 50 MVAR STATCOM at the GR PRAIRIE 345 kV substation | 11314100 | 100% | 11314100 | 1
GEN-2018-056 | 02 - Nebraska | NTC 200220 | ERIS | Gentleman to Cherry County and Cherry County to Holt new 345 kV line | Contingent | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | 0 | 0% | 450832958 | 0.19079
GEN-2018-060 | 02 - Nebraska | NTC 200220 | ERIS | Gentleman to Cherry County and Cherry County to Holt new 345 kV line | Contingent | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | 0 | 0% | 450832958 | 0.02979
ASGI-2018-003 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 94099.08 | 0.2821% | 33350992.8 | 0.01655
ASGI-2018-006 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 87105.61 | 0.2612% | 33350992.8 | 0.01532
ASGI-2018-007 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 39800.21 | 0.1193% | 33350992.8 | 0.007
ASGI-2018-010 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 162484.37 | 0.4872% | 33350992.8 | 0.01633
ASGI-2018-011 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 167260.4 | 0.5015% | 33350992.8 | 0.01681
GEN-2018-022 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 30097490.22 | 90.24% | 33350992.8 | 0.3529
GEN-2018-031 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 339581.11 | 1.018% | 33350992.8 | 0.02389
GEN-2018-032 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 1150965.32 | 3.451% | 33350992.8 | 0.01306
GEN-2018-054 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 837169.07 | 2.51% | 33350992.8 | 0.02454
GEN-2018-062 | 03 - Central | 158563 | ERIS | Build New Holt to Atchison 345 kV Line | Current Study | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | 375037.41 | 1.125% | 33350992.8 | 0.01745
GEN-2018-009 | 03 - Central | TBD | ERIS | Potter County 345/230 kV Circuit 1 Transformer Switch Replacement | Current Study | Replace the switch at the existing 345/230 kV transformer at Potter to achieve a minimum rating of 534 MVA | 300000 | 100% | 300000 | 0.05751
GEN-2018-030 | 03 - Central | 158569 | ERIS | Build a second circuit from Holcomb 345 kV to Finney 345 kV | Current Study | Build a second circuit from Holcomb 345 kV substation to Finney 345 kV substation (0.75 miiles) | 13400000 | 100% | 13400000 | 1
GEN-2018-027 | 04 - Southeast | NTC 210708 | ERIS | 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | Contingent | Rebuild the existing Delaware Tap to 36th&Lewis 138 kV 0.97 mile line with a minimum summer emergency rating of 335 MVA | 0 | 0% | 1491941 | 0.29454
GEN-2018-027 | 04 - Southeast | 158556 | ERIS | Delaware Tap to T.S.E. 138 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing Delaware Tap to T.S.E. 138 kV 2.09 mile line with a minimum summer emergency rating of 295 MVA | 2015092.31 | 100% | 2015092.31 | 0.29454
GEN-2018-003 | 04 - Southeast | 158555 | ERIS | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001) | Current Study | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating of 165 MVA | 1667995.07 | 100% | 1667995.07 | 0.45629
GEN-2018-021 | 04 - Southeast | TBD | ERIS | GEN-2016-037 Interconnection Costs | Contingent | Facilitate the interconnection of GEN-2018-021 | 0 | 0% | 18000000 | 1
GEN-2018-003 | 04 - Southeast | 156178 | ERIS | North Boston-Bann 138kV GEN-2018-003 Interconnection (TOIF) (AEPW) | Interconnection | Facilitate the interconnection of GEN-2018-003 | 1337068 | 100% | 1337068 | 1
GEN-2018-003 | 04 - Southeast | 156179 | ERIS | North Boston-Bann 138kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-003 | 8857127 | 100% | 8857127 | 1
GEN-2018-004 | 05 - Southwest | 156242 | ERIS | T14 Circuit 115kV GEN-2018-004 Interconnection (TOIF) | Interconnection | Facilitate the interconnection of GEN-2018-004 | 1107176 | 100% | 1107176 | 1
GEN-2018-004 | 05 - Southwest | 156243 | ERIS | T14 Circuit 115kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-004 | 10430297 | 100% | 10430297 | 1
GEN-2018-008 | 01 - North | 156037 | ERIS | Groton-Leland Olds 345kV GEN-2018-008 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2018-008 | 2334054 | 100% | 2334054 | 1
GEN-2018-008 | 01 - North | 156038 | ERIS | Groton-Leland Olds 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-008 | 20903079 | 100% | 20903079 | 1
GEN-2018-009 | 03 - Central | 155901 | ERIS | Cimarron 115kV Substation GEN-2018-009 Interconnection (TOIF) (SUNC) | Interconnection | Facilitate the interconnection of GEN-2018-009 | 500000 | 100% | 500000 | 1
GEN-2018-009 | 03 - Central | 155902 | ERIS | Cimarron 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-009 | 4000000 | 100% | 4000000 | 1
GEN-2018-010 | 01 - North | 156176 | ERIS | Neset 230kV Substation GEN-2018-010 Interconnection (TOIF) (BEPC) | Interconnection | Facilitate the interconnection of GEN-2018-010 | 120000 | 100% | 120000 | 1
GEN-2018-010 | 01 - North | 156177 | ERIS | Neset 230kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-010 | 0 | 100% | 0 | 1
GEN-2018-011 | 04 - Southeast | 155903 | ERIS | Dover 138 kV Switching Station GEN-2018-011 Interconnection (TOIF) (WFEC) | Interconnection | Facilitate the interconnection of GEN-2018-011 | 1479500 | 100% | 1479500 | 1
GEN-2018-011 | 04 - Southeast | 155904 | ERIS | Dover 138 kV Switching Station Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-011 | 0 | 100% | 0 | 1
GEN-2018-012 | 02 - Nebraska | 155889 | ERIS | Antelope Substation 345kV GEN-2018-012 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-012 | 1500000 | 100% | 1500000 | 1
GEN-2018-012 | 02 - Nebraska | 155890 | ERIS | Antelope Substation 345kV Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-012 | 5500000 | 100% | 5500000 | 1
GEN-2018-013 | 03 - Central | 155729 | ERIS | Abilene Energy Center-Northview 115kV GEN-2018-013 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-013 | 0 | 0% | 0 | 1
GEN-2018-013 | 03 - Central | 155730 | ERIS | Abilene Energy Center-Northview 115kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-013 | 0 | 0% | 0 | 1
GEN-2018-015 | 05 - Southwest | 156219 | ERIS | Tuco-Oklaunion 345kV GEN-2018-015 Interconnection (TOIF) (SWPS) | Interconnection | Facilitate the interconnection of GEN-2018-015 | 1860250 | 100% | 1860250 | 1
GEN-2018-015 | 05 - Southwest | 156220 | ERIS | Tuco-Oklaunion 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-015 | 18641931 | 100% | 18641931 | 1
GEN-2018-022 | 03 - Central | 156168 | ERIS | Mullen Creek 345kV Substation GEN-2018-022 Interconnection (TOIF) (EMW) | Interconnection | Facilitate the interconnection of GEN-2018-022 | 1900000 | 100% | 1900000 | 1
GEN-2018-022 | 03 - Central | 156169 | ERIS | Mullen Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-022 | 5800000 | 100% | 5800000 | 1
GEN-2018-024 | 04 - Southeast | 155895 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV GEN-2018-024 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-024 | 1500000 | 100% | 1500000 | 1
GEN-2018-024 | 04 - Southeast | 155896 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-024 | 2500000 | 100% | 2500000 | 1
GEN-2018-025 | 02 - Nebraska | 155907 | ERIS | Fort Calhoun 345kV Substation GEN-2018-025 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-025 | 0 | 100% | 0 | 1
GEN-2018-025 | 02 - Nebraska | 156027 | ERIS | Fort Calhoun 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-025 and GEN-2018-044 | 3021587 | 100% | 3021587 | 1
GEN-2018-026 | 04 - Southeast | 156170 | ERIS | Mustang 138kV Substation GEN-2018-026 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2018-026 | 750000 | 100% | 750000 | 1
GEN-2018-026 | 04 - Southeast | 156171 | ERIS | Mustang 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-026 | 2000000 | 100% | 2000000 | 1
GEN-2018-027 | 04 - Southeast | 156223 | ERIS | Tulsa Power Station 38kV Substation GEN-2018-027 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-027 | 1337068 | 100% | 1337068 | 1
GEN-2018-027 | 04 - Southeast | 156224 | ERIS | Tulsa Power Station 38kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-027 | 9174000 | 100% | 9174000 | 1
GEN-2018-028 | 04 - Southeast | 156221 | ERIS | Tulsa North 138kV Substation GEN-2018-028 Interconnection (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-028 | 1337068 | 100% | 1337068 | 1
GEN-2018-028 | 04 - Southeast | 156222 | ERIS | Tulsa North 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-028 | 5324780 | 100% | 5324780 | 1
GEN-2018-029 | 04 - Southeast | 156041 | ERIS | Horseshoe Lake 138kV Substation GEN-2018-029 Interconnection (TOIF) (OKGE) | Interconnection | Facilitate the interconnection of GEN-2018-029 | 3500000 | 100% | 3500000 | 1
GEN-2018-029 | 04 - Southeast | 156042 | ERIS | Horseshoe Lake 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-029 | 750000 | 100% | 750000 | 1
GEN-2018-030 | 03 - Central | 156162 | ERIS | Lamar-Finney 345kV Substation GEN-2018-030 Interconnection (TOIF) (SWPS) | Interconnection | Facilitate the interconnection of GEN-2018-030 | 1975117 | 100% | 1975117 | 1
GEN-2018-030 | 03 - Central | 156163 | ERIS | Lamar-Finney 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-030 | 1152973 | 100% | 1152973 | 1
GEN-2018-031 | 03 - Central | 155893 | ERIS | Blue Valley 161kV Substation GEN-2018-031 Interconnection (TOIF) (INDN) | Interconnection | Facilitate the interconnection of GEN-2018-031 | 1500000 | 100% | 1500000 | 1
GEN-2018-031 | 03 - Central | 155894 | ERIS | Blue Valley 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-031 | 4500000 | 100% | 4500000 | 1
GEN-2018-032 | 03 - Central | 156174 | ERIS | Neosho 345kV Substation GEN-2018-032 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-032 | 1158673 | 100% | 1158673 | 1
GEN-2018-032 | 03 - Central | 156175 | ERIS | Neosho 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-032 | 2287131 | 100% | 2287131 | 1
GEN-2018-033 | 02 - Nebraska | 155897 | ERIS | Cass County 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-033 | 2292537 | 100% | 2292537 | 1
GEN-2018-033 | 02 - Nebraska | 155898 | ERIS | Cass County 345kV Substation Interconnection Expansion GEN-2018-033 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-033 | 1662072 | 100% | 1662072 | 1
GEN-2018-037 | 02 - Nebraska | 156166 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-037 | 1722352 | 100% | 1722352 | 1
GEN-2018-037 | 02 - Nebraska | 156167 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV GEN-2018-037 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-037 | 10260510 | 100% | 10260510 | 1
GEN-2018-039 | 01 - North | 155905 | ERIS | Edgeley 115kV Substation GEN-2018-039 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-039 | 1709000 | 100% | 1709000 | 1
GEN-2018-039 | 01 - North | 155906 | ERIS | Edgeley 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-039 | 1709000 | 100% | 1709000 | 1
GEN-2018-043 | 02 - Nebraska | 156030 | ERIS | Ft. Calhoun - Raun 345 kV GEN-2018-043 Interconnection (TOIF) (OPPD) | Interconnection | Facilitate the interconnection of GEN-2018-043 | 8894071 | 100% | 8894071 | 1
GEN-2018-043 | 02 - Nebraska | 156031 | ERIS | Ft. Calhoun - Raun 345 kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-043 | 0 | 100% | 0 | 1
GEN-2018-048 | 04 - Southeast | 156180 | ERIS | Pecan Creek 345kV Substation GEN-2018-048 Interconnection (TOIF) (OGE) | Interconnection | Facilitate the interconnection of GEN-2018-048 | 1500000 | 100% | 1500000 | 1
GEN-2018-048 | 04 - Southeast | 156182 | ERIS | Pecan Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-048 and GEN-2018-051 (Group 05) | 10000000 | 100% | 10000000 | 1
GEN-2018-049 | 03 - Central | 156246 | ERIS | Thistle 345kV Substation GEN-2018-049 Interconnection (TOIF) (ITCGP) | Interconnection | Facilitate the interconnection of GEN-2018-049 | 857280 | 100% | 857280 | 1
GEN-2018-049 | 03 - Central | 156247 | ERIS | Thistle 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-049 | 3000000 | 100% | 3000000 | 1
GEN-2018-050 | 04 - Southeast | 156164 | ERIS | Longwood 345kV Substation GEN-2018-050 Interconnection (TOIF) (AEPW) | Interconnection | Facilitate the interconnection of GEN-2018-050 | 1541013 | 100% | 1541013 | 1
GEN-2018-050 | 04 - Southeast | 156165 | ERIS | Longwood 345kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-050 | 8130655 | 100% | 8130655 | 1
GEN-2018-052 | 05 - Southwest | 156183 | ERIS | Roadrunner 115kV Substation GEN-2018-052 Interconnection (TOIF) (SWPS) | Interconnection | Facilitate the interconnection of GEN-2018-052 | 1128837 | 100% | 1128837 | 1
GEN-2018-052 | 05 - Southwest | 156184 | ERIS | Roadrunner 115kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-052 | 1039552 | 100% | 1039552 | 1
GEN-2018-054 | 03 - Central | 156043 | ERIS | KC South - N. Raymore 161kV GEN-2018-054 Interconnection (TOIF) (EMW) | Interconnection | Facilitate the interconnection of GEN-2018-054 | 750897 | 100% | 750897 | 1
GEN-2018-054 | 03 - Central | 156044 | ERIS | KC South - N. Raymore 161kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-054 | 30735337 | 100% | 30735337 | 1
GEN-2018-055 | 04 - Southeast | 156244 | ERIS | Terry Road 345kV Substation (TOIF) (AEP) | Interconnection | Facilitate the interconnection of GEN-2018-055 | 733380 | 100% | 733380 | 1
GEN-2018-055 | 04 - Southeast | 156245 | ERIS | Terry Road 345kV Substation Interconnection Expansion | Interconnection | Facilitate the interconnection of GEN-2018-055 | 50000 | 100% | 50000 | 1
GEN-2018-056 | 02 - Nebraska | 156028 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV GEN-2018-056 Interconnection (TOIF) (WAPA) | Interconnection | Facilitate the interconnection of GEN-2018-056 | 2898000 | 100% | 2898000 | 1
GEN-2018-056 | 02 - Nebraska | 156029 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-056 | 2898000 | 100% | 2898000 | 1
GEN-2018-057 | 03 - Central | 156035 | ERIS | Gordon Evans 138kV Substation GEN-2018-057 Interconnection (TOIF) (EKC) | Interconnection | Facilitate the interconnection of GEN-2018-057 | 744762 | 100% | 744762 | 1
GEN-2018-057 | 03 - Central | 156036 | ERIS | Gordon Evans 138kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-057 | 1234682 | 100% | 1234682 | 1
GEN-2018-060 | 02 - Nebraska | 155891 | ERIS | Axtell-Post Rock 345 kV GEN-2018-060 Interconnection (TOIF) (NPPD) | Interconnection | Facilitate the interconnection of GEN-2018-060 | 1500000 | 100% | 1500000 | 1
GEN-2018-060 | 02 - Nebraska | 155892 | ERIS | Axtell-Post Rock 345 kV Line Tap (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-060 | 50000 | 100% | 50000 | 1
GEN-2018-062 | 03 - Central | 156172 | ERIS | Nearman 161kV Substation GEN-2018-062 Interconnection (TOIF) (KACY) | Interconnection | Facilitate the interconnection of GEN-2018-062 | 510232 | 100% | 510232 | 1
GEN-2018-062 | 03 - Central | 156173 | ERIS | Nearman 161kV Substation Interconnection Expansion (DISIS-2018-001) | Interconnection | Facilitate the interconnection of GEN-2018-062 | 2005192 | 100% | 2005192 | 1
Total | [8 empty] | 338708005.58

## Upgrade Summary
Upgrade Type | Study Type | Group | Assigned Study Number | Service Type | Upgrade Name | Upgrade ID | Upgrade Details | Transmission Owner(s) | Estimated Lead Time | Total Upgrade Cost
Current Study | Steady State | 00-NR | DISIS-2018-001 | NRIS | Edgeley 115/69 kV Transformer Replacement | 158552 | Replace the existing 115/69 kV transformer at Edgeley to a minimum rating of 42 MVA | WAPA | 36 | 2777743
Current Study | Steady State | 01 - North | DISIS-2018-001 | ERIS | Groton to Bristol 115 kV Rebuild | 158559 | Rebuild the existing Groton to Bristol 115 kV 21.3 miles line with a minimum summer emergency rating of 139 MVA | WAPA/BEPC | 36 | 15140892
Current Study | Steady State | 01 - North | DISIS-2018-001 | ERIS | Summit to Bristol 115 kV Rebuild | 158560 | Rebuild the existing Summit to Bristol 115 kV 32.56 mile line with a minimum summer emergency rating of 136 MVA | WAPA/BEPC | 36 | 23144950.4
Current Study | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Raise Spans on Holt Co to Grand Island 345 kV | 158561 | Raise spans on the existing Holt Co to Grand Island 345 kV 82.3 mile line with a minimum summer emergency rating of 844 MVA | WAPA | 36 | 6000000
Current Study | Stability | 02 - Nebraska | DISIS-2018-001 | ERIS | Build a 50 MVAR STATCOM at GR PRAIRIE 345 kV | 158562 | Install a 50 MVAR STATCOM at the GR PRAIRIE 345 kV substation | WAPA | 42 | 11314100
Contingent | Steady State | 02 - Nebraska | DISIS-2017-002 | ERIS | Gentleman to Cherry County and Cherry County to Holt new 345 kV line | NTC 200220 | Build approximately 110 miles of new 345kV line from Gentleman to Cherry County and 117 miles from Cherry County to Holt County | NPPD | NTC 200220 | 450832958
Current Study | Steady State/ Stability | 03 - Central | DISIS-2018-001 | ERIS | Build New Holt to Atchison 345 kV Line | 158563 | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles) | KCPL/MEC | 42 | 33350992.8
Current Study | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Potter County 345/230 kV Circuit 1 Transformer Switch Replacement | TBD | Replace the switch at the existing 345/230 kV transformer at Potter to achieve a minimum rating of 534 MVA | SPS | 24 | 300000
Current Study | Stability | 03 - Central | DISIS-2018-001 | ERIS | Build a second circuit from Holcomb 345 kV to Finney 345 kV | 158569 | Build a second circuit from Holcomb 345 kV substation to Finney 345 kV substation (0.75 miiles) | SUNC/SPS | 42 | 13400000
Contingent | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | 36th & Lewis - 52nd & Delaware Tap 138 kV Rebuild | NTC 210708 | Rebuild the existing Delaware Tap to 36th&Lewis 138 kV 0.97 mile line with a minimum summer emergency rating of 335 MVA | AEPW | NTC 210708 | 1491941
Current Study | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Delaware Tap to T.S.E. 138 kV Rebuild (DISIS-2018-001) | 158556 | Rebuild the existing Delaware Tap to T.S.E. 138 kV 2.09 mile line with a minimum summer emergency rating of 295 MVA | AEPW | 36 | 2015092.31
Current Study | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | N North Boston to GEN-2018-003-TAP 138 kV Rebuild (DISIS-2018-001) | 158555 | Rebuild the existing N North Boston to GEN-2018-003-TAP 138 kV 1.73 mile line with a minimum summer emergency rating of 165 MVA | AEPW | 36 | 1667995.07
Contingent | Steady State | 04 - Southeast | DISIS-2016-001 | ERIS | GEN-2016-037 Interconnection Costs | 132902/132903 | Facilitate the interconnection of GEN-2018-021 | AEP | 36 | 18000000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | North Boston-Bann 138kV GEN-2018-003 Interconnection (TOIF) (AEPW) | 156178 | Facilitate the interconnection of GEN-2018-003 | AEP | 36 | 1337068
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | North Boston-Bann 138kV Line Tap (DISIS-2018-001) | 156179 | Facilitate the interconnection of GEN-2018-003 | AEP | 36 | 8857127
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | T14 Circuit 115kV GEN-2018-004 Interconnection (TOIF) | 156242 | Facilitate the interconnection of GEN-2018-004 | SPS | 32 | 1107176
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | T14 Circuit 115kV Line Tap (DISIS-2018-001) | 156243 | Facilitate the interconnection of GEN-2018-004 | SPS | 32 | 10430297
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Groton-Leland Olds 345kV GEN-2018-008 Interconnection (TOIF) (BEPC) | 156037 | Facilitate the interconnection of GEN-2018-008 | BEPC | 24 | 2334054
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Groton-Leland Olds 345kV Line Tap (DISIS-2018-001) | 156038 | Facilitate the interconnection of GEN-2018-008 | BEPC | 24 | 20903079
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Cimarron 115kV Substation GEN-2018-009 Interconnection (TOIF) (SUNC) | 155901 | Facilitate the interconnection of GEN-2018-009 | SEPC | 33 | 500000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Cimarron 115kV Substation Interconnection Expansion (DISIS-2018-001) | 155902 | Facilitate the interconnection of GEN-2018-009 | SEPC | 33 | 4000000
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Neset 230kV Substation GEN-2018-010 Interconnection (TOIF) (BEPC) | 156176 | Facilitate the interconnection of GEN-2018-010 | BEPC | 3 | 120000
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Neset 230kV Substation Interconnection Expansion (DISIS-2018-001) | 156177 | Facilitate the interconnection of GEN-2018-010 | BEPC | 0 | 0
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Dover 138 kV Switching Station GEN-2018-011 Interconnection (TOIF) (WFEC) | 155903 | Facilitate the interconnection of GEN-2018-011 | WFEC | 36 | 1479500
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Dover 138 kV Switching Station Interconnection Expansion (DISIS-2018-001) | 155904 | Facilitate the interconnection of GEN-2018-011 | WFEC | 0 | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Antelope Substation 345kV GEN-2018-012 Interconnection (TOIF) (NPPD) | 155889 | Facilitate the interconnection of GEN-2018-012 | NPPD | 36 | 1500000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Antelope Substation 345kV Interconnection Expansion (DISIS-2018-001) | 155890 | Facilitate the interconnection of GEN-2018-012 | NPPD | 36 | 5500000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Abilene Energy Center-Northview 115kV GEN-2018-013 Interconnection (TOIF) (EKC) | 155729 | Facilitate the interconnection of GEN-2018-013 | WERE | 24 | 0
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Abilene Energy Center-Northview 115kV Line Tap (DISIS-2018-001) | 155730 | Facilitate the interconnection of GEN-2018-013 | WERE | 24 | 0
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | Tuco-Oklaunion 345kV GEN-2018-015 Interconnection (TOIF) (SWPS) | 156219 | Facilitate the interconnection of GEN-2018-015 | SPS | 32 | 1860250
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | Tuco-Oklaunion 345kV Line Tap (DISIS-2018-001) | 156220 | Facilitate the interconnection of GEN-2018-015 | SPS | 32 | 18641931
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Mullen Creek 345kV Substation GEN-2018-022 Interconnection (TOIF) (EMW) | 156168 | Facilitate the interconnection of GEN-2018-022 | WERE | 36 | 1900000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Mullen Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156169 | Facilitate the interconnection of GEN-2018-022 | WERE | 36 | 5800000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV GEN-2018-024 Interconnection (TOIF) (OGE) | 155895 | Facilitate the interconnection of GEN-2018-024 | OGE | 24 | 1500000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Canadian River-Muskogee and Muskogee-Seminole 345kV Line Tap (DISIS-2018-001) | 155896 | Facilitate the interconnection of GEN-2018-024 | OGE | 24 | 2500000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Fort Calhoun 345kV Substation GEN-2018-025 Interconnection (TOIF) (OPPD) | 155907 | Facilitate the interconnection of GEN-2018-025 | OPPD | 0 | 0
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Fort Calhoun 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156027 | Facilitate the interconnection of GEN-2018-025 and GEN-2018-044 | OPPD | 24 | 3021587
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Mustang 138kV Substation GEN-2018-026 Interconnection (TOIF) (OKGE) | 156170 | Facilitate the interconnection of GEN-2018-026 | OGE | 24 | 750000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Mustang 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156171 | Facilitate the interconnection of GEN-2018-026 | OGE | 24 | 2000000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Tulsa Power Station 38kV Substation GEN-2018-027 Interconnection (TOIF) (AEP) | 156223 | Facilitate the interconnection of GEN-2018-027 | AEP | 36 | 1337068
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Tulsa Power Station 38kV Substation Interconnection Expansion (DISIS-2018-001) | 156224 | Facilitate the interconnection of GEN-2018-027 | AEP | 36 | 9174000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Tulsa North 138kV Substation GEN-2018-028 Interconnection (TOIF) (AEP) | 156221 | Facilitate the interconnection of GEN-2018-028 | AEP | 36 | 1337068
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Tulsa North 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156222 | Facilitate the interconnection of GEN-2018-028 | AEP | 36 | 5324780
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Horseshoe Lake 138kV Substation GEN-2018-029 Interconnection (TOIF) (OKGE) | 156041 | Facilitate the interconnection of GEN-2018-029 | OGE | 24 | 3500000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Horseshoe Lake 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156042 | Facilitate the interconnection of GEN-2018-029 | OGE | 24 | 750000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Lamar-Finney 345kV Substation GEN-2018-030 Interconnection (TOIF) (SWPS) | 156162 | Facilitate the interconnection of GEN-2018-030 | SPS | 32 | 1975117
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Lamar-Finney 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156163 | Facilitate the interconnection of GEN-2018-030 | SPS | 32 | 1152973
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Blue Valley 161kV Substation GEN-2018-031 Interconnection (TOIF) (INDN) | 155893 | Facilitate the interconnection of GEN-2018-031 | INDN | 24 | 1500000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Blue Valley 161kV Substation Interconnection Expansion (DISIS-2018-001) | 155894 | Facilitate the interconnection of GEN-2018-031 | INDN | 36 | 4500000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Neosho 345kV Substation GEN-2018-032 Interconnection (TOIF) (EKC) | 156174 | Facilitate the interconnection of GEN-2018-032 | WERE | 36 | 1158673
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Neosho 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156175 | Facilitate the interconnection of GEN-2018-032 | WERE | 36 | 2287131
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Cass County 345kV Substation Interconnection Expansion (DISIS-2018-001) | 155897 | Facilitate the interconnection of GEN-2018-033 | OPPD | 24 | 2292537
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Cass County 345kV Substation Interconnection Expansion GEN-2018-033 Interconnection (TOIF) (OPPD) | 155898 | Facilitate the interconnection of GEN-2018-033 | OPPD | 24 | 1662072
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV (DISIS-2018-001) | 156166 | Facilitate the interconnection of GEN-2018-037 | OPPD | 24 | 1722352
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Looping in OPPD (S1211) (S1220) (S1211) (S1299) 161kV GEN-2018-037 Interconnection (TOIF) (OPPD) | 156167 | Facilitate the interconnection of GEN-2018-037 | OPPD | 24 | 10260510
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Edgeley 115kV Substation GEN-2018-039 Interconnection (TOIF) (WAPA) | 155905 | Facilitate the interconnection of GEN-2018-039 | WAPA | 36 | 1709000
Interconnection | Steady State | 01 - North | DISIS-2018-001 | ERIS | Edgeley 115kV Substation Interconnection Expansion (DISIS-2018-001) | 155906 | Facilitate the interconnection of GEN-2018-039 | WAPA | 36 | 1709000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Ft. Calhoun - Raun 345 kV GEN-2018-043 Interconnection (TOIF) (OPPD) | 156030 | Facilitate the interconnection of GEN-2018-043 | OPPD | 30 | 8894071
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Ft. Calhoun - Raun 345 kV Line Tap (DISIS-2018-001) | 156031 | Facilitate the interconnection of GEN-2018-043 | OPPD | 0 | 0
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Pecan Creek 345kV Substation GEN-2018-048 Interconnection (TOIF) (OGE) | 156180 | Facilitate the interconnection of GEN-2018-048 | OGE | 24 | 1500000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Pecan Creek 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156182 | Facilitate the interconnection of GEN-2018-048 and GEN-2018-051 (Group 05) | OGE | 24 | 10000000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Thistle 345kV Substation GEN-2018-049 Interconnection (TOIF) (ITCGP) | 156246 | Facilitate the interconnection of GEN-2018-049 | ITCGP | 36 | 857280
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Thistle 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156247 | Facilitate the interconnection of GEN-2018-049 | ITCGP | 36 | 3000000
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Longwood 345kV Substation GEN-2018-050 Interconnection (TOIF) (AEPW) | 156164 | Facilitate the interconnection of GEN-2018-050 | AEP | 36 | 1541013
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Longwood 345kV Substation Interconnection Expansion (DISIS-2018-001) | 156165 | Facilitate the interconnection of GEN-2018-050 | AEP | 36 | 8130655
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | Roadrunner 115kV Substation GEN-2018-052 Interconnection (TOIF) (SWPS) | 156183 | Facilitate the interconnection of GEN-2018-052 | SPS | 24 | 1128837
Interconnection | Steady State | 05 - Southwest | DISIS-2018-001 | ERIS | Roadrunner 115kV Substation Interconnection Expansion (DISIS-2018-001) | 156184 | Facilitate the interconnection of GEN-2018-052 | SPS | 24 | 1039552
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | KC South - N. Raymore 161kV GEN-2018-054 Interconnection (TOIF) (EMW) | 156043 | Facilitate the interconnection of GEN-2018-054 | WERE | 42 | 750897
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | KC South - N. Raymore 161kV Line Tap (DISIS-2018-001) | 156044 | Facilitate the interconnection of GEN-2018-054 | WERE | 42 | 30735337
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Terry Road 345kV Substation (TOIF) (AEP) | 156244 | Facilitate the interconnection of GEN-2018-055 | AEP | 36 | 733380
Interconnection | Steady State | 04 - Southeast | DISIS-2018-001 | ERIS | Terry Road 345kV Substation Interconnection Expansion | 156245 | Facilitate the interconnection of GEN-2018-055 | AEP | 36 | 50000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV GEN-2018-056 Interconnection (TOIF) (WAPA) | 156028 | Facilitate the interconnection of GEN-2018-056 | WAPA | 36 | 2898000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Fort Thompson-Grand Island (Grand Prairie) 345kV Line Tap (DISIS-2018-001) | 156029 | Facilitate the interconnection of GEN-2018-056 | WAPA | 36 | 2898000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Gordon Evans 138kV Substation GEN-2018-057 Interconnection (TOIF) (EKC) | 156035 | Facilitate the interconnection of GEN-2018-057 | WERE | 24 | 744762
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Gordon Evans 138kV Substation Interconnection Expansion (DISIS-2018-001) | 156036 | Facilitate the interconnection of GEN-2018-057 | WERE | 24 | 1234682
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Axtell-Post Rock 345 kV GEN-2018-060 Interconnection (TOIF) (NPPD) | 155891 | Facilitate the interconnection of GEN-2018-060 | NPPD | 36 | 1500000
Interconnection | Steady State | 02 - Nebraska | DISIS-2018-001 | ERIS | Axtell-Post Rock 345 kV Line Tap (DISIS-2018-001) | 155892 | Facilitate the interconnection of GEN-2018-060 | NPPD | 36 | 50000
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Nearman 161kV Substation GEN-2018-062 Interconnection (TOIF) (KACY) | 156172 | Facilitate the interconnection of GEN-2018-062 | KACY | 36 | 510232
Interconnection | Steady State | 03 - Central | DISIS-2018-001 | ERIS | Nearman 161kV Substation Interconnection Expansion (DISIS-2018-001) | 156173 | Facilitate the interconnection of GEN-2018-062 | KACY | 36 | 2005192
809032904.58

## All Thermal
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | DIRECTION | MONTCOMMONNAME | RATEA | RATEB | TDF | TC%LOADING | CONTNAME
Non-Converge | 00NR | 0 | 23SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 00NR | 0 | 26WP | N/A | " | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | 23SP | N/A | " | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | 26L | N/A | " | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 01ALL | 0 | 26WP | N/A | " | None |  |  |  |  | None
Non-Converge | 01NR | 0 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 00NR | 1 | 26WP | GEN-2018-039 | FROM -> TO | 652432 EDGELEY7 115 996753 ED KY6A _1 69.0 1 | 30 | 37.5 | 0.23657 | 101.93 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 00NR | 1 | 26WP | GEN-2018-039 | TO -> FROM | 652433 EDGELEY8 69.0 996753 ED KY6A _1 69.0 1 | 30 | 37.5 | 0.23657 | 102.75 | 652432 EDGELEY7 115 652445 JAMESTN7 115 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 106.17 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 106.13 | P42:345:UMZB:# 7115 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 106.13 | P42:345:UMZB:# 7116 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 106.13 | P42:345:UMZB:# 7113 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 106.13 | P42:345:UMZB:# 7117 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 106.13 | P42:345:UMZB:# 7118 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 106.13 | P42:345:UMZB:# 7114 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 105.86 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09218 | 100.33 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 26SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09218 | 100.02 | P42:345:UMZB:# 7117 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09218 | 100.02 | P42:345:UMZB:# 7116 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09218 | 100.02 | P42:345:UMZB:# 7118 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09218 | 100.02 | P42:345:UMZB:# 7115 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09218 | 100.02 | P42:345:UMZB:# 7114 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-008 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09218 | 100.02 | P42:345:UMZB:# 7113 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 106.17 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 106.13 | P42:345:UMZB:# 7115 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Non-Converge | 02ALL | 0 | 26L | N/A | " | None |  |  |  |  | None
Non-Converge | 02ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 02ALL | 0 | 26WP | N/A | " | None |  |  |  |  | None
Non-Converge | 02NR | 0 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 106.13 | P42:345:UMZB:# 7116 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 106.13 | P42:345:UMZB:# 7113 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 106.13 | P42:345:UMZB:# 7117 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 106.13 | P42:345:UMZB:# 7118 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 106.13 | P42:345:UMZB:# 7114 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 105.86 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.05015 | 100.33 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.05015 | 100.02 | P42:345:UMZB:# 7117 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.05015 | 100.02 | P42:345:UMZB:# 7116 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.05015 | 100.02 | P42:345:UMZB:# 7118 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.05015 | 100.02 | P42:345:UMZB:# 7115 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.05015 | 100.02 | P42:345:UMZB:# 7114 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26SP | GEN-2018-039 | FROM -> TO | 652512 GROTON 7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.05015 | 100.02 | P42:345:UMZB:# 7113 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 103.09 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 103.05 | P42:345:UMZB:# 7114 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 103.05 | P42:345:UMZB:# 7115 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 103.05 | P42:345:UMZB:# 7116 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 103.05 | P42:345:UMZB:# 7117 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 103.05 | P42:345:UMZB:# 7113 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 103.05 | P42:345:UMZB:# 7118 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.09338 | 102.85 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 26L | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 73 | 73 | 0.09144 | 124.2 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 26L | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 73 | 73 | 0.09144 | 124.1 | P42:345:UMZB:# 7115 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26L | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 73 | 73 | 0.09144 | 124.1 | P42:345:UMZB:# 7116 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26L | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 73 | 73 | 0.09144 | 124.1 | P42:345:UMZB:# 7118 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26L | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 73 | 73 | 0.09144 | 124.1 | P42:345:UMZB:# 7114 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26L | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 73 | 73 | 0.09144 | 124.1 | P42:345:UMZB:# 7113 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26L | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 73 | 73 | 0.09144 | 124.1 | P42:345:UMZB:# 7117 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 26L | GEN-2018-008 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 73 | 73 | 0.09144 | 124.06 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 103.09 | 659160 GROTON__-BE3 345 659165 CROCKER_-BE3 345 1
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 103.05 | P42:345:UMZB:# 7114 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 103.05 | P42:345:UMZB:# 7115 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 292 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 103.05 | P42:345:UMZB:# 7116 #:: CKE IN SD. CKE-GRT BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 103.05 | P42:345:UMZB:# 7117 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 103.05 | P42:345:UMZB:# 7113 #:: CKE IN SD. CKE-WT2 BRANCH FAULT & CKE 192 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 103.05 | P42:345:UMZB:# 7118 #:: CKE IN SD. CKE-CKW BRANCH FAULT & CKE 392 STUCK BKR:EHV:
Thermal | 01ALL | 1 | 23SP | GEN-2018-039 | FROM -> TO | 652522 SUMMIT-7 115 655457 BRISTOL-ER7 115 1 | 120 | 120 | 0.0521 | 102.85 | P12:345:UMZW:# 1681 #:: WT2 IN SD. WT2-GRT BRANCH FAULT:EHV:
Thermal | 02ALL | 1 | 26SP | GEN-2018-056 | FROM -> TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 0.69486 | 100.18 | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 02ALL | 1 | 26SP | GEN-2018-056 | FROM -> TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 0.69486 | 100.18 | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Thermal | 02ALL | 1 | 26SP | GEN-2018-056 | FROM -> TO | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1 | 842 | 842 | 0.69486 | 100.18 | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.56966 |  | P12:345:UMZ:# 6231 #: GI IN SD. OUT-YEAR GRI TO HOLT CO - PROPER N-1 (LINE) FOR 640510-653871-1 AND 653571-653871-Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43034 |  | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43034 |  | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43034 |  | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.56966 |  | P21:345:UMZW:# 2421 #:: GI IN NE. GI-GILNX3 OPENED:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43034 |  | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.56966 |  | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.56966 |  | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.56966 |  | 640510 HOLT.CO3 345 653871 GR ISLD-LNX3 345 1
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43034 |  | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-056 | " | Non-Converge |  |  | 0.43034 |  | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05312 |  | P12:345:UMZ:# 5855 #: PROPER N-1 (LINE) FOR 652506-652807-Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05312 |  | P21:345:UMZW:# 324 #:: FT2 IN SD. OPENING OF A LINE SECTION W
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05312 |  | P21:345:UMZW:# 2410 #:: FT2 IN SD. FT2-FT22LNX3 OPENED:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05312 |  | P43:014:UMZW:# 2401 #:: FT IN SD. FT KU1B TRANSFORMER FAULT & FT 2386 STUCK BKR:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.15123 |  | P42:345:UMZW:# 2413 #:: FT2 IN SD. FT2-LO2 BRANCH FAULT & FT2 2992 STUCK BKR:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.15123 |  | P42:345:UMZW:# 2415 #:: FT2 IN SD. FT2-GI BRANCH FAULT & FT2 3392 STUCK BKR:EHV:
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05312 |  | 652532 GR PRAIRIE 3 345 652833 GRPRAR2-LNX3 345 Z
Non-Converge | 02ALL | 0 | 23SP | GEN-2018-060 | " | Non-Converge |  |  | 0.05312 |  | 652807 FTTHOM2-LNX3 345 652833 GRPRAR2-LNX3 345 1
Thermal | 03ALL | 1 | 26L | GEN-2018-009 | TO -> FROM | 523959 POTTER_CO 6 230 997752 WAUK 90343-A 230 1 | 516 | 559 | 0.05751 | 103.39 | System Intact
Thermal | 03ALL | 1 | 26L | GEN-2018-009 | FROM -> TO | 523961 POTTER_CO 7 345 997752 WAUK 90343-A 230 1 | 516 | 559 | 0.05751 | 102.63 | System Intact
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04415 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04415 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04415 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04415 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04415 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04153 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04153 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04153 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04153 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04153 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04807 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04807 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04807 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04807 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04807 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04816 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04816 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04816 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04816 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04816 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54177 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54177 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54177 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54177 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54177 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06228 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06228 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06228 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06228 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06228 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06143 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06143 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06143 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06143 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06143 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05223 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05223 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05223 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05223 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 23SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05223 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04362 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04362 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04362 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04362 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-003 | " | Non-Converge |  |  | 0.04362 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04109 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04109 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04109 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04109 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04109 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04721 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04721 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04721 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04721 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-010 | " | Non-Converge |  |  | 0.04721 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04733 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04733 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04733 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04733 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | ASGI-2018-011 | " | Non-Converge |  |  | 0.04733 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54112 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54112 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54112 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54112 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-022 | " | Non-Converge |  |  | 0.54112 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06147 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06147 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06147 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06147 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-031 | " | Non-Converge |  |  | 0.06147 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06061 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06061 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06061 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06061 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-054 | " | Non-Converge |  |  | 0.06061 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05161 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05161 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05161 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05161 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26SP | GEN-2018-062 | " | Non-Converge |  |  | 0.05161 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-003 | " | Non-Converge |  |  | 0.04951 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-003 | " | Non-Converge |  |  | 0.04951 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-003 | " | Non-Converge |  |  | 0.04951 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-003 | " | Non-Converge |  |  | 0.04951 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-003 | " | Non-Converge |  |  | 0.04951 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-006 | " | Non-Converge |  |  | 0.04696 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-006 | " | Non-Converge |  |  | 0.04696 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-006 | " | Non-Converge |  |  | 0.04696 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-006 | " | Non-Converge |  |  | 0.04696 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-006 | " | Non-Converge |  |  | 0.04696 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-007 | " | Non-Converge |  |  | 0.03363 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-007 | " | Non-Converge |  |  | 0.03363 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-007 | " | Non-Converge |  |  | 0.03363 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-007 | " | Non-Converge |  |  | 0.03363 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-007 | " | Non-Converge |  |  | 0.03363 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-010 | " | Non-Converge |  |  | 0.05296 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-010 | " | Non-Converge |  |  | 0.05296 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-010 | " | Non-Converge |  |  | 0.05296 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-010 | " | Non-Converge |  |  | 0.05296 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-010 | " | Non-Converge |  |  | 0.05296 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-011 | " | Non-Converge |  |  | 0.05309 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-011 | " | Non-Converge |  |  | 0.05309 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-011 | " | Non-Converge |  |  | 0.05309 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-011 | " | Non-Converge |  |  | 0.05309 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | ASGI-2018-011 | " | Non-Converge |  |  | 0.05309 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-022 | " | Non-Converge |  |  | 0.54665 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-022 | " | Non-Converge |  |  | 0.54665 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-022 | " | Non-Converge |  |  | 0.54665 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-022 | " | Non-Converge |  |  | 0.54665 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-022 | " | Non-Converge |  |  | 0.54665 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-031 | " | Non-Converge |  |  | 0.06726 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-031 | " | Non-Converge |  |  | 0.06726 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-031 | " | Non-Converge |  |  | 0.06726 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-031 | " | Non-Converge |  |  | 0.06726 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-031 | " | Non-Converge |  |  | 0.06726 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | " | Non-Converge |  |  | 0.0342 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | " | Non-Converge |  |  | 0.0342 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | " | Non-Converge |  |  | 0.0342 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | " | Non-Converge |  |  | 0.0342 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Thermal | 00NR | 0 | 23SP | N/A | " | None |  |  |  |  | None
Thermal | 00NR | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 03ALL | 0 | 26L | GEN-2018-032 | " | Non-Converge |  |  | 0.0342 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-054 | " | Non-Converge |  |  | 0.06637 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-054 | " | Non-Converge |  |  | 0.06637 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-054 | " | Non-Converge |  |  | 0.06637 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-054 | " | Non-Converge |  |  | 0.06637 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-054 | " | Non-Converge |  |  | 0.06637 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-062 | " | Non-Converge |  |  | 0.05727 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26L | GEN-2018-062 | " | Non-Converge |  |  | 0.05727 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-062 | " | Non-Converge |  |  | 0.05727 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-062 | " | Non-Converge |  |  | 0.05727 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26L | GEN-2018-062 | " | Non-Converge |  |  | 0.05727 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | " | Non-Converge |  |  | 0.0481 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | " | Non-Converge |  |  | 0.0481 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | " | Non-Converge |  |  | 0.0481 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | " | Non-Converge |  |  | 0.0481 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-003 | " | Non-Converge |  |  | 0.0481 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04558 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04558 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04558 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04558 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-006 | " | Non-Converge |  |  | 0.04558 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | " | Non-Converge |  |  | 0.03174 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | " | Non-Converge |  |  | 0.03174 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | " | Non-Converge |  |  | 0.03174 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | " | Non-Converge |  |  | 0.03174 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-007 | " | Non-Converge |  |  | 0.03174 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | " | Non-Converge |  |  | 0.05171 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | " | Non-Converge |  |  | 0.05171 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | " | Non-Converge |  |  | 0.05171 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | " | Non-Converge |  |  | 0.05171 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-010 | " | Non-Converge |  |  | 0.05171 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | " | Non-Converge |  |  | 0.05182 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | " | Non-Converge |  |  | 0.05182 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | " | Non-Converge |  |  | 0.05182 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | " | Non-Converge |  |  | 0.05182 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | ASGI-2018-011 | " | Non-Converge |  |  | 0.05182 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | " | Non-Converge |  |  | 0.54564 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | " | Non-Converge |  |  | 0.54564 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | " | Non-Converge |  |  | 0.54564 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | " | Non-Converge |  |  | 0.54564 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-022 | " | Non-Converge |  |  | 0.54564 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | " | Non-Converge |  |  | 0.06598 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | " | Non-Converge |  |  | 0.06598 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | " | Non-Converge |  |  | 0.06598 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | " | Non-Converge |  |  | 0.06598 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-031 | " | Non-Converge |  |  | 0.06598 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | " | Non-Converge |  |  | 0.03287 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | " | Non-Converge |  |  | 0.03287 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | " | Non-Converge |  |  | 0.03287 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | " | Non-Converge |  |  | 0.03287 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-032 | " | Non-Converge |  |  | 0.03287 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | " | Non-Converge |  |  | 0.06509 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | " | Non-Converge |  |  | 0.06509 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | " | Non-Converge |  |  | 0.06509 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | " | Non-Converge |  |  | 0.06509 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-054 | " | Non-Converge |  |  | 0.06509 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | " | Non-Converge |  |  | 0.05611 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREACT_1
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | " | Non-Converge |  |  | 0.05611 |  | P12:345:GMO-OPPD:HOLT-NEBCITY-HOLTREA:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | " | Non-Converge |  |  | 0.05611 |  | P12:345:GMO-OPPD:S3458-HOLT:::EHV:
Thermal | 03ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None
Thermal | 03ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None
Thermal | 03ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | " | Non-Converge |  |  | 0.05611 |  | P14:345:GMO-OPPD:S3458 REACTOR:::EHV:
Non-Converge | 03ALL | 0 | 26WP | GEN-2018-062 | " | Non-Converge |  |  | 0.05611 |  | P45:345:OPPD:S3455-S3761&T3:::EHV:
Non-Converge | 03NR | 0 | 26L | N/A | " | None |  |  |  |  | None
Non-Converge | 04ALL | 0 | 26WP | N/A | " | None |  |  |  |  | None
Non-Converge | 04ALL | 0 | 26L | N/A | " | None |  |  |  |  | None
Non-Converge | 04ALL | 0 | 23SP | N/A | " | None |  |  |  |  | None
Non-Converge | 04ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 04NR | 0 | 26L | N/A | " | None |  |  |  |  | None
Non-Converge | 05ALL | 0 | 26WP | N/A | " | None |  |  |  |  | None
Non-Converge | 05ALL | 0 | 26L | N/A | " | None |  |  |  |  | None
Non-Converge | 05ALL | 0 | 23SP | N/A | " | None |  |  |  |  | None
Non-Converge | 05ALL | 0 | 26SP | N/A | " | None |  |  |  |  | None
Non-Converge | 05NR | 0 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 01ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 01NR | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 02ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 02NR | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 03NR | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.46058 | 107.13 | 508054 BANN 4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.46058 | 105.86 | P12:138:AEPW:IPC-DOM4:BANN4
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.44803 | 105.84 | P13:138-345:AEPW:WILKES 4
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.43862 | 105.22 | 508053 BANN 2 69.0 508063 LSORDTP2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.46058 | 104.78 | 508060 IPC-DOM4 138 508075 REDSPRG4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.46058 | 104.57 | 508059 IPC T 4 138 508060 IPC-DOM4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.43862 | 104.53 | 508057 HOOKS 2 69.0 508063 LSORDTP2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.45106 | 104.23 | P12:HV:EES::OKAY 4:TURK 4%:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.45106 | 104.23 | P12:138:AEPW:OKAY4:TURK4
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.45747 | 103.07 | P12:345:AEPW:LYDIA7:WELSH7
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.43862 | 102.35 | 508057 HOOKS 2 69.0 508074 REDRVR-2 69.0 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.45092 | 101.43 | 507402 ASHDWNR4 138 507428 OKAY 4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.45092 | 101.11 | P12:138:AEPW:PATTERS4:OKAY4
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.45092 | 101.01 | P12:HV:EES::ASHDWNR4:PATTERS4!:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.45832 | 100.43 | P12:345:AEPW:WELSH7:WILKES7
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.45006 | 100.19 | P12:138:AEPW:PATTERS4:NWTXARK4
Thermal | 04ALL | 1 | 23SP | GEN-2018-003 | FROM -> TO | 508069 NNBOSTN4 138 762431 G18-003-TAP 138 1 |  | 153 | 0.45006 | 100.19 | P12:HV:EES::PATTERS4!:NWTXARK4:1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29591 | 118.8 | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29427 | 115.74 | 509783 R.S.S.-4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29591 | 115.46 | 509849 ORU ETP4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29427 | 113.17 | 509813 SHILETP4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29591 | 111.41 | P12:138:AEPW:R.S.S.-4:R:96YALE-4
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29427 | 110.28 | 509809 81YALTP4 138 509813 SHILETP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29591 | 109.86 | 509847 96YALE-4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29427 | 107.24 | 509764 WRNMEDT4 138 509809 81YALTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29427 | 106.02 | P12:138:AEPW:R.S.S.-4:S.HUD.-4
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29427 | 104.01 | 509764 WRNMEDT4 138 509833 S.HUD.-4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29591 | 103.69 | 509766 77MEM-W4 138 509847 96YALE-4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29591 | 100.97 | P12:138:AEPW:E.61ST-4:96YALE-4
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29591 | 100.37 | 509766 77MEM-W4 138 509831 E.61ST-4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29266 | 118.56 | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29099 | 115.45 | 509783 R.S.S.-4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29266 | 115.17 | 509849 ORU ETP4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29099 | 112.86 | 509813 SHILETP4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29266 | 110.93 | P12:138:AEPW:R.S.S.-4:R:96YALE-4
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29099 | 109.92 | 509809 81YALTP4 138 509813 SHILETP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29266 | 109.45 | 509847 96YALE-4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29099 | 106.83 | 509764 WRNMEDT4 138 509809 81YALTP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29099 | 105.56 | P12:138:AEPW:R.S.S.-4:S.HUD.-4
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29099 | 103.64 | 509764 WRNMEDT4 138 509833 S.HUD.-4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29266 | 103.11 | 509766 77MEM-W4 138 509847 96YALE-4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509800 36LEWIS4 138 1 |  | 278 | 0.29266 | 100.28 | P12:138:AEPW:E.61ST-4:96YALE-4
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 | 0.29591 | 105.9 | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 | 0.29427 | 102.77 | 509783 R.S.S.-4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 | 0.29591 | 102.55 | 509849 ORU ETP4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 1 | 23SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 | 0.29427 | 100.2 | 509813 SHILETP4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 | 0.29266 | 105.82 | 509783 R.S.S.-4 138 509849 ORU ETP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 | 0.29099 | 102.61 | 509783 R.S.S.-4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 | 0.29266 | 102.41 | 509849 ORU ETP4 138 509858 WARNTAP4 138 1
Thermal | 04ALL | 1 | 26SP | GEN-2018-027 | FROM -> TO | 509776 52DELTP4 138 509811 T.S.E.-4 138 1 |  | 278 | 0.29099 | 100.02 | 509813 SHILETP4 138 509853 ORU-WTP4 138 1
Thermal | 04ALL | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 04NR | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 23SP | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 26L | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 26SP | N/A | " | None |  |  |  |  | None
Thermal | 05ALL | 1 | 26WP | N/A | " | None |  |  |  |  | None
Thermal | 05NR | 1 | 26L | N/A | " | None |  |  |  |  | None

## All Voltage
SOLUTIONTYPE | GROUP | SCENARIO | SEASON | SOURCE | MONTCOMMONNAME | BC VOLTAGE | TC VOLTAGE | VOLTAGE DIFF | VINIT | VMIN | VMAX | TDF | CONTNAME
Voltage | 00NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 01ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 01NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 02ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 02NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 03ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 03NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 04ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 04NR | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 05ALL | 2 | N/A | N/A | None | [7 empty] | None
Voltage | 05NR | 2 | N/A | N/A | None | [7 empty] | None

## Stability Analysis Results
Group | Season | Model Dispatch | Event ID | Event Description | Event Category | Rotor Angle Stability | Transient Voltage Response > 0.7 p.u. | Transient Voltage Response < 1.2 p.u. | Post Fault Steady State Voltage > 0.9 p.u. | Post Fault Steady State Voltage < 1.1 p.u. | Damping Factor > 0.8 % | Low Voltage Rides Through | Violation Summary | Primary Mitigation | Alternate Mitigation | Alternate Mitigation2 (Informational)
01 - North | 25S | Transfer | GROUP1_FAULT_1 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_2 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_3 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_4 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_5 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_6 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_7 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_8 | 3 Phase fault on ELLENDL4 230.00 (661026) 230 kV Bus a. Apply fault at the ELLENDL4 230.00 (661026) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_9 | 3 Phase fault on MERRCRT4 230.00 (661093) 230 kV Bus a. Apply fault at the MERRCRT4 230.00 (661093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRCRT4 (661093) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_10 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_11 | 3 Phase fault on KENMARE7 115.00 (661052) 115 kV Bus a. Apply fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_12 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_13 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_14 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_15 | 3 Phase fault on KENMARE7 115.00 (661052) 115 kV Bus a. Apply fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_16 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_17 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_18 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_19 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to MAPLE R4 (657754) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_20 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_21 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_22 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_23 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_24 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_25 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_26 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_27 | 3 Phase fault on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_28 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_29 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to COYOTE 3 (661016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_30 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_31 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE6 9 (605730) 13.8 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_32 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_33 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_34 | 3 Phase fault on GRE-COALFB14230.00 (615604) 230 kV Bus a. Apply fault at the GRE-COALFB14230.00 (615604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB14 (615604) 230.0 kV Fixed Shunt Device #bp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_35 | 3 Phase fault on GRE-COALFB14230.00 (615604) 230 kV Bus a. Apply fault at the GRE-COALFB14230.00 (615604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB14 (615604) 230.0 kV Fixed Shunt Device #hp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_36 | 3 Phase fault on GRE-COALFB24230.00 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24230.00 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Fixed Shunt Device #bp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_37 | 3 Phase fault on GRE-COALFB24230.00 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24230.00 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Fixed Shunt Device #hp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_38 | 3 Phase fault on GRE-COALFB24230.00 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24230.00 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_39 | 3 Phase fault on GRE-COALFB34230.00 (615606) 230 kV Bus a. Apply fault at the GRE-COALFB34230.00 (615606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB34 (615606) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_40 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_41 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_42 | 3 Phase fault on CNTSHNT3 345.00 (657951) 345 kV Bus a. Apply fault at the CNTSHNT3 345.00 (657951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_43 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1456 POI (44568) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_44 | 3 Phase fault on JAMETAP7 115.00 (620273) 115 kV Bus a. Apply fault at the JAMETAP7 115.00 (620273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.2. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.3. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.4. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_45 | 3 Phase fault on AVIKO 7 115.00 (620271) 115 kV Bus a. Apply fault at the AVIKO 7 115.00 (620271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.2. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_46 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_47 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_48 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_49 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_50 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_51 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_52 | 3 Phase fault on BARLOW -CP7115.00 (655610) 115 kV Bus a. Apply fault at the BARLOW -CP7115.00 (655610) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_53 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT9 (620167) 41.6 kV to PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV Three Winding #1 b.5. PICKERT8 (657923) 69.0 kV to PICKERT4 (657759) 230.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_54 | 3 Phase fault on ENDERLIN 7 115.00 (652638) 115 kV Bus a. Apply fault at the ENDERLIN 7 115.00 (652638) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_55 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_56 | 3 Phase fault on DICKEYTP-CP869.000 (655625) 69 kV Bus a. Apply fault at the DICKEYTP-CP869.000 (655625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.3. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_57 | 3 Phase fault on OMEGATAP-CP869.000 (655626) 69 kV Bus a. Apply fault at the OMEGATAP-CP869.000 (655626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.2. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 b.3. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_58 | 3 Phase fault on LAMOURTP-CP869.000 (655627) 69 kV Bus a. Apply fault at the LAMOURTP-CP869.000 (655627) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 b.2. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 b.3. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_59 | 3 Phase fault on WESTOAKS-CP869.000 (655628) 69 kV Bus a. Apply fault at the WESTOAKS-CP869.000 (655628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 b.2. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 b.3. NRTHOAKS-CP8 (655629) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_60 | 3 Phase fault on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENASTON-BE7 (659308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_61 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_62 | 3 Phase fault on FARMVL_T-MW7115.00 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7115.00 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.3. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_63 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_64 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_65 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_66 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_67 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_68 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_69 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_70 | 3 Phase fault on EDGELEY8 69.000 (652433) 69 kV Bus a. Apply fault at the EDGELEY8 69.000 (652433) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. FORMAN 8 (652439) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_71 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.3. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_72 | 3 Phase fault on ABERDN JCT 7115.00 (660000) 115 kV Bus a. Apply fault at the ABERDN JCT 7115.00 (660000) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_73 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_74 | 3 Phase fault on HURON WPARK7115.00 (660003) 115 kV Bus a. Apply fault at the HURON WPARK7115.00 (660003) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON WPARK7 (660003) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_75 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_76 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_77 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_78 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_79 | 3 Phase fault on BLAISDEL-BE7115.00 (659144) 115 kV Bus a. Apply fault at the BLAISDEL-BE7115.00 (659144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_80 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_81 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_82 | 3 Phase fault on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_83 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_84 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_85 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_86 | 3 Phase fault on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC7 (652454) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_87 | 3 Phase fault on JAMESTN7 115.00 (652445) 115 kV Bus a. Apply fault at the JAMESTN7 115.00 (652445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN7 (652445) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_88 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_89 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_90 | 3 Phase fault on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_91 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_92 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_93 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_94 | 3 Phase fault on NORMANLK-BD7115.00 (655780) 115 kV Bus a. Apply fault at the NORMANLK-BD7115.00 (655780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORMANLK-BD7 (655780) 115.0 kV to LINDAHLS-MW7 (655910) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_95 | 3 Phase fault on MOE -MW7115.00 (655900) 115 kV Bus a. Apply fault at the MOE -MW7115.00 (655900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.2. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 b.4. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 b.5. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.6. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.7. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_96 | 3 Phase fault on PALERMO -MW7115.00 (655916) 115 kV Bus a. Apply fault at the PALERMO -MW7115.00 (655916) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_97 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_98 | 3 Phase fault on ROSEGLEN-CP7115.00 (655662) 115 kV Bus a. Apply fault at the ROSEGLEN-CP7115.00 (655662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLS.C-CP7 (655661) 115.0 kV to ROSEGLEN-CP7 (655662) 115.0 kV Transmission Circuit #1 b.2. ROSEGLEN-CP7 (655662) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.3. RAUB TAP-CP7 (655663) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 b.4. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_99 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN-LNX3 (652829) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_100 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_101 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_102 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_103 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_104 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_105 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_106 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_107 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_108 | 3 Phase fault on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_109 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_110 | 3 Phase fault on SATTER -MW7115.00 (655967) 115 kV Bus a. Apply fault at the SATTER -MW7115.00 (655967) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATTER -MW7 (655967) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_111 | 3 Phase fault on JAMESPK9 41.600 (620172) 41.59999847 kV Bus a. Apply fault at the JAMESPK9 41.600 (620172) 41.59999847 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESPK9 (620172) 41.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_112 | 3 Phase fault on JAMESPK9 41.600 (620172) 41.59999847 kV Bus a. Apply fault at the JAMESPK9 41.600 (620172) 41.59999847 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESPK9 (620172) 41.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_113 | 3 Phase fault on ANTELP_1-BEG23.000 (659103) 23 kV Bus a. Apply fault at the ANTELP_1-BEG23.000 (659103) 23 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELP_1-BEG (659103) 23.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_114 | 3 Phase fault on ANTELP_2-BEG23.000 (659107) 23 kV Bus a. Apply fault at the ANTELP_2-BEG23.000 (659107) 23 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELP_2-BEG (659107) 23.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_115 | 3 Phase fault on LELAND_1-BEG22.000 (659110) 22 kV Bus a. Apply fault at the LELAND_1-BEG22.000 (659110) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_1-BEG (659110) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_116 | 3 Phase fault on LELAND_2-BEG20.000 (659111) 20 kV Bus a. Apply fault at the LELAND_2-BEG20.000 (659111) 20 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_2-BEG (659111) 20.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_117 | 3 Phase fault on GROTON_2-BEG13.800 (659272) 13.80000019 kV Bus a. Apply fault at the GROTON_2-BEG13.800 (659272) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON_2-BEG (659272) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_118 | 3 Phase fault on GROTON_1-BEG13.800 (659274) 13.80000019 kV Bus a. Apply fault at the GROTON_1-BEG13.800 (659274) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON_1-BEG (659274) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_119 | 3 Phase fault on POMONA__-PPW0.6900 (659290) 0.689999998 kV Bus a. Apply fault at the POMONA__-PPW0.6900 (659290) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POMONA__-PPW (659290) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_120 | 3 Phase fault on BEPCPXCTG1X218.000 (659581) 18 kV Bus a. Apply fault at the BEPCPXCTG1X218.000 (659581) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEPCPXCTG1X2 (659581) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_121 | 3 Phase fault on BEPCPXCTG2X218.000 (659582) 18 kV Bus a. Apply fault at the BEPCPXCTG2X218.000 (659582) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEPCPXCTG2X2 (659582) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_122 | 3 Phase fault on AS17-013GEN10.6900 (762353) 0.689999998 kV Bus a. Apply fault at the AS17-013GEN10.6900 (762353) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AS17-013GEN1 (762353) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_123 | 3 Phase fault on G18-010-GEN10.6300 (762485) 0.629999995 kV Bus a. Apply fault at the G18-010-GEN10.6300 (762485) 0.629999995 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-010-GEN1 (762485) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_124 | 3 Phase fault on G18-008-GEN10.6900 (762540) 0.689999998 kV Bus a. Apply fault at the G18-008-GEN10.6900 (762540) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-008-GEN1 (762540) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_125 | 3 Phase fault on G18-039GEN1 0.6600 (762738) 0.660000026 kV Bus a. Apply fault at the G18-039GEN1 0.6600 (762738) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-039GEN1 (762738) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_126 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_127 | 3 Phase fault on SQBP1DC4 230.00 (608597) 230 kV Bus a. Apply fault at the SQBP1DC4 230.00 (608597) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBP1DC4 (608597) 230.0 kV to SQBEAST4 (608602) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_128 | 3 Phase fault on SQBP2DC4 230.00 (608599) 230 kV Bus a. Apply fault at the SQBP2DC4 230.00 (608599) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBP2DC4 (608599) 230.0 kV to SQBEAST4 (608602) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_129 | 3 Phase fault on VALLEYC8 69.000 (652204) 69 kV Bus a. Apply fault at the VALLEYC8 69.000 (652204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC8 (652204) 69.0 kV to MPC-VCY8 (657804) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_130 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_131 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_132 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_133 | 3 Phase fault on HURON 8 69.000 (652284) 69 kV Bus a. Apply fault at the HURON 8 69.000 (652284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to SW-HURN2-ER8 (655066) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_134 | 3 Phase fault on HURON 8 69.000 (652284) 69 kV Bus a. Apply fault at the HURON 8 69.000 (652284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to SW-HURN3-ER8 (655067) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_135 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_136 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_137 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_138 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_139 | 3 Phase fault on CARNGTN7 115.00 (652428) 115 kV Bus a. Apply fault at the CARNGTN7 115.00 (652428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_140 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_141 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_142 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_143 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_144 | 3 Phase fault on JAMESTN7 115.00 (652445) 115 kV Bus a. Apply fault at the JAMESTN7 115.00 (652445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_145 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_146 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_147 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_148 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_149 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_150 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_151 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_152 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_153 | 3 Phase fault on MOS-MILR-ER869.000 (655053) 69 kV Bus a. Apply fault at the MOS-MILR-ER869.000 (655053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-MILR-ER8 (655053) 69.0 kV to SW-HURN4-ER8 (655064) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_154 | 3 Phase fault on MOS-HRON-ER869.000 (655058) 69 kV Bus a. Apply fault at the MOS-HRON-ER869.000 (655058) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-HRON-ER8 (655058) 69.0 kV to HURON-ER8 (655231) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_155 | 3 Phase fault on SW-HURN4-ER869.000 (655064) 69 kV Bus a. Apply fault at the SW-HURN4-ER869.000 (655064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-HURN4-ER8 (655064) 69.0 kV to SW-HURN2-ER8 (655066) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_156 | 3 Phase fault on MOS-YLTI-ER869.000 (655065) 69 kV Bus a. Apply fault at the MOS-YLTI-ER869.000 (655065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-YLTI-ER8 (655065) 69.0 kV to MORNINGS-ER8 (655236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_157 | 3 Phase fault on SW-HURN3-ER869.000 (655067) 69 kV Bus a. Apply fault at the SW-HURN3-ER869.000 (655067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-HURN3-ER8 (655067) 69.0 kV to MORNINGS-ER8 (655236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_158 | 3 Phase fault on MOS-WOLS-ER869.000 (655069) 69 kV Bus a. Apply fault at the MOS-WOLS-ER869.000 (655069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-WOLS-ER8 (655069) 69.0 kV to VIRGIL-ER8 (655241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_159 | 3 Phase fault on MOS-VRCV-ER869.000 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER869.000 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to MOS-DAK-ER8 (655071) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_160 | 3 Phase fault on MOS-VRCV-ER869.000 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER869.000 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to VIRGIL-ER8 (655241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_161 | 3 Phase fault on MOS-VRCV-ER869.000 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER869.000 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to CAVOUR-ER8 (655242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_162 | 3 Phase fault on MOS-DAK-ER8 69.000 (655071) 69 kV Bus a. Apply fault at the MOS-DAK-ER8 69.000 (655071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-DAK-ER8 (655071) 69.0 kV to DAKOTA-ER8 (655244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_163 | 3 Phase fault on MOS-CLRM-ER869.000 (655082) 69 kV Bus a. Apply fault at the MOS-CLRM-ER869.000 (655082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CLRM-ER8 (655082) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_164 | 3 Phase fault on MOS-SWAB-ER869.000 (655085) 69 kV Bus a. Apply fault at the MOS-SWAB-ER869.000 (655085) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-SWAB-ER8 (655085) 69.0 kV to BATH-ER8 (655269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_165 | 3 Phase fault on MOS-IPAB-ER869.000 (655086) 69 kV Bus a. Apply fault at the MOS-IPAB-ER869.000 (655086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-IPAB-ER8 (655086) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_166 | 3 Phase fault on MOS-ABDN-ER869.000 (655087) 69 kV Bus a. Apply fault at the MOS-ABDN-ER869.000 (655087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ABDN-ER8 (655087) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_167 | 3 Phase fault on SW-IPABD-ER869.000 (655089) 69 kV Bus a. Apply fault at the SW-IPABD-ER869.000 (655089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-IPABD-ER8 (655089) 69.0 kV to IPABRDEN-ER8 (655264) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_168 | 3 Phase fault on SW-IPABD-ER869.000 (655089) 69 kV Bus a. Apply fault at the SW-IPABD-ER869.000 (655089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-IPABD-ER8 (655089) 69.0 kV to BATH-ER8 (655269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_169 | 3 Phase fault on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_170 | 3 Phase fault on BATH-ER8 69.000 (655269) 69 kV Bus a. Apply fault at the BATH-ER8 69.000 (655269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATH-ER8 (655269) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_171 | 3 Phase fault on BERTHOLD-CP7115.00 (655641) 115 kV Bus a. Apply fault at the BERTHOLD-CP7115.00 (655641) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_172 | 3 Phase fault on PLSNTV_T-MW7115.00 (655902) 115 kV Bus a. Apply fault at the PLSNTV_T-MW7115.00 (655902) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to PLSNTVAL-MW7 (655913) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_173 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to AUSTIN -MW7 (655912) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_174 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_175 | 3 Phase fault on W.BANK__-MW7115.00 (655922) 115 kV Bus a. Apply fault at the W.BANK__-MW7115.00 (655922) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_176 | 3 Phase fault on TWELVE_M-MW7115.00 (655939) 115 kV Bus a. Apply fault at the TWELVE_M-MW7115.00 (655939) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_177 | 3 Phase fault on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV to BLAISDEL-MW7 (655949) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_178 | 3 Phase fault on BLAISDEL-MW7115.00 (655949) 115 kV Bus a. Apply fault at the BLAISDEL-MW7115.00 (655949) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_179 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_180 | 3 Phase fault on W.BANK_T-MW7115.00 (655953) 115 kV Bus a. Apply fault at the W.BANK_T-MW7115.00 (655953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK_T-MW7 (655953) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_181 | 3 Phase fault on HESSRAIL-MW7115.00 (655961) 115 kV Bus a. Apply fault at the HESSRAIL-MW7115.00 (655961) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESSRAIL-MW7 (655961) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_182 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_183 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_184 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_185 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_186 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_187 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_188 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_189 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_190 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_191 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_192 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_193 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_194 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_195 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_196 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_197 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_198 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_199 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_200 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_201 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_202 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_203 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_204 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_205 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_206 | 3 Phase fault on BD 4230.00 (672601) 230 kV Bus a. Apply fault at the BD 4230.00 (672601) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BD 4 (672601) 230.0 kV to SHAND 4 (672621) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_207 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_208 | 3 Phase fault on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC8 (652204) 69.0 kV to VALLEYC7 (652454) 115.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_209 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_210 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_211 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_212 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_213 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_214 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_215 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_216 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_217 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_218 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_219 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_220 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_221 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_222 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_223 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_224 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_225 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_226 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_227 | 3 Phase fault on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_228 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_229 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_230 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_231 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_232 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_233 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_234 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_235 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_236 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_237 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE8 (659198) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_238 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_239 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_240 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_241 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_242 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_243 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_244 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_245 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_246 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_247 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_248 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_249 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_250 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_251 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_252 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_253 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_254 | 3 Phase fault on ELLENDL345 3345.00 (661097) 345 kV Bus a. Apply fault at the ELLENDL345 3345.00 (661097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELLENDL345 3 (661097) 345.0 kV to ELLENDL345 4 (661098) 230.0 kV to ELLENDL345 9 (661907) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_255 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_256 | 3 Phase fault on BDV 4230.00 (672603) 230 kV Bus a. Apply fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_257 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_258 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_259 | 3 Phase fault on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_260 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_261 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_262 | 3 Phase fault on ELLENDL345 4230.00 (661098) 230 kV Bus a. Apply fault at the ELLENDL345 4230.00 (661098) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLENDL345 4 (661098) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_1 | Single Phase Fault with Stuck Breaker on ELLENDL4 230.00 (661026) 230 kV Bus a. Apply Fault at the ELLENDL4 230.00 (661026) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_2 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_3 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_4 | Single Phase Fault with Stuck Breaker on OAKES 4 230.00 (620362) 230 kV Bus a. Apply Fault at the OAKES 4 230.00 (620362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_5 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_6 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_7 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_8 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_9 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_10 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_11 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_12 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.9. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.10. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_13 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_14 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to GEN-2018-039 (762735) 115.0 kV Transmission Circuit #1 b.5. EDGELEY9 (652322) 41.8 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.6. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_15 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 b.6. LEEDS 7 (652447) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_16 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 b.6. DEVILSE7 (620265) 115.0 kV to DEVIL J7 (620267) 115.0 kV Transmission Circuit #1 b.7. DEVIL J7 (620267) 115.0 kV to DEVIL S7 (620268) 115.0 kV Transmission Circuit #1 b.8. DEVILSE7 (620265) 115.0 kV to RAMSEY 7 (620266) 115.0 kV Transmission Circuit #1 b.9. DEVILSE7 (620265) 115.0 kV to SWEETWA7 (657720) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_17 | Single Phase Fault with Stuck Breaker on CULB_GEN-BE7115.00 (659269) 115 kV Bus a. Apply Fault at the CULB_GEN-BE7115.00 (659269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.10. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_18 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_19 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_20 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_21 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_22 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_23 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_24 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_25 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_26 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_27 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.10. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.11. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_28 | Single Phase Fault with Stuck Breaker on ENDERLIN 7 115.00 (652638) 115 kV Bus a. Apply Fault at the ENDERLIN 7 115.00 (652638) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_29 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.5. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_30 | Single Phase Fault with Stuck Breaker on ENDERLIN 7 115.00 (652638) 115 kV Bus a. Apply Fault at the ENDERLIN 7 115.00 (652638) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_31 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.5. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_32 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_33 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_34 | Single Phase Fault with Stuck Breaker on ECKLUND_-PP4230.00 (659284) 230 kV Bus a. Apply Fault at the ECKLUND_-PP4230.00 (659284) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_35 | Single Phase Fault with Stuck Breaker on ECKLUND_-PP4230.00 (659284) 230 kV Bus a. Apply Fault at the ECKLUND_-PP4230.00 (659284) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_36 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_37 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_38 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_39 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.5. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.6. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_40 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.5. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.6. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_41 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.5. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.6. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_42 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_43 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_44 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_45 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_46 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_47 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_48 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_49 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_50 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_51 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_52 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_53 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_54 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_55 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_56 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_57 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_58 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_59 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 b.6. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_60 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_61 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_62 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_63 | Single Phase Fault with Stuck Breaker on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_64 | Single Phase Fault with Stuck Breaker on DAKOTACCESS7115.00 (660040) 115 kV Bus a. Apply Fault at the DAKOTACCESS7115.00 (660040) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDFIELD 7 (660002) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.2. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_65 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_66 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_67 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_68 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_69 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_70 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_71 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_72 | Single Phase Fault with Stuck Breaker on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_73 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to GEN-2018-039 (762735) 115.0 kV Transmission Circuit #1 b.5. EDGELEY9 (652322) 41.8 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.6. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_74 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_75 | Single Phase Fault with Stuck Breaker on GARRISN7 115.00 (652442) 115 kV Bus a. Apply Fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_76 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_77 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_78 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_79 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_80 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_81 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_82 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_83 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_84 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_85 | Single Phase Fault with Stuck Breaker on CARNGTN7 115.00 (652428) 115 kV Bus a. Apply Fault at the CARNGTN7 115.00 (652428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.3. CARNGTN9 (652321) 41.8 kV to CARNGTN7 (652428) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_86 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_87 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_88 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_89 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.4. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_90 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_91 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_92 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_93 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_94 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_95 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_96 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_97 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.11. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_98 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_99 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.7. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_100 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_101 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_102 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_103 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_104 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_105 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_106 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_107 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_108 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_109 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.3. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.4. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.5. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_110 | Single Phase Fault with Stuck Breaker on SUMMIT-7 115.00 (652522) 115 kV Bus a. Apply Fault at the SUMMIT-7 115.00 (652522) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.3. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. SUMMIT-7 (652522) 115.0 kV to GEN-2018-007 (762449) 115.0 kV Two Winding #1 b.5. SUMMIT-8 (652209) 69.0 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 b.6. SUMMIT-9 (652326) 43.8 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_111 | Single Phase Fault with Stuck Breaker on SUMMIT-7 115.00 (652522) 115 kV Bus a. Apply Fault at the SUMMIT-7 115.00 (652522) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.3. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. SUMMIT-7 (652522) 115.0 kV to GEN-2018-007 (762449) 115.0 kV Two Winding #1 b.5. SUMMIT-8 (652209) 69.0 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 b.6. SUMMIT-9 (652326) 43.8 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_112 | Single Phase Fault with Stuck Breaker on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_113 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_114 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_115 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_116 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_117 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_118 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_119 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_120 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_121 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_122 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_123 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_124 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_125 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_126 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_127 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_128 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_129 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_130 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_131 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_132 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_133 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_134 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_135 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_136 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_137 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_138 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_139 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_140 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_141 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_142 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_143 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_144 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_145 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_146 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_147 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_148 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_149 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_150 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_151 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_152 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_153 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_154 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_155 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_156 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_157 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_158 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_159 | Single Phase Fault with Stuck Breaker on GARRISN7 115.00 (652442) 115 kV Bus a. Apply Fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_160 | Single Phase Fault with Stuck Breaker on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_161 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.6. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_162 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_163 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.5. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.6. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.7. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.8. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.9. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_164 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.5. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_165 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.5. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_166 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_167 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_168 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_169 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_170 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_171 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_172 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_173 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_174 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_175 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_176 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_177 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.6. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_178 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_179 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_180 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_181 | Single Phase Fault with Stuck Breaker on ELLIOTT7 115.00 (652462) 115 kV Bus a. Apply Fault at the ELLIOTT7 115.00 (652462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_182 | Single Phase Fault with Stuck Breaker on ELLIOTT7 115.00 (652462) 115 kV Bus a. Apply Fault at the ELLIOTT7 115.00 (652462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_183 | Single Phase Fault with Stuck Breaker on ELLIOTT7 115.00 (652462) 115 kV Bus a. Apply Fault at the ELLIOTT7 115.00 (652462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_184 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_185 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_186 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.7. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_187 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_188 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_189 | Single Phase Fault with Stuck Breaker on GRNDFKS4 230.00 (652437) 230 kV Bus a. Apply Fault at the GRNDFKS4 230.00 (652437) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_190 | Single Phase Fault with Stuck Breaker on GRNDFKS4 230.00 (652437) 230 kV Bus a. Apply Fault at the GRNDFKS4 230.00 (652437) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_191 | Single Phase Fault with Stuck Breaker on GRNDFKS4 230.00 (652437) 230 kV Bus a. Apply Fault at the GRNDFKS4 230.00 (652437) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_192 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_193 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_194 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_195 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_196 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_197 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_198 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_199 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.5. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.6. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_200 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_201 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_202 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_203 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_204 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_205 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_206 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_207 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_208 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_209 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_210 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_211 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_212 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_213 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_214 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_215 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_216 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_217 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_218 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_219 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_220 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_221 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_222 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_223 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_224 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_225 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_226 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_227 | Single Phase Fault with Stuck Breaker on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply Fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_228 | Single Phase Fault with Stuck Breaker on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply Fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_229 | Single Phase Fault with Stuck Breaker on TWELVE_M-MW7115.00 (655939) 115 kV Bus a. Apply Fault at the TWELVE_M-MW7115.00 (655939) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to SLETTE -MW7 (655964) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_230 | Single Phase Fault with Stuck Breaker on TWELVE_M-MW7115.00 (655939) 115 kV Bus a. Apply Fault at the TWELVE_M-MW7115.00 (655939) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to SLETTE -MW7 (655964) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_231 | Single Phase Fault with Stuck Breaker on TWELVE_M-MW7115.00 (655939) 115 kV Bus a. Apply Fault at the TWELVE_M-MW7115.00 (655939) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to SLETTE -MW7 (655964) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_232 | Single Phase Fault with Stuck Breaker on EPPING -MW7115.00 (655959) 115 kV Bus a. Apply Fault at the EPPING -MW7115.00 (655959) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_233 | Single Phase Fault with Stuck Breaker on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply Fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.2. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.4. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.5. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.6. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.7. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_234 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 b.4. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_235 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_236 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_237 | Single Phase Fault with Stuck Breaker on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply Fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.3. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_238 | Single Phase Fault with Stuck Breaker on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply Fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.3. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.4. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.5. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_239 | Single Phase Fault with Stuck Breaker on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply Fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.2. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.3. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_240 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_241 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_242 | Single Phase Fault with Stuck Breaker on NORMANLK-BD7115.00 (655780) 115 kV Bus a. Apply Fault at the NORMANLK-BD7115.00 (655780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMANLK-BD7 (655780) 115.0 kV to LARSON -BD7 (655781) 115.0 kV Transmission Circuit #1 b.2. NORMANLK-BD7 (655780) 115.0 kV to LINDAHLS-MW7 (655910) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_243 | Single Phase Fault with Stuck Breaker on NORMANLK-BD7115.00 (655780) 115 kV Bus a. Apply Fault at the NORMANLK-BD7115.00 (655780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMANLK-BD7 (655780) 115.0 kV to LARSON -BD7 (655781) 115.0 kV Transmission Circuit #1 b.2. NORMANLK-BD7 (655780) 115.0 kV to LINDAHLS-MW7 (655910) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_244 | Single Phase Fault with Stuck Breaker on LINDAHLS-MW7115.00 (655910) 115 kV Bus a. Apply Fault at the LINDAHLS-MW7115.00 (655910) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINDAHLS-MW7 (655910) 115.0 kV to SIMPSON -MW7 (655911) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_245 | Single Phase Fault with Stuck Breaker on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply Fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.2. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.3. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_246 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_247 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_248 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_249 | Single Phase Fault with Stuck Breaker on CARNGTN7 115.00 (652428) 115 kV Bus a. Apply Fault at the CARNGTN7 115.00 (652428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.3. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.4. CARNGTN9 (652321) 41.8 kV to CARNGTN7 (652428) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_250 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_251 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_252 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_253 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_254 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_255 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_256 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_257 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_258 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_259 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.7. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_260 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_261 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_262 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_263 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_264 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_265 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_266 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_267 | Single Phase Fault with Stuck Breaker on NBCS_10_-PPR12.500 (659278) 12.5 kV Bus a. Apply Fault at the NBCS_10_-PPR12.500 (659278) 12.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. NBCS_10_-PPR (659278) 12.5 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_268 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_269 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_270 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_271 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_272 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_273 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_274 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.5. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_275 | Single Phase Fault with Stuck Breaker on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply Fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 b.2. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_276 | Single Phase Fault with Stuck Breaker on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply Fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_277 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_278 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_279 | Single Phase Fault with Stuck Breaker on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply Fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBP2DC4 (608599) 230.0 kV Transmission Circuit #z1 b.2. SQBEAST4 (608602) 230.0 kV to SQBP1DC4 (608597) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_280 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_281 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_282 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY8 (652433) 69.0 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 b.2. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_283 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z b.2. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_284 | Single Phase Fault with Stuck Breaker on MOS-IPAB-ER869.000 (655086) 69 kV Bus a. Apply Fault at the MOS-IPAB-ER869.000 (655086) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-IPAB-ER8 (655086) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 b.2. MOS-IPAB-ER8 (655086) 69.0 kV to SW-IPABD-ER8 (655089) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_285 | Single Phase Fault with Stuck Breaker on MOS-ABDN-ER869.000 (655087) 69 kV Bus a. Apply Fault at the MOS-ABDN-ER869.000 (655087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-ABDN-ER8 (655087) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 b.2. MOS-ABDN-ER8 (655087) 69.0 kV to MCSINCRK-ER8 (655516) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_286 | Single Phase Fault with Stuck Breaker on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply Fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 b.2. ABERDEEN-ER8 (655262) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_287 | Single Phase Fault with Stuck Breaker on DICKEYTP-CP869.000 (655625) 69 kV Bus a. Apply Fault at the DICKEYTP-CP869.000 (655625) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to EDGELEY8 (652433) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_288 | Single Phase Fault with Stuck Breaker on OMEGATAP-CP869.000 (655626) 69 kV Bus a. Apply Fault at the OMEGATAP-CP869.000 (655626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMEGATAP-CP8 (655626) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_289 | Single Phase Fault with Stuck Breaker on MAKOTI -CP7115.00 (655664) 115 kV Bus a. Apply Fault at the MAKOTI -CP7115.00 (655664) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAKOTI -CP7 (655664) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.2. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_290 | Single Phase Fault with Stuck Breaker on PLSNTV_T-MW7115.00 (655902) 115 kV Bus a. Apply Fault at the PLSNTV_T-MW7115.00 (655902) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to MOE -MW7 (655900) 115.0 kV Transmission Circuit #1 b.2. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_291 | Single Phase Fault with Stuck Breaker on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply Fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN -MW7 (655904) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_292 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_293 | Single Phase Fault with Stuck Breaker on W.BANK__-MW7115.00 (655922) 115 kV Bus a. Apply Fault at the W.BANK__-MW7115.00 (655922) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 b.2. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_294 | Single Phase Fault with Stuck Breaker on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply Fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLAZA -MW7 (655944) 115.0 kV to PARSHALL-MW7 (655908) 115.0 kV Transmission Circuit #1 b.2. PLAZA -MW7 (655944) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_295 | Single Phase Fault with Stuck Breaker on BLAISDEL-MW7115.00 (655949) 115 kV Bus a. Apply Fault at the BLAISDEL-MW7115.00 (655949) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 b.2. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_296 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_297 | Single Phase Fault with Stuck Breaker on W.BANK_T-MW7115.00 (655953) 115 kV Bus a. Apply Fault at the W.BANK_T-MW7115.00 (655953) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.BANK_T-MW7 (655953) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #1 b.2. W.BANK_T-MW7 (655953) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_298 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_299 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_300 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE7115.00 (659141) 115 kV Bus a. Apply Fault at the NRTSHORE-BE7115.00 (659141) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE7 (659141) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_301 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_302 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_303 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_304 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_305 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_306 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_307 | Single Phase Fault with Stuck Breaker on BD 4230.00 (672601) 230 kV Bus a. Apply Fault at the BD 4230.00 (672601) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD 4 (672601) 230.0 kV to AUBURNTON 4 (672613) 230.0 kV Transmission Circuit #1 b.2. BD 4 (672601) 230.0 kV to KISBEY TAP 4 (673601) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_308 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_309 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_310 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_311 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_312 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to SHEYNNE4 (602006) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_313 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to GARRISN4 (652441) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_314 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_315 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_316 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_317 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #1 b.2. BRISTOL-ER7 (655457) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_318 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to EDGELEY7 (652432) 115.0 kV Transmission Circuit #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_319 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PICKERT4 (657759) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. PICKERT4 (657759) 230.0 kV to GRNDFKS4 (652437) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_320 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to COYOTE 3 (661016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_321 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_322 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_323 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_324 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_325 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_326 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_327 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_328 | Single Phase Fault with Stuck Breaker on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply Fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_329 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_330 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_331 | Single Phase Fault with Stuck Breaker on ELLENDL345 3345.00 (661097) 345 kV Bus a. Apply Fault at the ELLENDL345 3345.00 (661097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL345 3 (661097) 345.0 kV to ELLENDL345 4 (661098) 230.0 kV to ELLENDL345 9 (661907) 34.5 kV Three Winding #1 b.2. ELLENDL345 3 (661097) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_332 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDX 4 (672602) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_333 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_334 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_335 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN7 (652445) 115.0 kV to EDGELEY7 (652432) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_336 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. VALLEYC7 (652454) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_337 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_338 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN-LNX3 (652829) 345.0 kV to WATERTN3 (652529) 345.0 kV Transmission Circuit #z b.2. WATERTN-LNX3 (652829) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_339 | Single Phase Fault with Stuck Breaker on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply Fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_340 | Single Phase Fault with Stuck Breaker on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply Fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.2. AV.LS-BD-BE3 (659420) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_341 | Single Phase Fault with Stuck Breaker on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply Fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #1 b.2. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND-BE3 (659120) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_342 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_343 | Single Phase Fault with Stuck Breaker on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply Fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_344 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_345 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. TN.LS-JD-BE3 (659427) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_346 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z b.2. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_347 | Single Phase Fault with Stuck Breaker on KENMARE7 115.00 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. KENMARE7 (661052) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_348 | Single Phase Fault with Stuck Breaker on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply Fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_349 | Single Phase Fault with Stuck Breaker on ELLENDL345 4230.00 (661098) 230 kV Bus a. Apply Fault at the ELLENDL345 4230.00 (661098) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL345 4 (661098) 230.0 kV to FOXTAIL 4 (661092) 230.0 kV Transmission Circuit #1 b.2. ELLENDL345 4 (661098) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_350 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 b.2. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_351 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_352 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_353 | Single Phase Fault with Stuck Breaker on LAMOURTP-CP869.000 (655627) 69 kV Bus a. Apply Fault at the LAMOURTP-CP869.000 (655627) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMOURTP-CP8 (655627) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.2. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_354 | Single Phase Fault with Stuck Breaker on HESSRTAP-MW7115.00 (655962) 115 kV Bus a. Apply Fault at the HESSRTAP-MW7115.00 (655962) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESSRTAP-MW7 (655962) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 b.2. HESSRTAP-MW7 (655962) 115.0 kV to W.BANK__-MW7 (655922) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_355 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to BLAISDEL-BE4 (659143) 230.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_356 | Single Phase Fault with Stuck Breaker on SHAND 4230.00 (672621) 230 kV Bus a. Apply Fault at the SHAND 4230.00 (672621) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHAND 4 (672621) 230.0 kV to PEEBLES 4 (672616) 230.0 kV Transmission Circuit #1 b.2. SHAND 4 (672621) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_357 | Single Phase Fault with Stuck Breaker on G18-008-TAP 345.00 (762544) 345 kV Bus a. Apply Fault at the G18-008-TAP 345.00 (762544) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-008-TAP (762544) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. G18-008-TAP (762544) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_358 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE7 (603018) 115.0 kV to MODEROW7 (657704) 115.0 kV Transmission Circuit #1 b.2. SHEYNNE7 (603018) 115.0 kV to SHEYNNE4 (602006) 230.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_359 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK7 (652427) 115.0 kV to E.BISMRK-CP7 (655652) 115.0 kV Transmission Circuit #1 b.2. BISMARK7 (652427) 115.0 kV to BISMARK4 (652426) 230.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_360 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_361 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.2. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_362 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 b.2. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_363 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_364 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE7 (659155) 115.0 kV to LOGAN___-BE4 (659108) 230.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE7 (659155) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_365 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE4 (659205) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_366 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTON__-BE3 (659160) 345.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_367 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_368 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_369 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_370 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_278 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_279 | Single Phase Fault with Stuck Breaker on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply Fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBP2DC4 (608599) 230.0 kV Transmission Circuit #z1 b.2. SQBEAST4 (608602) 230.0 kV to SQBP1DC4 (608597) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_280 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_281 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_282 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY8 (652433) 69.0 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 b.2. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_283 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z b.2. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_284 | Single Phase Fault with Stuck Breaker on MOS-IPAB-ER869.000 (655086) 69 kV Bus a. Apply Fault at the MOS-IPAB-ER869.000 (655086) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-IPAB-ER8 (655086) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 b.2. MOS-IPAB-ER8 (655086) 69.0 kV to SW-IPABD-ER8 (655089) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_285 | Single Phase Fault with Stuck Breaker on MOS-ABDN-ER869.000 (655087) 69 kV Bus a. Apply Fault at the MOS-ABDN-ER869.000 (655087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-ABDN-ER8 (655087) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 b.2. MOS-ABDN-ER8 (655087) 69.0 kV to MCSINCRK-ER8 (655516) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_286 | Single Phase Fault with Stuck Breaker on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply Fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 b.2. ABERDEEN-ER8 (655262) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_287 | Single Phase Fault with Stuck Breaker on DICKEYTP-CP869.000 (655625) 69 kV Bus a. Apply Fault at the DICKEYTP-CP869.000 (655625) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to EDGELEY8 (652433) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_288 | Single Phase Fault with Stuck Breaker on OMEGATAP-CP869.000 (655626) 69 kV Bus a. Apply Fault at the OMEGATAP-CP869.000 (655626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMEGATAP-CP8 (655626) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_289 | Single Phase Fault with Stuck Breaker on MAKOTI -CP7115.00 (655664) 115 kV Bus a. Apply Fault at the MAKOTI -CP7115.00 (655664) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAKOTI -CP7 (655664) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.2. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_290 | Single Phase Fault with Stuck Breaker on PLSNTV_T-MW7115.00 (655902) 115 kV Bus a. Apply Fault at the PLSNTV_T-MW7115.00 (655902) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to MOE -MW7 (655900) 115.0 kV Transmission Circuit #1 b.2. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_291 | Single Phase Fault with Stuck Breaker on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply Fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN -MW7 (655904) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_292 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_293 | Single Phase Fault with Stuck Breaker on W.BANK__-MW7115.00 (655922) 115 kV Bus a. Apply Fault at the W.BANK__-MW7115.00 (655922) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 b.2. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_294 | Single Phase Fault with Stuck Breaker on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply Fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLAZA -MW7 (655944) 115.0 kV to PARSHALL-MW7 (655908) 115.0 kV Transmission Circuit #1 b.2. PLAZA -MW7 (655944) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_295 | Single Phase Fault with Stuck Breaker on BLAISDEL-MW7115.00 (655949) 115 kV Bus a. Apply Fault at the BLAISDEL-MW7115.00 (655949) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 b.2. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_296 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_297 | Single Phase Fault with Stuck Breaker on W.BANK_T-MW7115.00 (655953) 115 kV Bus a. Apply Fault at the W.BANK_T-MW7115.00 (655953) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.BANK_T-MW7 (655953) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #1 b.2. W.BANK_T-MW7 (655953) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_298 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_299 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_300 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE7115.00 (659141) 115 kV Bus a. Apply Fault at the NRTSHORE-BE7115.00 (659141) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE7 (659141) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_301 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_302 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_303 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_304 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_305 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_306 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_307 | Single Phase Fault with Stuck Breaker on BD 4230.00 (672601) 230 kV Bus a. Apply Fault at the BD 4230.00 (672601) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD 4 (672601) 230.0 kV to AUBURNTON 4 (672613) 230.0 kV Transmission Circuit #1 b.2. BD 4 (672601) 230.0 kV to KISBEY TAP 4 (673601) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_308 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_309 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_310 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_311 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_312 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to SHEYNNE4 (602006) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_313 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to GARRISN4 (652441) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_314 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_315 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_316 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_317 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #1 b.2. BRISTOL-ER7 (655457) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_318 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to EDGELEY7 (652432) 115.0 kV Transmission Circuit #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_319 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PICKERT4 (657759) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. PICKERT4 (657759) 230.0 kV to GRNDFKS4 (652437) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_320 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to COYOTE 3 (661016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_321 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_322 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_323 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_324 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_325 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_326 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_327 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_328 | Single Phase Fault with Stuck Breaker on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply Fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_329 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_330 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_331 | Single Phase Fault with Stuck Breaker on ELLENDL345 3345.00 (661097) 345 kV Bus a. Apply Fault at the ELLENDL345 3345.00 (661097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL345 3 (661097) 345.0 kV to ELLENDL345 4 (661098) 230.0 kV to ELLENDL345 9 (661907) 34.5 kV Three Winding #1 b.2. ELLENDL345 3 (661097) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_332 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDX 4 (672602) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_333 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_334 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_335 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN7 (652445) 115.0 kV to EDGELEY7 (652432) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_336 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. VALLEYC7 (652454) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_337 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_338 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN-LNX3 (652829) 345.0 kV to WATERTN3 (652529) 345.0 kV Transmission Circuit #z b.2. WATERTN-LNX3 (652829) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_339 | Single Phase Fault with Stuck Breaker on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply Fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_340 | Single Phase Fault with Stuck Breaker on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply Fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.2. AV.LS-BD-BE3 (659420) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_341 | Single Phase Fault with Stuck Breaker on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply Fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #1 b.2. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND-BE3 (659120) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_342 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_343 | Single Phase Fault with Stuck Breaker on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply Fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_344 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_345 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. TN.LS-JD-BE3 (659427) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_346 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z b.2. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_347 | Single Phase Fault with Stuck Breaker on KENMARE7 115.00 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. KENMARE7 (661052) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_348 | Single Phase Fault with Stuck Breaker on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply Fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_349 | Single Phase Fault with Stuck Breaker on ELLENDL345 4230.00 (661098) 230 kV Bus a. Apply Fault at the ELLENDL345 4230.00 (661098) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL345 4 (661098) 230.0 kV to FOXTAIL 4 (661092) 230.0 kV Transmission Circuit #1 b.2. ELLENDL345 4 (661098) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_350 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 b.2. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_351 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_352 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_353 | Single Phase Fault with Stuck Breaker on LAMOURTP-CP869.000 (655627) 69 kV Bus a. Apply Fault at the LAMOURTP-CP869.000 (655627) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMOURTP-CP8 (655627) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.2. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_354 | Single Phase Fault with Stuck Breaker on HESSRTAP-MW7115.00 (655962) 115 kV Bus a. Apply Fault at the HESSRTAP-MW7115.00 (655962) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESSRTAP-MW7 (655962) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 b.2. HESSRTAP-MW7 (655962) 115.0 kV to W.BANK__-MW7 (655922) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_355 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to BLAISDEL-BE4 (659143) 230.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_356 | Single Phase Fault with Stuck Breaker on SHAND 4230.00 (672621) 230 kV Bus a. Apply Fault at the SHAND 4230.00 (672621) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHAND 4 (672621) 230.0 kV to PEEBLES 4 (672616) 230.0 kV Transmission Circuit #1 b.2. SHAND 4 (672621) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_357 | Single Phase Fault with Stuck Breaker on G18-008-TAP 345.00 (762544) 345 kV Bus a. Apply Fault at the G18-008-TAP 345.00 (762544) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-008-TAP (762544) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. G18-008-TAP (762544) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_358 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE7 (603018) 115.0 kV to MODEROW7 (657704) 115.0 kV Transmission Circuit #1 b.2. SHEYNNE7 (603018) 115.0 kV to SHEYNNE4 (602006) 230.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_359 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK7 (652427) 115.0 kV to E.BISMRK-CP7 (655652) 115.0 kV Transmission Circuit #1 b.2. BISMARK7 (652427) 115.0 kV to BISMARK4 (652426) 230.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_360 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_361 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.2. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_362 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 b.2. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_363 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_364 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE7 (659155) 115.0 kV to LOGAN___-BE4 (659108) 230.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE7 (659155) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_365 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE4 (659205) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_366 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTON__-BE3 (659160) 345.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_367 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_368 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_369 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_370 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_371 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_372 | Single Phase Fault with Stuck Breaker on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply Fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBP2DC4 (608599) 230.0 kV Transmission Circuit #z1 b.2. SQBEAST4 (608602) 230.0 kV to SQBP1DC4 (608597) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_373 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_374 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_375 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY8 (652433) 69.0 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 b.2. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_376 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z b.2. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_377 | Single Phase Fault with Stuck Breaker on MOS-IPAB-ER869.000 (655086) 69 kV Bus a. Apply Fault at the MOS-IPAB-ER869.000 (655086) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-IPAB-ER8 (655086) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 b.2. MOS-IPAB-ER8 (655086) 69.0 kV to SW-IPABD-ER8 (655089) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_378 | Single Phase Fault with Stuck Breaker on MOS-ABDN-ER869.000 (655087) 69 kV Bus a. Apply Fault at the MOS-ABDN-ER869.000 (655087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-ABDN-ER8 (655087) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 b.2. MOS-ABDN-ER8 (655087) 69.0 kV to MCSINCRK-ER8 (655516) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_379 | Single Phase Fault with Stuck Breaker on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply Fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 b.2. ABERDEEN-ER8 (655262) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_380 | Single Phase Fault with Stuck Breaker on DICKEYTP-CP869.000 (655625) 69 kV Bus a. Apply Fault at the DICKEYTP-CP869.000 (655625) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to EDGELEY8 (652433) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_381 | Single Phase Fault with Stuck Breaker on OMEGATAP-CP869.000 (655626) 69 kV Bus a. Apply Fault at the OMEGATAP-CP869.000 (655626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMEGATAP-CP8 (655626) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_382 | Single Phase Fault with Stuck Breaker on MAKOTI -CP7115.00 (655664) 115 kV Bus a. Apply Fault at the MAKOTI -CP7115.00 (655664) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAKOTI -CP7 (655664) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.2. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_383 | Single Phase Fault with Stuck Breaker on PLSNTV_T-MW7115.00 (655902) 115 kV Bus a. Apply Fault at the PLSNTV_T-MW7115.00 (655902) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to MOE -MW7 (655900) 115.0 kV Transmission Circuit #1 b.2. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_384 | Single Phase Fault with Stuck Breaker on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply Fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN -MW7 (655904) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_385 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_386 | Single Phase Fault with Stuck Breaker on W.BANK__-MW7115.00 (655922) 115 kV Bus a. Apply Fault at the W.BANK__-MW7115.00 (655922) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 b.2. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_387 | Single Phase Fault with Stuck Breaker on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply Fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLAZA -MW7 (655944) 115.0 kV to PARSHALL-MW7 (655908) 115.0 kV Transmission Circuit #1 b.2. PLAZA -MW7 (655944) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_388 | Single Phase Fault with Stuck Breaker on BLAISDEL-MW7115.00 (655949) 115 kV Bus a. Apply Fault at the BLAISDEL-MW7115.00 (655949) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 b.2. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_389 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_390 | Single Phase Fault with Stuck Breaker on W.BANK_T-MW7115.00 (655953) 115 kV Bus a. Apply Fault at the W.BANK_T-MW7115.00 (655953) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.BANK_T-MW7 (655953) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #1 b.2. W.BANK_T-MW7 (655953) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_391 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_392 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_393 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE7115.00 (659141) 115 kV Bus a. Apply Fault at the NRTSHORE-BE7115.00 (659141) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE7 (659141) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_394 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_395 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_396 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_397 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_398 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_399 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_400 | Single Phase Fault with Stuck Breaker on BD 4230.00 (672601) 230 kV Bus a. Apply Fault at the BD 4230.00 (672601) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD 4 (672601) 230.0 kV to AUBURNTON 4 (672613) 230.0 kV Transmission Circuit #1 b.2. BD 4 (672601) 230.0 kV to KISBEY TAP 4 (673601) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_401 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_402 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_403 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_404 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_405 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to SHEYNNE4 (602006) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_406 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to GARRISN4 (652441) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_407 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_408 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_409 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_410 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #1 b.2. BRISTOL-ER7 (655457) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_411 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to EDGELEY7 (652432) 115.0 kV Transmission Circuit #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_412 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PICKERT4 (657759) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. PICKERT4 (657759) 230.0 kV to GRNDFKS4 (652437) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_413 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to COYOTE 3 (661016) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_414 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_415 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_416 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_417 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_418 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_419 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_420 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_421 | Single Phase Fault with Stuck Breaker on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply Fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_422 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_423 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to JUDSON__-BE3 (659333) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_424 | Single Phase Fault with Stuck Breaker on ELLENDL345 3345.00 (661097) 345 kV Bus a. Apply Fault at the ELLENDL345 3345.00 (661097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL345 3 (661097) 345.0 kV to ELLENDL345 4 (661098) 230.0 kV to ELLENDL345 9 (661907) 34.5 kV Three Winding #1 b.2. ELLENDL345 3 (661097) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_425 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDX 4 (672602) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_426 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_427 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_428 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN7 (652445) 115.0 kV to EDGELEY7 (652432) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_429 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. VALLEYC7 (652454) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_430 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_431 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN-LNX3 (652829) 345.0 kV to WATERTN3 (652529) 345.0 kV Transmission Circuit #z b.2. WATERTN-LNX3 (652829) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_432 | Single Phase Fault with Stuck Breaker on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply Fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_433 | Single Phase Fault with Stuck Breaker on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply Fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.2. AV.LS-BD-BE3 (659420) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_434 | Single Phase Fault with Stuck Breaker on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply Fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #1 b.2. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND-BE3 (659120) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_435 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_436 | Single Phase Fault with Stuck Breaker on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply Fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_437 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_438 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. TN.LS-JD-BE3 (659427) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_439 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z b.2. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_440 | Single Phase Fault with Stuck Breaker on KENMARE7 115.00 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. KENMARE7 (661052) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_441 | Single Phase Fault with Stuck Breaker on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply Fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_442 | Single Phase Fault with Stuck Breaker on ELLENDL345 4230.00 (661098) 230 kV Bus a. Apply Fault at the ELLENDL345 4230.00 (661098) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL345 4 (661098) 230.0 kV to FOXTAIL 4 (661092) 230.0 kV Transmission Circuit #1 b.2. ELLENDL345 4 (661098) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_443 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 b.2. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_444 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_445 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_446 | Single Phase Fault with Stuck Breaker on LAMOURTP-CP869.000 (655627) 69 kV Bus a. Apply Fault at the LAMOURTP-CP869.000 (655627) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMOURTP-CP8 (655627) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.2. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_447 | Single Phase Fault with Stuck Breaker on HESSRTAP-MW7115.00 (655962) 115 kV Bus a. Apply Fault at the HESSRTAP-MW7115.00 (655962) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESSRTAP-MW7 (655962) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 b.2. HESSRTAP-MW7 (655962) 115.0 kV to W.BANK__-MW7 (655922) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_448 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to BLAISDEL-BE4 (659143) 230.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_449 | Single Phase Fault with Stuck Breaker on SHAND 4230.00 (672621) 230 kV Bus a. Apply Fault at the SHAND 4230.00 (672621) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHAND 4 (672621) 230.0 kV to PEEBLES 4 (672616) 230.0 kV Transmission Circuit #1 b.2. SHAND 4 (672621) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_450 | Single Phase Fault with Stuck Breaker on G18-008-TAP 345.00 (762544) 345 kV Bus a. Apply Fault at the G18-008-TAP 345.00 (762544) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-008-TAP (762544) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. G18-008-TAP (762544) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_451 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE7 (603018) 115.0 kV to MODEROW7 (657704) 115.0 kV Transmission Circuit #1 b.2. SHEYNNE7 (603018) 115.0 kV to SHEYNNE4 (602006) 230.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_452 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK7 (652427) 115.0 kV to E.BISMRK-CP7 (655652) 115.0 kV Transmission Circuit #1 b.2. BISMARK7 (652427) 115.0 kV to BISMARK4 (652426) 230.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to High voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25S | Transfer | GROUP1_FAULT_453 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_454 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.2. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_455 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 b.2. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_456 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_457 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE7 (659155) 115.0 kV to LOGAN___-BE4 (659108) 230.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE7 (659155) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_458 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE4 (659205) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_459 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTON__-BE3 (659160) 345.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_460 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_461 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to KILDEER7 (652419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_462 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25S | Transfer | GROUP1_FAULT_463 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_1 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_2 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_3 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_4 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.6. 33SUPERIOR7 (650233) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_5 | 3 Phase fault on 56&Q 7 115.00 (650260) 115 kV Bus a. Apply fault at the 56&Q 7 115.00 (650260) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_6 | 3 Phase fault on 57&GARLAND7 115.00 (650262) 115 kV Bus a. Apply fault at the 57&GARLAND7 115.00 (650262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_7 | 3 Phase fault on 93&O 7 115.00 (650273) 115 kV Bus a. Apply fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_8 | 3 Phase fault on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_9 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_10 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_11 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_12 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_13 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_14 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_15 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_16 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_17 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_18 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_19 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_20 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_21 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_22 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_23 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_24 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_25 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_26 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_27 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_28 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_29 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_30 | 3 Phase fault on HASTING5 161.00 (635032) 161 kV Bus a. Apply fault at the HASTING5 161.00 (635032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNGE 5 (635031) 161.0 kV to HASTING5 (635032) 161.0 kV Transmission Circuit #1 b.2. HASTING5 (635032) 161.0 kV to HASTING8 (635033) 69.0 kV Two Winding #1 b.3. HASTING5 (635032) 161.0 kV to CLRNDA 5 (635034) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_31 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_32 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_33 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_34 | 3 Phase fault on LEHIGH 3 345.00 (636010) 345 kV Bus a. Apply fault at the LEHIGH 3 345.00 (636010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEHIGH 3 (636010) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_35 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_36 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_37 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_38 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_39 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_40 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_41 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_42 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_43 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_44 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_45 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_46 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_47 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_48 | 3 Phase fault on QUICK 5 161.00 (635012) 161 kV Bus a. Apply fault at the QUICK 5 161.00 (635012) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_49 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_50 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_51 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_52 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_53 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_54 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_55 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_56 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_57 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_58 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_59 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_60 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_61 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_62 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_63 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_64 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_65 | 3 Phase fault on WEBSTER3 345.00 (636000) 345 kV Bus a. Apply fault at the WEBSTER3 345.00 (636000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_66 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_67 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_68 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_69 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_70 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_71 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_72 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_73 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_74 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_75 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_76 | 3 Phase fault on MANAWA 5 161.00 (635010) 161 kV Bus a. Apply fault at the MANAWA 5 161.00 (635010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 b.2. MANAWA 5 (635010) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_77 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_78 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_79 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_80 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_81 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_82 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_83 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_84 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_85 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_86 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 70&CALVERT7 (650270) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_87 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_88 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_89 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_90 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations; GEN-2018-056 | Build a 50 MVAR STATCOM at GR PRAIRIE 345 kV | Tuned (if applicable) GEN-2018-056 developer model that provides VAR support
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_91 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_92 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_93 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_94 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_95 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_96 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_97 | 3 Phase fault on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_98 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_99 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_100 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_101 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_102 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_103 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_104 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_105 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_106 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_107 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_108 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_109 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_110 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_111 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_112 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_113 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_114 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_115 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_116 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_117 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_118 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_119 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_120 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_121 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_122 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_123 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_124 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_125 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_126 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_127 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_128 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_129 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_130 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_131 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_132 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_133 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_134 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_135 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_136 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_137 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_138 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_139 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_140 | 3 Phase fault on HOSK.T89 34.500 (640230) 34.5 kV Bus a. Apply fault at the HOSK.T89 34.500 (640230) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_141 | 3 Phase fault on HOSK.T89 34.500 (640230) 34.5 kV Bus a. Apply fault at the HOSK.T89 34.500 (640230) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_142 | 3 Phase fault on HOSK.T89 34.500 (640230) 34.5 kV Bus a. Apply fault at the HOSK.T89 34.500 (640230) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_143 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_144 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_145 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_146 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_147 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_148 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_149 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_150 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_151 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_152 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_153 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_154 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_155 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_156 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_157 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_158 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_159 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_160 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_161 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_162 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_163 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_164 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_165 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_166 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_167 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_168 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_169 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_170 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_171 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_172 | 3 Phase fault on S1222 5 161.00 (646222) 161 kV Bus a. Apply fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_173 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_174 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_175 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_176 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_177 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_178 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_179 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_180 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_181 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_182 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_183 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_184 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_185 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_186 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_187 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_188 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_189 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_190 | 3 Phase fault on S1256 5 161.00 (646256) 161 kV Bus a. Apply fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_191 | 3 Phase fault on S1254 5 161.00 (646254) 161 kV Bus a. Apply fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_192 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_193 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_194 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_195 | 3 Phase fault on S1278 5 161.00 (646278) 161 kV Bus a. Apply fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_196 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_197 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_198 | 3 Phase fault on S1286 5 161.00 (646286) 161 kV Bus a. Apply fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_199 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_200 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_201 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_202 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_203 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_204 | 3 Phase fault on S1367 5 161.00 (646367) 161 kV Bus a. Apply fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_205 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_206 | 3 Phase fault on JCT205 8 69.000 (647105) 69 kV Bus a. Apply fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_207 | 3 Phase fault on S901 8 69.000 (647901) 69 kV Bus a. Apply fault at the S901 8 69.000 (647901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_208 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_209 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_210 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_211 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_212 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_213 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_214 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_215 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_216 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_217 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_218 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_219 | 3 Phase fault on S910 8 69.000 (647910) 69 kV Bus a. Apply fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_220 | 3 Phase fault on S911 8 69.000 (647911) 69 kV Bus a. Apply fault at the S911 8 69.000 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_221 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_222 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_223 | 3 Phase fault on S918 8 69.000 (647918) 69 kV Bus a. Apply fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_224 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_225 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_226 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_227 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_228 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_229 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_230 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_231 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_232 | 3 Phase fault on S939 8 69.000 (647939) 69 kV Bus a. Apply fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_233 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_234 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_235 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_236 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_237 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_238 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_239 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_240 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_241 | 3 Phase fault on S3761 3 345.00 (645761) 345 kV Bus a. Apply fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_242 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_243 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_244 | 3 Phase fault on S1210 5 161.00 (646210) 161 kV Bus a. Apply fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_245 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_246 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_247 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_248 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_249 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_250 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_251 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_252 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_253 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_254 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_255 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_256 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_257 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_258 | 3 Phase fault on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_259 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_260 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_261 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_262 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_263 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_264 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_265 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_266 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_267 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 29 (652598) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_268 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_269 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_270 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_271 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_272 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_273 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_274 | 3 Phase fault on WSEC 3G 24.000 (635023) 24 kV Bus a. Apply fault at the WSEC 3G 24.000 (635023) 24 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSEC 3G (635023) 24.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_275 | 3 Phase fault on WSEC 4G 26.000 (635024) 26 kV Bus a. Apply fault at the WSEC 4G 26.000 (635024) 26 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSEC 4G (635024) 26.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_276 | 3 Phase fault on NEAL 3G 22.000 (635213) 22 kV Bus a. Apply fault at the NEAL 3G 22.000 (635213) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL 3G (635213) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_277 | 3 Phase fault on NEAL 4G 24.000 (635214) 24 kV Bus a. Apply fault at the NEAL 4G 24.000 (635214) 24 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL 4G (635214) 24.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_278 | 3 Phase fault on COOPER1G 22.000 (640009) 22 kV Bus a. Apply fault at the COOPER1G 22.000 (640009) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER1G (640009) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_279 | 3 Phase fault on NEBCTY1G 18.000 (645011) 18 kV Bus a. Apply fault at the NEBCTY1G 18.000 (645011) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEBCTY1G (645011) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_280 | 3 Phase fault on NEBCTY2G 23.000 (645012) 23 kV Bus a. Apply fault at the NEBCTY2G 23.000 (645012) 23 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEBCTY2G (645012) 23.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_281 | 3 Phase fault on N OMA 4G 15.000 (645024) 15 kV Bus a. Apply fault at the N OMA 4G 15.000 (645024) 15 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N OMA 4G (645024) 15.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_282 | 3 Phase fault on N OMA 5G 20.000 (645025) 20 kV Bus a. Apply fault at the N OMA 5G 20.000 (645025) 20 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N OMA 5G (645025) 20.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_283 | 3 Phase fault on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARPY 3G (645033) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_284 | 3 Phase fault on SARPY 4G 13.800 (645034) 13.80000019 kV Bus a. Apply fault at the SARPY 4G 13.800 (645034) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARPY 4G (645034) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_285 | 3 Phase fault on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARPY 5G (645035) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_286 | 3 Phase fault on CASS 1G 15.000 (645041) 15 kV Bus a. Apply fault at the CASS 1G 15.000 (645041) 15 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASS 1G (645041) 15.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_287 | 3 Phase fault on CASS 2G 15.000 (645042) 15 kV Bus a. Apply fault at the CASS 2G 15.000 (645042) 15 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASS 2G (645042) 15.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_288 | 3 Phase fault on JONES 1G 13.800 (645051) 13.80000019 kV Bus a. Apply fault at the JONES 1G 13.800 (645051) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 1G (645051) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_289 | 3 Phase fault on JONES 2G 13.800 (645052) 13.80000019 kV Bus a. Apply fault at the JONES 2G 13.800 (645052) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 2G (645052) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_290 | 3 Phase fault on GRPR11 W 0.6900 (645065) 0.689999998 kV Bus a. Apply fault at the GRPR11 W 0.6900 (645065) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPR11 W (645065) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_291 | 3 Phase fault on GRPR12 W 0.6900 (645066) 0.689999998 kV Bus a. Apply fault at the GRPR12 W 0.6900 (645066) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPR12 W (645066) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_292 | 3 Phase fault on GRPR21 W 0.6900 (645067) 0.689999998 kV Bus a. Apply fault at the GRPR21 W 0.6900 (645067) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPR21 W (645067) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_293 | 3 Phase fault on GRPR22 W 0.6900 (645068) 0.689999998 kV Bus a. Apply fault at the GRPR22 W 0.6900 (645068) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPR22 W (645068) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_294 | 3 Phase fault on S1297 9 13.800 (649297) 13.80000019 kV Bus a. Apply fault at the S1297 9 13.800 (649297) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1297 9 (649297) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_295 | 3 Phase fault on G18-012-GEN10.6900 (762507) 0.689999998 kV Bus a. Apply fault at the G18-012-GEN10.6900 (762507) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-012-GEN1 (762507) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_296 | 3 Phase fault on G18-025GEN1 0.6600 (762606) 0.660000026 kV Bus a. Apply fault at the G18-025GEN1 0.6600 (762606) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-025GEN1 (762606) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_297 | 3 Phase fault on G18-033GEN1 0.6600 (762694) 0.660000026 kV Bus a. Apply fault at the G18-033GEN1 0.6600 (762694) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-033GEN1 (762694) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_298 | 3 Phase fault on G18-037GEN1 0.6600 (762716) 0.660000026 kV Bus a. Apply fault at the G18-037GEN1 0.6600 (762716) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-037GEN1 (762716) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_299 | 3 Phase fault on G18-043-GEN10.6600 (762783) 0.660000026 kV Bus a. Apply fault at the G18-043-GEN10.6600 (762783) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-043-GEN1 (762783) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_300 | 3 Phase fault on G18-043-GEN20.6600 (762786) 0.660000026 kV Bus a. Apply fault at the G18-043-GEN20.6600 (762786) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-043-GEN2 (762786) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_301 | 3 Phase fault on G18-043-GEN30.6600 (762789) 0.660000026 kV Bus a. Apply fault at the G18-043-GEN30.6600 (762789) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-043-GEN3 (762789) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_302 | 3 Phase fault on G18-056-GEN10.6600 (762914) 0.660000026 kV Bus a. Apply fault at the G18-056-GEN10.6600 (762914) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-056-GEN1 (762914) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_303 | 3 Phase fault on G18-060-GEN10.6300 (762957) 0.629999995 kV Bus a. Apply fault at the G18-060-GEN10.6300 (762957) 0.629999995 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-060-GEN1 (762957) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_304 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_305 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_306 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_307 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_308 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_309 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_310 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_311 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_312 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_313 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_314 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_315 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_316 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_317 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_318 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_319 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_320 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_321 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB703 8 (635006) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_322 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB704 8 (635007) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_323 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to HONEYCK8 (635080) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_324 | 3 Phase fault on SUB704 8 69.000 (635007) 69 kV Bus a. Apply fault at the SUB704 8 69.000 (635007) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB704 8 (635007) 69.0 kV to SUB705 8 (635008) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_325 | 3 Phase fault on OVRLND 5 161.00 (635015) 161 kV Bus a. Apply fault at the OVRLND 5 161.00 (635015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_326 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_327 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_328 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Divergence of simulation due to low voltage after fault unable to be recovered | Reclosing Removed
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_329 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_330 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_331 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_332 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_333 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_334 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_335 | 3 Phase fault on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_336 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_337 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_338 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_339 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_340 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_341 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_342 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_343 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_344 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_345 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_346 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_347 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_348 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_349 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_350 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_351 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_352 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_353 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_354 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_355 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_356 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_357 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_358 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_359 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_360 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_361 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_362 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_363 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_364 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_365 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_366 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_367 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_368 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_369 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_370 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_371 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_372 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_373 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_374 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_375 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_376 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_377 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_378 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_379 | 3 Phase fault on FTTHOM1-LNX5345.00 (652808) 345 kV Bus a. Apply fault at the FTTHOM1-LNX5345.00 (652808) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM1-LNX5 (652808) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_380 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_381 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_382 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_383 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_384 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_385 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_386 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_387 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_388 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_389 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_390 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_391 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_392 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_393 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_394 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_395 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_396 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_397 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_398 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_399 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_400 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_401 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_402 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_403 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_404 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_405 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_406 | 3 Phase fault on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_407 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_408 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_409 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_410 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_1 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_2 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_3 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_4 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_5 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_6 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_7 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_8 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_9 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_10 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_11 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_12 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_13 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_14 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_15 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_16 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_17 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S1366 5 (646366) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_18 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S1366 5 (646366) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_19 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S1366 5 (646366) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_20 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_21 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_22 | Single Phase Fault with Stuck Breaker on S994 8 69.000 (647994) 69 kV Bus a. Apply Fault at the S994 8 69.000 (647994) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.8. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_23 | Single Phase Fault with Stuck Breaker on SAC629 8 69.000 (647108) 69 kV Bus a. Apply Fault at the SAC629 8 69.000 (647108) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.6. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.7. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_24 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.8. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_25 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.6. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.7. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_26 | Single Phase Fault with Stuck Breaker on S995 8 69.000 (647995) 69 kV Bus a. Apply Fault at the S995 8 69.000 (647995) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_27 | Single Phase Fault with Stuck Breaker on SAC623 8 69.000 (647107) 69 kV Bus a. Apply Fault at the SAC623 8 69.000 (647107) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.9. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.10. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_28 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_29 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_30 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_31 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_32 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_33 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_34 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_35 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_36 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_37 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_38 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_39 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_40 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_41 | Single Phase Fault with Stuck Breaker on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply Fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 29LEIGHTON7 (650240) 115.0 kV Transmission Circuit #1 b.2. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.4. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.7. 33SUPERIOR7 (650233) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_42 | Single Phase Fault with Stuck Breaker on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply Fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.3. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.4. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.5. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 b.8. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.11. 33SUPERIOR7 (650233) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_43 | Single Phase Fault with Stuck Breaker on 56&Q 7 115.00 (650260) 115 kV Bus a. Apply Fault at the 56&Q 7 115.00 (650260) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&Q 7 (650260) 115.0 kV Transmission Circuit #1 b.2. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 56&Q 7 (650260) 115.0 kV to 56&Q A9 (650360) 13.2 kV to 601TERTIARY (650560) 7.2 kV Three Winding #1 b.4. 56&Q 7 (650260) 115.0 kV to 56&Q B9 (650460) 13.2 kV to 602TERTIARY (650660) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_44 | Single Phase Fault with Stuck Breaker on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply Fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.4. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.7. 33SUPERIOR7 (650233) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_45 | Single Phase Fault with Stuck Breaker on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply Fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.4. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.7. 33SUPERIOR7 (650233) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_46 | Single Phase Fault with Stuck Breaker on 57&GARLAND7 115.00 (650262) 115 kV Bus a. Apply Fault at the 57&GARLAND7 115.00 (650262) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_47 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_48 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_49 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_50 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.5. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.6. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.9. 70&CALVERT7 (650270) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_51 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.5. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.8. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 b.11. 70&CALVERT7 (650270) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_52 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_53 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_54 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_55 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_56 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_57 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_58 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_59 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_60 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.6. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 b.7. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.8. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.9. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_61 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.10. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.11. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.12. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_62 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_63 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_64 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.3. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.4. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 b.5. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.6. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.7. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_65 | Single Phase Fault with Stuck Breaker on WAVERLY 7 115.00 (650283) 115 kV Bus a. Apply Fault at the WAVERLY 7 115.00 (650283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.3. WAVERLY 7 (650283) 115.0 kV to WAVERLY A9 (650383) 13.2 kV to 831TERTIARY (650583) 7.2 kV Three Winding #1 b.4. WAVERLY 7 (650283) 115.0 kV to WAVERLY B9 (650483) 12.5 kV to 832TERTIARY (650683) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_66 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_67 | Single Phase Fault with Stuck Breaker on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply Fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.3. 120&ALVO 7 (650279) 115.0 kV to 120&ALVO 9 (650379) 12.5 kV to 791TERTIARY (650579) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_68 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_69 | Single Phase Fault with Stuck Breaker on WAGENER 7 115.00 (650285) 115 kV Bus a. Apply Fault at the WAGENER 7 115.00 (650285) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_70 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.5. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.6. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_71 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.5. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.8. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 b.11. 70&CALVERT7 (650270) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_72 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.4. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.7. 70&CALVERT7 (650270) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_73 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_74 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.6. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_75 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.6. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_76 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.6. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_77 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.4. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 b.5. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.6. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.7. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.9. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_78 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.4. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 b.5. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.6. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.7. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.9. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_79 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY3 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_80 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_81 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_82 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HILLCTY3 (531387) 34.5 kV Two Winding #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_83 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_84 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_85 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_86 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_87 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_88 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_89 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_90 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.4. ALEXND-T (539902) 12.5 kV to ALEXNDR1 (539702) 34.5 kV to ALXNDR 3 (530606) 115.0 kV Three Winding #1 b.6. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.8. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.11. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.12. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_91 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_92 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.6. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.7. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_93 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_94 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_95 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_96 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_97 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_98 | Single Phase Fault with Stuck Breaker on SHAYS_COLLR134.500 (530613) 34.5 kV Bus a. Apply Fault at the SHAYS_COLLR134.500 (530613) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.5. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.7. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_99 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_100 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_101 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_102 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.5. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_103 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_104 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_105 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_106 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_107 | Single Phase Fault with Stuck Breaker on OGALATP3 115.00 (530677) 115 kV Bus a. Apply Fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.6. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.7. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_108 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_109 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_110 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_112 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_113 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_114 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_115 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_116 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_117 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_118 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_119 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_120 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_121 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_122 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_123 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_124 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_125 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_126 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_127 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_128 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_129 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_130 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_131 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_132 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_133 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_134 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_135 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_136 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_137 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_138 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_139 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_140 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_141 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_142 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_143 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_144 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_145 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_146 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_147 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_148 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_149 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_150 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_151 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_152 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_153 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_154 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_155 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_156 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_157 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_158 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_159 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_160 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_161 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_162 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_163 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_164 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_165 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_166 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_167 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_168 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_169 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_170 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_171 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_172 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_173 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_174 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_175 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_176 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_177 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_178 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_179 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_180 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_181 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_182 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_183 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_184 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_185 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_186 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_187 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_188 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_189 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_190 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_191 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_192 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_193 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_194 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_195 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_196 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_197 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_198 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_199 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_200 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_201 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_202 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_203 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_204 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_205 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_206 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_207 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_208 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_209 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_210 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_211 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_212 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_213 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_214 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_215 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_216 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_217 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_218 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_219 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_220 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_221 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_222 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_223 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator # b.3. SARPY 5G (645035) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_224 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator # b.3. SARPY 5G (645035) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_225 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator # b.3. SARPY 5G (645035) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_226 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_227 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_228 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_229 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_230 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_231 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_232 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_233 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_234 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_235 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_236 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_237 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_238 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_239 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_240 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_241 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_242 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_243 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_244 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_245 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_246 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_247 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_248 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_249 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_250 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_251 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_252 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_253 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_254 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_255 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.4. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_256 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.4. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_257 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.4. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_258 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.4. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_259 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.4. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_260 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.4. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_261 | Single Phase Fault with Stuck Breaker on NO4 AUX9 2.4000 (645124) 2.400000095 kV Bus a. Apply Fault at the NO4 AUX9 2.4000 (645124) 2.400000095 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_262 | Single Phase Fault with Stuck Breaker on NO4 AUX9 2.4000 (645124) 2.400000095 kV Bus a. Apply Fault at the NO4 AUX9 2.4000 (645124) 2.400000095 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_263 | Single Phase Fault with Stuck Breaker on NO4 AUX9 2.4000 (645124) 2.400000095 kV Bus a. Apply Fault at the NO4 AUX9 2.4000 (645124) 2.400000095 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_264 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_265 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_266 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_267 | Single Phase Fault with Stuck Breaker on NO5 AUX9 4.2000 (645125) 4.199999809 kV Bus a. Apply Fault at the NO5 AUX9 4.2000 (645125) 4.199999809 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_268 | Single Phase Fault with Stuck Breaker on NO5 AUX9 4.2000 (645125) 4.199999809 kV Bus a. Apply Fault at the NO5 AUX9 4.2000 (645125) 4.199999809 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_269 | Single Phase Fault with Stuck Breaker on NO5 AUX9 4.2000 (645125) 4.199999809 kV Bus a. Apply Fault at the NO5 AUX9 4.2000 (645125) 4.199999809 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.2. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_270 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_271 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_272 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_273 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_274 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_275 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_276 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_277 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_278 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_279 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_280 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_281 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_282 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_283 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_284 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_285 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_286 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_287 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_288 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_289 | Single Phase Fault with Stuck Breaker on S1220 5 161.00 (646220) 161 kV Bus a. Apply Fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_290 | Single Phase Fault with Stuck Breaker on S1220 5 161.00 (646220) 161 kV Bus a. Apply Fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_291 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_292 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_293 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_294 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_295 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_296 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_297 | Single Phase Fault with Stuck Breaker on S1222 5 161.00 (646222) 161 kV Bus a. Apply Fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_298 | Single Phase Fault with Stuck Breaker on S1222 5 161.00 (646222) 161 kV Bus a. Apply Fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_299 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_300 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_301 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_302 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_303 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_304 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_305 | Single Phase Fault with Stuck Breaker on S1227 5 161.00 (646227) 161 kV Bus a. Apply Fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_306 | Single Phase Fault with Stuck Breaker on S1227 5 161.00 (646227) 161 kV Bus a. Apply Fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_307 | Single Phase Fault with Stuck Breaker on S1229 5 161.00 (646229) 161 kV Bus a. Apply Fault at the S1229 5 161.00 (646229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_308 | Single Phase Fault with Stuck Breaker on S1229 5 161.00 (646229) 161 kV Bus a. Apply Fault at the S1229 5 161.00 (646229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_309 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_310 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_311 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_312 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_313 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_314 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_315 | Single Phase Fault with Stuck Breaker on S1233 5 161.00 (646233) 161 kV Bus a. Apply Fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_316 | Single Phase Fault with Stuck Breaker on S1233 5 161.00 (646233) 161 kV Bus a. Apply Fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_317 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_318 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_319 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.3. S1235 5 (646235) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_320 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.3. S1235 5 (646235) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_321 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_322 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_323 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_324 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_325 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_326 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_327 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_328 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_329 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_330 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_331 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_332 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_333 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_334 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_335 | Single Phase Fault with Stuck Breaker on S1249 5 161.00 (646249) 161 kV Bus a. Apply Fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_336 | Single Phase Fault with Stuck Breaker on S1249 5 161.00 (646249) 161 kV Bus a. Apply Fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_337 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_338 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_339 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_340 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_341 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_342 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_343 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_344 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_345 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_346 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1211 5 (646211) 161.0 kV to Load # b.4. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_347 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1211 5 (646211) 161.0 kV to Load # b.4. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_348 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_349 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_350 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_351 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_352 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_353 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_354 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_355 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_356 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_357 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_358 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_359 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_360 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S1366 5 (646366) 161.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_361 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S1366 5 (646366) 161.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_362 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S1366 5 (646366) 161.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_363 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_364 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_365 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_366 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_367 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_368 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_369 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_370 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_371 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_372 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_373 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_374 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_375 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_376 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_377 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_378 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_379 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_380 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_381 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_382 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_383 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_384 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_385 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_386 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_387 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_388 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_389 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_390 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_391 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_392 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_393 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_394 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_395 | Single Phase Fault with Stuck Breaker on S1256 5 161.00 (646256) 161 kV Bus a. Apply Fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_396 | Single Phase Fault with Stuck Breaker on S1256 5 161.00 (646256) 161 kV Bus a. Apply Fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_397 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_398 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_399 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_400 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_401 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_402 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_403 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_404 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_405 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_406 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_407 | Single Phase Fault with Stuck Breaker on S1286 5 161.00 (646286) 161 kV Bus a. Apply Fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_408 | Single Phase Fault with Stuck Breaker on S1286 5 161.00 (646286) 161 kV Bus a. Apply Fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_409 | Single Phase Fault with Stuck Breaker on S1287 5 161.00 (646287) 161 kV Bus a. Apply Fault at the S1287 5 161.00 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_410 | Single Phase Fault with Stuck Breaker on S1287 5 161.00 (646287) 161 kV Bus a. Apply Fault at the S1287 5 161.00 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_411 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_412 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_413 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_414 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_415 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_416 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_417 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_418 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_419 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_420 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_421 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_422 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_423 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_424 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_425 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_426 | Single Phase Fault with Stuck Breaker on S1367 5 161.00 (646367) 161 kV Bus a. Apply Fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_427 | Single Phase Fault with Stuck Breaker on S1367 5 161.00 (646367) 161 kV Bus a. Apply Fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_428 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_429 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.8. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_430 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_431 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_432 | Single Phase Fault with Stuck Breaker on S1255 5 161.00 (646255) 161 kV Bus a. Apply Fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_433 | Single Phase Fault with Stuck Breaker on S1255 5 161.00 (646255) 161 kV Bus a. Apply Fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_434 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_435 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_436 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_437 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_438 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_439 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_440 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.2. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.3. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.4. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.5. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 b.6. S901 8 (647901) 69.0 kV to S1201 5 (646201) 161.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_441 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_442 | Single Phase Fault with Stuck Breaker on S985 8 69.000 (647985) 69 kV Bus a. Apply Fault at the S985 8 69.000 (647985) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.3. PLTSMTH8 (640320) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.4. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_443 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_444 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.5. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_445 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.2. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_446 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.2. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_447 | Single Phase Fault with Stuck Breaker on S907 8 69.000 (647907) 69 kV Bus a. Apply Fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_448 | Single Phase Fault with Stuck Breaker on S909 8 69.000 (647909) 69 kV Bus a. Apply Fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S1209 5 (646209) 161.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.6. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_449 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S1209 5 (646209) 161.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_450 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.2. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S1210 5 (646210) 161.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_451 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S910 8 (647910) 69.0 kV to S1210 5 (646210) 161.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_452 | Single Phase Fault with Stuck Breaker on N OMA 1G 13.800 (645021) 13.80000019 kV Bus a. Apply Fault at the N OMA 1G 13.800 (645021) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S1211 5 (646211) 161.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 b.8. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_453 | Single Phase Fault with Stuck Breaker on S912 8 69.000 (647912) 69 kV Bus a. Apply Fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_454 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_455 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_456 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S917 8 (647917) 69.0 kV to S1217 5 (646217) 161.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.4. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.5. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_457 | Single Phase Fault with Stuck Breaker on S918 8 69.000 (647918) 69 kV Bus a. Apply Fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_458 | Single Phase Fault with Stuck Breaker on S919 8 69.000 (647919) 69 kV Bus a. Apply Fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.3. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_459 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.3. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 b.4. S921 8 (647921) 69.0 kV to S1221 5 (646221) 161.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_460 | Single Phase Fault with Stuck Breaker on S923 8 69.000 (647923) 69 kV Bus a. Apply Fault at the S923 8 69.000 (647923) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.3. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_461 | Single Phase Fault with Stuck Breaker on S912 8 69.000 (647912) 69 kV Bus a. Apply Fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_462 | Single Phase Fault with Stuck Breaker on JCT205 8 69.000 (647105) 69 kV Bus a. Apply Fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 b.2. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_463 | Single Phase Fault with Stuck Breaker on S924 8 69.000 (647924) 69 kV Bus a. Apply Fault at the S924 8 69.000 (647924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_464 | Single Phase Fault with Stuck Breaker on S928 8 69.000 (647928) 69 kV Bus a. Apply Fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_465 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_466 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_467 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_468 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_469 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.9. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.10. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_470 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_471 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_472 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_473 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.4. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.5. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.6. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.7. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.8. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.9. S906 N 8 (647006) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_474 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.2. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_475 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_476 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_477 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.9. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.11. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_478 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.10. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.11. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.12. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.13. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_479 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_480 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_481 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_482 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.5. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.6. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_483 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_484 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_485 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_486 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_487 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.3. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_488 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_489 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_490 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_491 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_492 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_493 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_494 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESSINGTON1W (662101) 0.6 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_495 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_496 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_497 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESSINGTON1W (662101) 0.6 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_498 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_499 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_500 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_501 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_502 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_503 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_504 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_505 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_506 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_507 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_508 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_509 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_510 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_511 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_512 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_513 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_514 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_515 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_516 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_517 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_518 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_519 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 b.7. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_520 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_521 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_522 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_523 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_524 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_525 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_526 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_527 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_528 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_529 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_530 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_531 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_532 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_533 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_534 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_535 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_536 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_537 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_538 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_539 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_540 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_541 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_542 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_543 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_544 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_545 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_546 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_547 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_548 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_549 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_550 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_551 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_552 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_553 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_554 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_555 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_556 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_557 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_558 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_559 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_560 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_561 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_562 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_563 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_564 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_565 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_566 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_567 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_568 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_569 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_570 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_571 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_572 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_573 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_574 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_575 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_576 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_577 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_578 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_579 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_580 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_581 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_582 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_583 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_584 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_585 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_586 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_587 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_588 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_589 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_590 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_591 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_592 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_593 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_594 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_595 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_596 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_597 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_598 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_599 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_600 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_601 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_602 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_603 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_604 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_605 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_606 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_607 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_608 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_609 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_610 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_611 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_612 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_613 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_614 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_615 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_616 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_617 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_618 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_619 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_620 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_621 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_622 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_623 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_624 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_625 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_626 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_627 | Single Phase Fault with Stuck Breaker on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply Fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. WESTBORO 3 (635018) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_628 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_629 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_630 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_631 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_632 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_633 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_634 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_635 | Single Phase Fault with Stuck Breaker on GEN-2016-075345.00 (579450) 345 kV Bus a. Apply Fault at the GEN-2016-075345.00 (579450) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-075 (579450) 345.0 kV to G16-075XFMR1 (579457) 34.5 kV Two Winding #1 b.2. GEN-2016-075 (579450) 345.0 kV to GRPR2 3 (648520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_636 | Single Phase Fault with Stuck Breaker on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-023 (584650) 345.0 kV to G15-023XFMR2 (584654) 34.5 kV to G15-023-TER2 (584659) 13.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_637 | Single Phase Fault with Stuck Breaker on GEN-2015-088345.00 (585241) 345 kV Bus a. Apply Fault at the GEN-2015-088345.00 (585241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-088 (585241) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-088 (585241) 345.0 kV to G15-088-XF-2 (585249) 34.5 kV to G15-088-TR-1 (906007) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_638 | Single Phase Fault with Stuck Breaker on GEN-2016-021345.00 (587150) 345 kV Bus a. Apply Fault at the GEN-2016-021345.00 (587150) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-021 (587150) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-021 (587150) 345.0 kV to G16-021-XF-1 (587155) 34.5 kV to G16-021-TER1 (587159) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_639 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 b.2. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_640 | Single Phase Fault with Stuck Breaker on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply Fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 b.2. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_641 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_642 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 b.2. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_643 | Single Phase Fault with Stuck Breaker on SUB704 8 69.000 (635007) 69 kV Bus a. Apply Fault at the SUB704 8 69.000 (635007) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB704 8 (635007) 69.0 kV to SUB701 8 (635004) 69.0 kV Transmission Circuit #1 b.2. SUB704 8 (635007) 69.0 kV to SUB705 8 (635008) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_644 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_645 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_646 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_647 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_648 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARD AVE 3 (635219) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_649 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REMSEN 3 (635398) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_650 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_651 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_652 | Single Phase Fault with Stuck Breaker on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CO.LINE7 (640115) 115.0 kV to BATTLCR7 (640072) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_653 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_654 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_655 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations; GEN-2018-056 | Build a 50 MVAR STATCOM at GR PRAIRIE 345 kV | Tuned (if applicable) GEN-2018-056 developer model that provides VAR support
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_656 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 3 (640520) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_657 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 7 (640521) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_658 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_659 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to HOSKINS4 (640227) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_660 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to GEN-2016-021 (587150) 345.0 kV Transmission Circuit #1 b.2. TURTLE.CRK 3 (640588) 345.0 kV to PLUMBCR.W 3 (643271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_661 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_662 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_663 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_664 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_665 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_666 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_667 | Single Phase Fault with Stuck Breaker on S1362 5 161.00 (646362) 161 kV Bus a. Apply Fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1362 5 (646362) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_668 | Single Phase Fault with Stuck Breaker on S908 8 69.000 (647908) 69 kV Bus a. Apply Fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.2. S908 8 (647908) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_669 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_670 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_671 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX5345.00 (652808) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX5345.00 (652808) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM1-LNX5 (652808) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #1 b.2. FTTHOM1-LNX5 (652808) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_672 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations; GEN-2018-056 | Build a 50 MVAR STATCOM at GR PRAIRIE 345 kV | Tuned (if applicable) GEN-2018-056 developer model that provides VAR support
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_673 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z b.2. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_674 | Single Phase Fault with Stuck Breaker on GEN-2017-181345.00 (761292) 345 kV Bus a. Apply Fault at the GEN-2017-181345.00 (761292) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-181 (761292) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-181 (761292) 345.0 kV to GEN-2017-182 (761313) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_675 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_676 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_677 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_678 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_679 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_680 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_681 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_682 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_683 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_684 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_685 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.2. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_686 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_687 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_688 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_689 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_690 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_691 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 b.2. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_692 | Single Phase Fault with Stuck Breaker on SHELDON7 115.00 (640278) 115 kV Bus a. Apply Fault at the SHELDON7 115.00 (640278) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 b.2. SHELDON7 (640278) 115.0 kV to FOLSM&PHIL7 (650242) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_693 | Single Phase Fault with Stuck Breaker on PAULINE7 115.00 (640313) 115 kV Bus a. Apply Fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to HASTING7 (640215) 115.0 kV Transmission Circuit #1 b.2. PAULINE7 (640313) 115.0 kV to HASTING7 (640215) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_694 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK4 (640343) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_695 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_696 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER_ESST8 (640141) 69.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_697 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_698 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S3456 3 (645456) 345.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_699 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_700 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_701 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_702 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1366 5 (646366) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_703 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_704 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_705 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_706 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #3 b.2. OAHE 4 (652519) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_707 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_708 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LETCHER4 (652606) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 b.2. LETCHER4 (652606) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_709 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_710 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_711 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STORLA__-BE4 (659122) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. STORLA__-BE4 (659122) 230.0 kV to HANLON 4 (652513) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_712 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_713 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_714 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL N 8 (635204) 69.0 kV to NEAL N 5 (635203) 161.0 kV Two Winding #1 b.2. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_715 | Single Phase Fault with Stuck Breaker on LEHIGH 3 345.00 (636010) 345 kV Bus a. Apply Fault at the LEHIGH 3 345.00 (636010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEHIGH 3 (636010) 345.0 kV to BVR CRK 3 (636003) 345.0 kV Transmission Circuit #1 b.2. LEHIGH 3 (636010) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_716 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_717 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 b.2. NELIGH 7 (640293) 115.0 kV to PETERSBRG.N7 (640444) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_718 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_719 | Single Phase Fault with Stuck Breaker on S909 8 69.000 (647909) 69 kV Bus a. Apply Fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_720 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_721 | Single Phase Fault with Stuck Breaker on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply Fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z b.2. GRPRAR2-LNX3 (652833) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_722 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_723 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z b.2. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_724 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_725 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z b.2. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_726 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z b.2. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_727 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_728 | Single Phase Fault with Stuck Breaker on GEN-2017-115345.00 (760746) 345 kV Bus a. Apply Fault at the GEN-2017-115345.00 (760746) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-115 (760746) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-115 (760746) 345.0 kV to G17-115XFMR1 (760747) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_729 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_730 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_731 | Single Phase Fault with Stuck Breaker on SUB703 8 69.000 (635006) 69 kV Bus a. Apply Fault at the SUB703 8 69.000 (635006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB703 8 (635006) 69.0 kV to SUB701 8 (635004) 69.0 kV Transmission Circuit #1 b.2. SUB703 8 (635006) 69.0 kV to SUB706 8 (635009) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_732 | Single Phase Fault with Stuck Breaker on HONEYCK8 69.000 (635080) 69 kV Bus a. Apply Fault at the HONEYCK8 69.000 (635080) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HONEYCK8 (635080) 69.0 kV to SUB701 8 (635004) 69.0 kV Transmission Circuit #1 b.2. HONEYCK8 (635080) 69.0 kV to MOVALLY8 (635081) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_733 | Single Phase Fault with Stuck Breaker on SUB705 8 69.000 (635008) 69 kV Bus a. Apply Fault at the SUB705 8 69.000 (635008) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB705 8 (635008) 69.0 kV to CBLUFFS8 (635002) 69.0 kV Transmission Circuit #1 b.2. SUB705 8 (635008) 69.0 kV to SUB704 8 (635007) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_734 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_735 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_736 | Single Phase Fault with Stuck Breaker on RICHLAND W 345.00 (637024) 345 kV Bus a. Apply Fault at the RICHLAND W 345.00 (637024) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAND W (637024) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. RICHLAND W (637024) 345.0 kV to J535 COL (637023) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_737 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLND 3 (635400) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 b.2. HIGHLND 3 (635400) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_738 | Single Phase Fault with Stuck Breaker on GEN-2017-144345.00 (760767) 345 kV Bus a. Apply Fault at the GEN-2017-144345.00 (760767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-144 (760767) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-144 (760767) 345.0 kV to G17-144XFMR2 (760771) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_739 | Single Phase Fault with Stuck Breaker on G18-056-TAP 345.00 (762916) 345 kV Bus a. Apply Fault at the G18-056-TAP 345.00 (762916) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. None to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_740 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_741 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_742 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_743 | Single Phase Fault with Stuck Breaker on GEN-2017-201345.00 (760788) 345 kV Bus a. Apply Fault at the GEN-2017-201345.00 (760788) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-201 (760788) 345.0 kV to SHOLES.W 3 (640589) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-201 (760788) 345.0 kV to G17-201XFMR1 (760789) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_744 | Single Phase Fault with Stuck Breaker on S1347 5 161.00 (646347) 161 kV Bus a. Apply Fault at the S1347 5 161.00 (646347) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1347 5 (646347) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1347 5 (646347) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_745 | Single Phase Fault with Stuck Breaker on S1363 5 161.00 (646363) 161 kV Bus a. Apply Fault at the S1363 5 161.00 (646363) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1363 5 (646363) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.2. S1363 5 (646363) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_746 | Single Phase Fault with Stuck Breaker on S913 8 69.000 (647913) 69 kV Bus a. Apply Fault at the S913 8 69.000 (647913) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S913 8 (647913) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S913 8 (647913) 69.0 kV to S908 8 (647908) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_747 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_748 | Single Phase Fault with Stuck Breaker on GEN-2017-182345.00 (761313) 345 kV Bus a. Apply Fault at the GEN-2017-182345.00 (761313) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-182 (761313) 345.0 kV to G17-182XFMR1 (761314) 34.5 kV Two Winding #1 b.2. GEN-2017-182 (761313) 345.0 kV to GEN-2017-181 (761292) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_749 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.2. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_750 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_751 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_752 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to GRTBEND3 (539678) 115.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_753 | Single Phase Fault with Stuck Breaker on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_754 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_755 | Single Phase Fault with Stuck Breaker on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply Fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 b.2. SPLT RK7 (603016) 115.0 kV to LAWRENC7 (603012) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_756 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_757 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_758 | Single Phase Fault with Stuck Breaker on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply Fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. E.COL. 4 (640126) 230.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_759 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_760 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_761 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_762 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_763 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_764 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_765 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_766 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_767 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to AXTELL 7 (640066) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_768 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_769 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.2. S1254 5 (646254) 161.0 kV to S1249 5 (646249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_770 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S906 S 8 (647906) 69.0 kV to S904 8 (647904) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_771 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_772 | Single Phase Fault with Stuck Breaker on S910 8 69.000 (647910) 69 kV Bus a. Apply Fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to S908 8 (647908) 69.0 kV Transmission Circuit #1 b.2. S910 8 (647910) 69.0 kV to JCT205 8 (647105) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_773 | Single Phase Fault with Stuck Breaker on S917 8 69.000 (647917) 69 kV Bus a. Apply Fault at the S917 8 69.000 (647917) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_774 | Single Phase Fault with Stuck Breaker on S921 8 69.000 (647921) 69 kV Bus a. Apply Fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_775 | Single Phase Fault with Stuck Breaker on S6866 8 69.000 (647866) 69 kV Bus a. Apply Fault at the S6866 8 69.000 (647866) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6866 8 (647866) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_776 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_777 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_778 | Single Phase Fault with Stuck Breaker on OAHE 7 115.00 (652520) 115 kV Bus a. Apply Fault at the OAHE 7 115.00 (652520) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 7 (652520) 115.0 kV to ASH TAP (652600) 115.0 kV Transmission Circuit #1 b.2. OAHE 7 (652520) 115.0 kV to IRVSIMM7 (658174) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_779 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_780 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LETCHER7 (652609) 115.0 kV to LETCHER4 (652606) 230.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 b.2. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_781 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Transfer | GROUP2_FAULT_782 | Single Phase Fault with Stuck Breaker on STORLA__-BE7115.00 (659123) 115 kV Bus a. Apply Fault at the STORLA__-BE7115.00 (659123) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STORLA__-BE7 (659123) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.2. STORLA__-BE7 (659123) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_1 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_2 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_3 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_4 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_5 | 3 Phase fault on JAGGER 3 115.00 (531360) 115 kV Bus a. Apply fault at the JAGGER 3 115.00 (531360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELER 3 (531359) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.2. BEELER 3 (531359) 115.0 kV to LIBERTYT (531495) 115.0 kV Transmission Circuit #1 b.3. JAGGER 3 (531360) 115.0 kV to DIGHTON3 (531361) 115.0 kV Transmission Circuit #1 b.4. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.5. JAGGER 3 (531360) 115.0 kV to LIBERTYT (531495) 115.0 kV Transmission Circuit #1 b.6. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.7. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_6 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_7 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_8 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_9 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_10 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_11 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_12 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_13 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_14 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_15 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_16 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_17 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_18 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_19 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_20 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_21 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_22 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_23 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_24 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_25 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_26 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscilations due to Low Voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25S | Transfer | GROUP3_FAULT_27 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_28 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_29 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_30 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_31 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_32 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_33 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_34 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_35 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_36 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_37 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_38 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_39 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_40 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_41 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_42 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_43 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_44 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_45 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_46 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_47 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_48 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_49 | 3 Phase fault on MANVILE3 115.00 (533426) 115 kV Bus a. Apply fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_50 | 3 Phase fault on REFINRY3 115.00 (533427) 115 kV Bus a. Apply fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_51 | 3 Phase fault on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_52 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_53 | 3 Phase fault on MEAD S 2 69.000 (533815) 69 kV Bus a. Apply fault at the MEAD S 2 69.000 (533815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_54 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_55 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_56 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_57 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_58 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_59 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_60 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_61 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_62 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_63 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_64 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_65 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_66 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_67 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_68 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_69 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_70 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_71 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_72 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_73 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_74 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_75 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_76 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_77 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_78 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_79 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_80 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_81 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_82 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_83 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_84 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_85 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_86 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_87 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_88 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_89 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_90 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_91 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_92 | 3 Phase fault on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_93 | 3 Phase fault on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_94 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_95 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_96 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_97 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_98 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_99 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_100 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_101 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_102 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_103 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_104 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_105 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_106 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_107 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_108 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_109 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_110 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_111 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_112 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_113 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_114 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_115 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_116 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_117 | 3 Phase fault on CORONAD3 115.00 (533394) 115 kV Bus a. Apply fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_118 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_119 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_120 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_121 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_122 | 3 Phase fault on COMOTAR4 138.00 (533037) 138 kV Bus a. Apply fault at the COMOTAR4 138.00 (533037) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_123 | 3 Phase fault on INTERST4 138.00 (533051) 138 kV Bus a. Apply fault at the INTERST4 138.00 (533051) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_124 | 3 Phase fault on 43LORAN 115.00 (533440) 115 kV Bus a. Apply fault at the 43LORAN 115.00 (533440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.3. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_125 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_126 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 b.5. DEARING1 (533089) 13.2 kV to DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_127 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 b.4. LIBERTY1 (533090) 13.2 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_128 | 3 Phase fault on NINMLTP4 138.00 (521128) 138 kV Bus a. Apply fault at the NINMLTP4 138.00 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_129 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_130 | 3 Phase fault on CDRDLTP4 138.00 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 138.00 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_131 | 3 Phase fault on BYRONTP4 138.00 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 138.00 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.2. CHRKCTY4 (520431) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.3. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. BYRONTP4 (520432) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.5. BYRONTP4 (520432) 138.0 kV to BYRON 4 (520477) 138.0 kV Transmission Circuit #1 b.6. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.7. SANDYCR4 (520433) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.8. SANDYCR4 (520433) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.9. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_132 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_133 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_134 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_135 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_136 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_137 | 3 Phase fault on NWMAID5 161.00 (512757) 161 kV Bus a. Apply fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_138 | 3 Phase fault on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_139 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_140 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_141 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_142 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_143 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_144 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_145 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_146 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_147 | 3 Phase fault on WMAIN ST5 161.00 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 161.00 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_148 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_149 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_150 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_151 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_152 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_153 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_154 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_155 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_156 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_157 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_158 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_159 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_160 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_161 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_162 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_163 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_164 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_165 | 3 Phase fault on BYPASJT2 69.000 (543084) 69 kV Bus a. Apply fault at the BYPASJT2 69.000 (543084) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYJT2 (543079) 69.0 kV to BYPASJT2 (543084) 69.0 kV Transmission Circuit #1 b.2. BYPASJT2 (543084) 69.0 kV to IND WTR2 (543086) 69.0 kV Transmission Circuit #1 b.3. BYPASJT2 (543084) 69.0 kV to LIBRTYS2 (543095) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_166 | 3 Phase fault on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_167 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_168 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_169 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_170 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_171 | 3 Phase fault on TALLGRS4 138.00 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 138.00 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_172 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_173 | 3 Phase fault on CENTENN4 138.00 (533034) 138 kV Bus a. Apply fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_174 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_175 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_176 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_177 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_178 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_179 | 3 Phase fault on ANDOVER4 138.00 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 138.00 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_180 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_181 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_182 | 3 Phase fault on MUND 3 115.00 (533282) 115 kV Bus a. Apply fault at the MUND 3 115.00 (533282) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_183 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_184 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_185 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_186 | 3 Phase fault on 17TH TP2 69.000 (533835) 69 kV Bus a. Apply fault at the 17TH TP2 69.000 (533835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_187 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_188 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_189 | 3 Phase fault on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_190 | 3 Phase fault on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.3. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_191 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_192 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_193 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_194 | 3 Phase fault on WATER1 2 69.000 (533855) 69 kV Bus a. Apply fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_195 | 3 Phase fault on WATER2 2 69.000 (533856) 69 kV Bus a. Apply fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.2. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_196 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.2. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.3. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_197 | 3 Phase fault on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_198 | 3 Phase fault on SENECA 2 69.000 (533839) 69 kV Bus a. Apply fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_199 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_200 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_201 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_202 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_203 | 3 Phase fault on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_204 | 3 Phase fault on GRDWST 2 69.000 (541286) 69 kV Bus a. Apply fault at the GRDWST 2 69.000 (541286) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDWCTY2 (541285) 69.0 kV to GRDWST 2 (541286) 69.0 kV Transmission Circuit #1 b.2. GRDWST 2 (541286) 69.0 kV to MARTCTY2 (541287) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_205 | 3 Phase fault on FROSTRD_CAP5161.00 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5161.00 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_206 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_207 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_208 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_209 | 3 Phase fault on TERRACE5 161.00 (542991) 161 kV Bus a. Apply fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_210 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_211 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_212 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_213 | 3 Phase fault on QUIND 5 161.00 (546652) 161 kV Bus a. Apply fault at the QUIND 5 161.00 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_214 | 3 Phase fault on QUIND 5 161.00 (546652) 161 kV Bus a. Apply fault at the QUIND 5 161.00 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_215 | 3 Phase fault on NEARMAN5 161.00 (546653) 161 kV Bus a. Apply fault at the NEARMAN5 161.00 (546653) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_216 | 3 Phase fault on NEARMAN5 161.00 (546653) 161 kV Bus a. Apply fault at the NEARMAN5 161.00 (546653) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_217 | 3 Phase fault on SUNSET 5 161.00 (546654) 161 kV Bus a. Apply fault at the SUNSET 5 161.00 (546654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_218 | 3 Phase fault on KAW W 5 161.00 (546655) 161 kV Bus a. Apply fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_219 | 3 Phase fault on KAW W 5 161.00 (546655) 161 kV Bus a. Apply fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_220 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_221 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_222 | 3 Phase fault on GIBBS 5 161.00 (546658) 161 kV Bus a. Apply fault at the GIBBS 5 161.00 (546658) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_223 | 3 Phase fault on CTR CTY5 161.00 (546659) 161 kV Bus a. Apply fault at the CTR CTY5 161.00 (546659) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_224 | 3 Phase fault on CTR CTY5 161.00 (546659) 161 kV Bus a. Apply fault at the CTR CTY5 161.00 (546659) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_225 | 3 Phase fault on ARMDALE5 161.00 (546661) 161 kV Bus a. Apply fault at the ARMDALE5 161.00 (546661) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_226 | 3 Phase fault on GM PLT 5 161.00 (546663) 161 kV Bus a. Apply fault at the GM PLT 5 161.00 (546663) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GM PLT 5 (546663) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_227 | 3 Phase fault on FAIRFX-5 161.00 (546667) 161 kV Bus a. Apply fault at the FAIRFX-5 161.00 (546667) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRFX-5 (546667) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_228 | 3 Phase fault on PIPER 5 161.00 (546668) 161 kV Bus a. Apply fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_229 | 3 Phase fault on PIPER 5 161.00 (546668) 161 kV Bus a. Apply fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_230 | 3 Phase fault on OAK KNOL 69.000 (546670) 69 kV Bus a. Apply fault at the OAK KNOL 69.000 (546670) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK KNOL (546670) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_231 | 3 Phase fault on OAK KNOL 69.000 (546670) 69 kV Bus a. Apply fault at the OAK KNOL 69.000 (546670) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK KNOL (546670) 69.0 kV to MAYWOOD2 (546677) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_232 | 3 Phase fault on MORRIS 2 69.000 (546672) 69 kV Bus a. Apply fault at the MORRIS 2 69.000 (546672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 2 (546672) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_233 | 3 Phase fault on MORRIS 2 69.000 (546672) 69 kV Bus a. Apply fault at the MORRIS 2 69.000 (546672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_234 | 3 Phase fault on GR WHL 2 69.000 (546673) 69 kV Bus a. Apply fault at the GR WHL 2 69.000 (546673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR WHL 2 (546673) 69.0 kV to GW TAP 1 (546675) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_235 | 3 Phase fault on SPEAKER2 69.000 (546674) 69 kV Bus a. Apply fault at the SPEAKER2 69.000 (546674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_236 | 3 Phase fault on GW TAP 1 69.000 (546675) 69 kV Bus a. Apply fault at the GW TAP 1 69.000 (546675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GW TAP 1 (546675) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_237 | 3 Phase fault on MAYWOOD2 69.000 (546677) 69 kV Bus a. Apply fault at the MAYWOOD2 69.000 (546677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD2 (546677) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_238 | 3 Phase fault on EVERETT2 69.000 (546682) 69 kV Bus a. Apply fault at the EVERETT2 69.000 (546682) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVERETT2 (546682) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_239 | 3 Phase fault on QUINDA 2 69.000 (546692) 69 kV Bus a. Apply fault at the QUINDA 2 69.000 (546692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_240 | 3 Phase fault on QUINDA 2 69.000 (546692) 69 kV Bus a. Apply fault at the QUINDA 2 69.000 (546692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_241 | 3 Phase fault on MAYSOTH5 161.00 (546722) 161 kV Bus a. Apply fault at the MAYSOTH5 161.00 (546722) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_242 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_243 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_244 | 3 Phase fault on QUIND 5 161.00 (546652) 161 kV Bus a. Apply fault at the QUIND 5 161.00 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_245 | 3 Phase fault on KAW W 5 161.00 (546655) 161 kV Bus a. Apply fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_246 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_247 | 3 Phase fault on BRMALL 2 69.000 (541283) 69 kV Bus a. Apply fault at the BRMALL 2 69.000 (541283) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMALL 2 (541283) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_248 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_249 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_250 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_251 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_252 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_253 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_254 | 3 Phase fault on SUB E 69.000 (548804) 69 kV Bus a. Apply fault at the SUB E 69.000 (548804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_255 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_256 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_257 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_258 | 3 Phase fault on SUB B 69.000 (548810) 69 kV Bus a. Apply fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_259 | 3 Phase fault on SUB J 69.000 (548811) 69 kV Bus a. Apply fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_260 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_261 | 3 Phase fault on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_262 | 3 Phase fault on STRLNGRD 69.000 (548826) 69 kV Bus a. Apply fault at the STRLNGRD 69.000 (548826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.3. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_263 | 3 Phase fault on KCPL JCT 69.000 (548832) 69 kV Bus a. Apply fault at the KCPL JCT 69.000 (548832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB F (548803) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 b.2. SUB E (548804) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_264 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_265 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_266 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_267 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_268 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_269 | 3 Phase fault on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_270 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_271 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_272 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_273 | 3 Phase fault on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCRK_S2 (543163) 69.0 kV Transmission Circuit #z1 b.2. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.3. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.4. SUGRCK_TP_W2 (543164) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.5. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_274 | 3 Phase fault on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_275 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_276 | 3 Phase fault on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_277 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_278 | 3 Phase fault on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.3. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_279 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_280 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_281 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_282 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_283 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_284 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_285 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_286 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_287 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_288 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_289 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_290 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_291 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_292 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_293 | 3 Phase fault on EDWARVL3 115.00 (533238) 115 kV Bus a. Apply fault at the EDWARVL3 115.00 (533238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_294 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_295 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_296 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_297 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_298 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_299 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_300 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_301 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_302 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_303 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_304 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_305 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_306 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_307 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_308 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_309 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_310 | 3 Phase fault on IODINE 4 138.00 (520957) 138 kV Bus a. Apply fault at the IODINE 4 138.00 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_311 | 3 Phase fault on GLASMTN4 138.00 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 138.00 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_312 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_313 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_314 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_315 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_316 | 3 Phase fault on SEILING4 138.00 (520553) 138 kV Bus a. Apply fault at the SEILING4 138.00 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_317 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_318 | 3 Phase fault on REDCLFT4 138.00 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 138.00 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_319 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_320 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_321 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_322 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_323 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_324 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_325 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_326 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_327 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_328 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_329 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_330 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_331 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_332 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_333 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_334 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_335 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_336 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_337 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_338 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_339 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_340 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_341 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_342 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Low voltage and controller oscillations; GEN-2018-030 | Build a second circuit from HOLCOMB 345 kV to Finney 345 kV
03 - Central | 25S | Transfer | GROUP3_FAULT_343 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_344 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage in the area after recovery | Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25S | Transfer | GROUP3_FAULT_345 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_346 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_347 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_348 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_349 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_350 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_351 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_352 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_353 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_354 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_355 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_356 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_357 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_358 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_359 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_360 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_361 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_362 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_363 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_364 | 3 Phase fault on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.3. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_365 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_366 | 3 Phase fault on SAWYER 3 115.00 (539649) 115 kV Bus a. Apply fault at the SAWYER 3 115.00 (539649) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAWYER 3 (539649) 115.0 kV to RVROAD (539651) 115.0 kV Transmission Circuit #1 b.2. SAWYER 3 (539649) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_367 | 3 Phase fault on MED-LDG3 115.00 (539673) 115 kV Bus a. Apply fault at the MED-LDG3 115.00 (539673) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MED-LDG3 (539673) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_368 | 3 Phase fault on SUNCITY3 115.00 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 115.00 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_369 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_370 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_371 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_372 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_373 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_374 | 3 Phase fault on BARBER 4 138.00 (539674) 138 kV Bus a. Apply fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_375 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_376 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage in the area after recovery | Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25S | Transfer | GROUP3_FAULT_377 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_378 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_379 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_380 | 3 Phase fault on NES3-1 22.000 (511840) 22 kV Bus a. Apply fault at the NES3-1 22.000 (511840) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NES3-1 (511840) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_381 | 3 Phase fault on GRECCTG_1 20.000 (512614) 20 kV Bus a. Apply fault at the GRECCTG_1 20.000 (512614) 20 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRECCTG_1 (512614) 20.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_382 | 3 Phase fault on GRECSTG_1 17.500 (512615) 17.5 kV Bus a. Apply fault at the GRECSTG_1 17.500 (512615) 17.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRECSTG_1 (512615) 17.5 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_383 | 3 Phase fault on GRDA17-1 22.800 (512688) 22.79999924 kV Bus a. Apply fault at the GRDA17-1 22.800 (512688) 22.79999924 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA17-1 (512688) 22.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_384 | 3 Phase fault on EMPEC121 13.800 (532740) 13.80000019 kV Bus a. Apply fault at the EMPEC121 13.800 (532740) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC121 (532740) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_385 | 3 Phase fault on EMPEC121 13.800 (532740) 13.80000019 kV Bus a. Apply fault at the EMPEC121 13.800 (532740) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC121 (532740) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_386 | 3 Phase fault on EMPEC341 13.800 (532741) 13.80000019 kV Bus a. Apply fault at the EMPEC341 13.800 (532741) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC341 (532741) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_387 | 3 Phase fault on EMPEC341 13.800 (532741) 13.80000019 kV Bus a. Apply fault at the EMPEC341 13.800 (532741) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC341 (532741) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_388 | 3 Phase fault on EMPEC5 1 18.000 (532742) 18 kV Bus a. Apply fault at the EMPEC5 1 18.000 (532742) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC5 1 (532742) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_389 | 3 Phase fault on EMPEC6 1 18.000 (532743) 18 kV Bus a. Apply fault at the EMPEC6 1 18.000 (532743) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC6 1 (532743) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_390 | 3 Phase fault on WCGS U1 25.000 (532751) 25 kV Bus a. Apply fault at the WCGS U1 25.000 (532751) 25 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WCGS U1 (532751) 25.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_391 | 3 Phase fault on LAC G1 1 22.000 (542955) 22 kV Bus a. Apply fault at the LAC G1 1 22.000 (542955) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC G1 1 (542955) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_392 | 3 Phase fault on LAC G2 1 24.000 (542956) 24 kV Bus a. Apply fault at the LAC G2 1 24.000 (542956) 24 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC G2 1 (542956) 24.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_393 | 3 Phase fault on NEBCTY1G 18.000 (645011) 18 kV Bus a. Apply fault at the NEBCTY1G 18.000 (645011) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEBCTY1G (645011) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_394 | 3 Phase fault on NEBCTY2G 23.000 (645012) 23 kV Bus a. Apply fault at the NEBCTY2G 23.000 (645012) 23 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEBCTY2G (645012) 23.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_395 | 3 Phase fault on G18-022GEN1 0.6000 (762584) 0.600000024 kV Bus a. Apply fault at the G18-022GEN1 0.6000 (762584) 0.600000024 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-022GEN1 (762584) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_396 | 3 Phase fault on G18-022GEN2 0.6000 (762587) 0.600000024 kV Bus a. Apply fault at the G18-022GEN2 0.6000 (762587) 0.600000024 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-022GEN2 (762587) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_397 | 3 Phase fault on G18-022GEN3 0.6300 (762588) 0.629999995 kV Bus a. Apply fault at the G18-022GEN3 0.6300 (762588) 0.629999995 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-022GEN3 (762588) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_398 | 3 Phase fault on G18-030GEN1 0.6600 (762661) 0.660000026 kV Bus a. Apply fault at the G18-030GEN1 0.6600 (762661) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-030GEN1 (762661) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_399 | 3 Phase fault on G18-031GEN1 0.6600 (762672) 0.660000026 kV Bus a. Apply fault at the G18-031GEN1 0.6600 (762672) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-031GEN1 (762672) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_400 | 3 Phase fault on G18-032GEN1 0.6500 (762683) 0.649999976 kV Bus a. Apply fault at the G18-032GEN1 0.6500 (762683) 0.649999976 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-032GEN1 (762683) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_401 | 3 Phase fault on G18-032GEN2 0.6500 (762686) 0.649999976 kV Bus a. Apply fault at the G18-032GEN2 0.6500 (762686) 0.649999976 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-032GEN2 (762686) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_402 | 3 Phase fault on G18-049-GEN10.6600 (762837) 0.660000026 kV Bus a. Apply fault at the G18-049-GEN10.6600 (762837) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-049-GEN1 (762837) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_403 | 3 Phase fault on G18-054-GEN10.6600 (762892) 0.660000026 kV Bus a. Apply fault at the G18-054-GEN10.6600 (762892) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-GEN1 (762892) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_404 | 3 Phase fault on G18-057-GEN10.6900 (762925) 0.689999998 kV Bus a. Apply fault at the G18-057-GEN10.6900 (762925) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-057-GEN1 (762925) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_405 | 3 Phase fault on G18-062-GEN10.6900 (762979) 0.689999998 kV Bus a. Apply fault at the G18-062-GEN10.6900 (762979) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-062-GEN1 (762979) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_406 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_407 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_408 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_409 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_410 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_411 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_412 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_413 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_414 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_415 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_416 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_417 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_418 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | Yes | Yes | Low voltage in the area after recovery | Operational steady state fixes (existing caps/taps/gen set points)
03 - Central | 25S | Transfer | GROUP3_FAULT_419 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_420 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_421 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_422 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_423 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_424 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_425 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_426 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_427 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_428 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_429 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_430 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_431 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_432 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_433 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_434 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_435 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_436 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_437 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_438 | 3 Phase fault on WACO S 4 138.00 (533071) 138 kV Bus a. Apply fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_439 | 3 Phase fault on WACO 4 138.00 (533072) 138 kV Bus a. Apply fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_440 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_441 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_442 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_443 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_444 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_445 | 3 Phase fault on HOOVERS2 69.000 (533806) 69 kV Bus a. Apply fault at the HOOVERS2 69.000 (533806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_446 | 3 Phase fault on PLAZA E2 69.000 (533829) 69 kV Bus a. Apply fault at the PLAZA E2 69.000 (533829) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_447 | 3 Phase fault on PLAZA M2 69.000 (533857) 69 kV Bus a. Apply fault at the PLAZA M2 69.000 (533857) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_448 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_449 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_450 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_451 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_452 | 3 Phase fault on FROSTRD_CAP5161.00 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5161.00 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_453 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_454 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_455 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_456 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_457 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_458 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_459 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_460 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_461 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_462 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_463 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_464 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_465 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_466 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_467 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_468 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_469 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_470 | 3 Phase fault on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_471 | 3 Phase fault on FROSTRD5 161.00 (541220) 161 kV Bus a. Apply fault at the FROSTRD5 161.00 (541220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_472 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_473 | 3 Phase fault on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_474 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_475 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_476 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_477 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_478 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_479 | 3 Phase fault on G18-054-TAP 161.00 (541231) 161 kV Bus a. Apply fault at the G18-054-TAP 161.00 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-TAP (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_480 | 3 Phase fault on G18-054-TAP 161.00 (541231) 161 kV Bus a. Apply fault at the G18-054-TAP 161.00 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-TAP (541231) 161.0 kV to NRAYMORE (541317) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_481 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_482 | 3 Phase fault on LNGVW 2 69.000 (541282) 69 kV Bus a. Apply fault at the LNGVW 2 69.000 (541282) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to BRMALL 2 (541283) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_483 | 3 Phase fault on NRAYMORE 161.00 (541317) 161 kV Bus a. Apply fault at the NRAYMORE 161.00 (541317) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_484 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_485 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_486 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_487 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_488 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM_CAP5 (542947) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_489 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_490 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN_CAP5 (542950) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_491 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_492 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_493 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_494 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_495 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_496 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_497 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_498 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_499 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_500 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_501 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_502 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_503 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_504 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_505 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_506 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_507 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_508 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_509 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_510 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_511 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_512 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_513 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_514 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_515 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_516 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_517 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_518 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_519 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_520 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_521 | 3 Phase fault on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSTWN5 (542990) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_522 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_523 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_524 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_525 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_526 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_527 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_528 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_529 | 3 Phase fault on LVISTA 5 161.00 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 161.00 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_530 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_531 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_532 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_533 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_534 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_535 | 3 Phase fault on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_536 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_537 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_538 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_539 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_540 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_541 | 3 Phase fault on SUGRCRK_S2 69.000 (543163) 69 kV Bus a. Apply fault at the SUGRCRK_S2 69.000 (543163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_S2 (543163) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_542 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_543 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_544 | 3 Phase fault on MILLST 5 161.00 (546224) 161 kV Bus a. Apply fault at the MILLST 5 161.00 (546224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_545 | 3 Phase fault on SPEAKER2 69.000 (546674) 69 kV Bus a. Apply fault at the SPEAKER2 69.000 (546674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW 2 (546678) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_546 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to EVERETT2 (546682) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_547 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_548 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_549 | 3 Phase fault on MUNCIE 2 69.000 (546681) 69 kV Bus a. Apply fault at the MUNCIE 2 69.000 (546681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNCIE 2 (546681) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_550 | 3 Phase fault on MUNCIE 2 69.000 (546681) 69 kV Bus a. Apply fault at the MUNCIE 2 69.000 (546681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNCIE 2 (546681) 69.0 kV to QUINDA 2 (546692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_551 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_552 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_553 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_554 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_555 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_556 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_557 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_558 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_559 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G18-030-TAP (762662) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_560 | 3 Phase fault on GI94_POI 345.00 (709400) 345 kV Bus a. Apply fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_561 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_562 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT12_2 (543664) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_563 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_564 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_565 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_566 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_567 | 3 Phase fault on MOORLND4 138.00 (520999) 138 kV Bus a. Apply fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 (520999) 138.0 kV to MOORLND2 (520995) 69.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_568 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_569 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_570 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_571 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_572 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_573 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_574 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_575 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_576 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_577 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_578 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_579 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_580 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_581 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_582 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_583 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_584 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_585 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_586 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_587 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_588 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_589 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_590 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_591 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_592 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_593 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_594 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_595 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_596 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_597 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_598 | 3 Phase fault on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_599 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_600 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_601 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_602 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_603 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_604 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_605 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_606 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_607 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_608 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_609 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_610 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_611 | 3 Phase fault on HEC 3 115.00 (533419) 115 kV Bus a. Apply fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_612 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_613 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_614 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_615 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_616 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_617 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_618 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_619 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_620 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY2 (541287) 69.0 kV to MARTCTY5 (541210) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_621 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_622 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_623 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_624 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_625 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_626 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_627 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_628 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_629 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_630 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_631 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_632 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_633 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_634 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_635 | 3 Phase fault on IATAN 7 345.00 (542982) 345 kV Bus a. Apply fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_636 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_637 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_638 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_639 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_640 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_641 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_642 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_643 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_644 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_645 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_646 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_647 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_648 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_649 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_650 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_651 | 3 Phase fault on SUB M 69.000 (548815) 69 kV Bus a. Apply fault at the SUB M 69.000 (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_652 | 3 Phase fault on SUB N 69.000 (548821) 69 kV Bus a. Apply fault at the SUB N 69.000 (548821) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_653 | 3 Phase fault on SUB C 69.000 (548825) 69 kV Bus a. Apply fault at the SUB C 69.000 (548825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB C (548825) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_654 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_1 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_2 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.3. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 b.4. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #1 b.5. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.6. WOODWRD4 (514785) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #2 b.7. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.8. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_3 | Single Phase Fault with Stuck Breaker on ECKLES-161 161.00 (548808) 161 kV Bus a. Apply Fault at the ECKLES-161 161.00 (548808) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_4 | Single Phase Fault with Stuck Breaker on BARBER 5 161.00 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_5 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_6 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_7 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_8 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_9 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_10 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_11 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_12 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_13 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_14 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_15 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_16 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_17 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_18 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_19 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_20 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_21 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_22 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_23 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_24 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_25 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_26 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_27 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_28 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_29 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_30 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_31 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_32 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_33 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_34 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_35 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_36 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_37 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_38 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_39 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_40 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_41 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_42 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_43 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_44 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_45 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_46 | Single Phase Fault with Stuck Breaker on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply Fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_47 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_48 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_49 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_50 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 b.4. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_51 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_52 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_53 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_54 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_55 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_56 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_57 | Single Phase Fault with Stuck Breaker on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply Fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_58 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_59 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_60 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_61 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_62 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_63 | Single Phase Fault with Stuck Breaker on OUSPRT 4 138.00 (515398) 138 kV Bus a. Apply Fault at the OUSPRT 4 138.00 (515398) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OUSPRT 1 (515397) 34.5 kV to OUSPRTC1 (515928) 34.5 kV Transmission Circuit #1 b.2. OUSPRT 1 (515397) 34.5 kV to OUSPRT 4 (515398) 138.0 kV to OUSPRT T (515396) 10.0 kV Three Winding #1 b.3. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_64 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_65 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_66 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_67 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_68 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_69 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_70 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_71 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_72 | Single Phase Fault with Stuck Breaker on BARBER 5 161.00 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.4. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.5. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.6. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_73 | Single Phase Fault with Stuck Breaker on QUIND 5 161.00 (546652) 161 kV Bus a. Apply Fault at the QUIND 5 161.00 (546652) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 b.2. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 b.3. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 b.4. QUIND 5 (546652) 161.0 kV to QGEN2 1 (546698) 15.0 kV Two Winding #1 b.5. QUIND 5 (546652) 161.0 kV to QCT3 1 (546701) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_74 | Single Phase Fault with Stuck Breaker on NEARMAN5 161.00 (546653) 161 kV Bus a. Apply Fault at the NEARMAN5 161.00 (546653) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 b.2. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 b.3. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 b.4. NEARMAN5 (546653) 161.0 kV to NM4BUS (546751) 161.0 kV Transmission Circuit #1 b.5. NEARMAN5 (546653) 161.0 kV to GEN-2018-062 (762976) 161.0 kV Transmission Circuit #1 b.6. NEARMAN5 (546653) 161.0 kV to NMISOBUS (546703) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_75 | Single Phase Fault with Stuck Breaker on SUNSET 5 161.00 (546654) 161 kV Bus a. Apply Fault at the SUNSET 5 161.00 (546654) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 b.2. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_76 | Single Phase Fault with Stuck Breaker on KAW W 5 161.00 (546655) 161 kV Bus a. Apply Fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.2. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.4. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_77 | Single Phase Fault with Stuck Breaker on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply Fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.4. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_78 | Single Phase Fault with Stuck Breaker on GIBBS 5 161.00 (546658) 161 kV Bus a. Apply Fault at the GIBBS 5 161.00 (546658) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.2. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_79 | Single Phase Fault with Stuck Breaker on CTR CTY5 161.00 (546659) 161 kV Bus a. Apply Fault at the CTR CTY5 161.00 (546659) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 b.2. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_80 | Single Phase Fault with Stuck Breaker on ARMDALE5 161.00 (546661) 161 kV Bus a. Apply Fault at the ARMDALE5 161.00 (546661) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 b.2. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_81 | Single Phase Fault with Stuck Breaker on GM PLT 5 161.00 (546663) 161 kV Bus a. Apply Fault at the GM PLT 5 161.00 (546663) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 b.2. GM PLT 5 (546663) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_82 | Single Phase Fault with Stuck Breaker on TURNER 5 161.00 (546665) 161 kV Bus a. Apply Fault at the TURNER 5 161.00 (546665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 b.2. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_83 | Single Phase Fault with Stuck Breaker on FAIRFX-5 161.00 (546667) 161 kV Bus a. Apply Fault at the FAIRFX-5 161.00 (546667) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 b.2. FAIRFX-5 (546667) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_84 | Single Phase Fault with Stuck Breaker on PIPER 5 161.00 (546668) 161 kV Bus a. Apply Fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.2. PIPER 5 (546668) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_85 | Single Phase Fault with Stuck Breaker on WOLCOTT5 161.00 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 161.00 (546669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_86 | Single Phase Fault with Stuck Breaker on FIBGLAS5 161.00 (546684) 161 kV Bus a. Apply Fault at the FIBGLAS5 161.00 (546684) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GM PLT 5 (546663) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 b.2. FAIRFX-5 (546667) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_87 | Single Phase Fault with Stuck Breaker on MAYSOTH5 161.00 (546722) 161 kV Bus a. Apply Fault at the MAYSOTH5 161.00 (546722) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.2. PIPER 5 (546668) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.3. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_88 | Single Phase Fault with Stuck Breaker on METRO 5 161.00 (546742) 161 kV Bus a. Apply Fault at the METRO 5 161.00 (546742) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.4. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_89 | Single Phase Fault with Stuck Breaker on MUNCIE 5 161.00 (546750) 161 kV Bus a. Apply Fault at the MUNCIE 5 161.00 (546750) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 b.2. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 b.3. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_90 | Single Phase Fault with Stuck Breaker on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply Fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 b.2. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_91 | Single Phase Fault with Stuck Breaker on MILLST 5 161.00 (546224) 161 kV Bus a. Apply Fault at the MILLST 5 161.00 (546224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 b.2. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_92 | Single Phase Fault with Stuck Breaker on KAW W 5 161.00 (546655) 161 kV Bus a. Apply Fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.2. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.4. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_93 | Single Phase Fault with Stuck Breaker on MORRIS 2 69.000 (546672) 69 kV Bus a. Apply Fault at the MORRIS 2 69.000 (546672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 2 (546672) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 b.2. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_94 | Single Phase Fault with Stuck Breaker on GR WHL 2 69.000 (546673) 69 kV Bus a. Apply Fault at the GR WHL 2 69.000 (546673) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR WHL 2 (546673) 69.0 kV to GW TAP 1 (546675) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_95 | Single Phase Fault with Stuck Breaker on SPEAKER2 69.000 (546674) 69 kV Bus a. Apply Fault at the SPEAKER2 69.000 (546674) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW 2 (546678) 69.0 kV Transmission Circuit #1 b.2. SPEAKER2 (546674) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_96 | Single Phase Fault with Stuck Breaker on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply Fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK KNOL (546670) 69.0 kV to MAYWOOD2 (546677) 69.0 kV Transmission Circuit #1 b.2. MAYWOOD2 (546677) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 b.3. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_97 | Single Phase Fault with Stuck Breaker on KAW 2 69.000 (546678) 69 kV Bus a. Apply Fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW 2 (546678) 69.0 kV Transmission Circuit #1 b.2. KAW 2 (546678) 69.0 kV to EVERETT2 (546682) 69.0 kV Transmission Circuit #1 b.3. KAW 2 (546678) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 b.4. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_98 | Single Phase Fault with Stuck Breaker on MUNCIE 2 69.000 (546681) 69 kV Bus a. Apply Fault at the MUNCIE 2 69.000 (546681) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUNCIE 2 (546681) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 b.2. MUNCIE 2 (546681) 69.0 kV to QUINDA 2 (546692) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_99 | Single Phase Fault with Stuck Breaker on EVERETT2 69.000 (546682) 69 kV Bus a. Apply Fault at the EVERETT2 69.000 (546682) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAW 2 (546678) 69.0 kV to EVERETT2 (546682) 69.0 kV Transmission Circuit #1 b.2. EVERETT2 (546682) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_100 | Single Phase Fault with Stuck Breaker on COL PAL2 69.000 (546687) 69 kV Bus a. Apply Fault at the COL PAL2 69.000 (546687) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAW 2 (546678) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 b.2. MUNCIE 2 (546681) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_101 | Single Phase Fault with Stuck Breaker on KAW W 5 161.00 (546655) 161 kV Bus a. Apply Fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 b.2. SPEAKER2 (546674) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 b.3. GW TAP 1 (546675) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 b.4. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_102 | Single Phase Fault with Stuck Breaker on QUINDC 2 69.000 (546695) 69 kV Bus a. Apply Fault at the QUINDC 2 69.000 (546695) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUNCIE 2 (546681) 69.0 kV to QUINDA 2 (546692) 69.0 kV Transmission Circuit #1 b.2. QUINDA 2 (546692) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 b.3. QUINDA 2 (546692) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 b.4. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 b.5. EVERETT2 (546682) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 b.6. QUINDB 2 (546694) 69.0 kV to QUINDC 2 (546695) 69.0 kV Transmission Circuit #1 b.7. QUINDB 2 (546694) 69.0 kV to QGEN1 1 (546697) 13.8 kV Two Winding #1 b.8. QUINDC 2 (546695) 69.0 kV to QCT2 1 (546700) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_103 | Single Phase Fault with Stuck Breaker on V WEST2 69.000 (546693) 69 kV Bus a. Apply Fault at the V WEST2 69.000 (546693) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYWOOD2 (546677) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 b.2. QUINDA 2 (546692) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_104 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_105 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_106 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_107 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_108 | Single Phase Fault with Stuck Breaker on GRPLNS-CB2-134.500 (523126) 34.5 kV Bus a. Apply Fault at the GRPLNS-CB2-134.500 (523126) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_109 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to None Transmission Circuit #1 b.7. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.8. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_110 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_111 | Single Phase Fault with Stuck Breaker on GRECCTG_1 20.000 (512614) 20 kV Bus a. Apply Fault at the GRECCTG_1 20.000 (512614) 20 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECCTG_1 (512614) 20.0 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GRECCTG_1 (512614) 20.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_112 | Single Phase Fault with Stuck Breaker on GRECSTG_1 17.500 (512615) 17.5 kV Bus a. Apply Fault at the GRECSTG_1 17.500 (512615) 17.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECSTG_1 (512615) 17.5 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GRECSTG_1 (512615) 17.5 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_113 | Single Phase Fault with Stuck Breaker on GRDA17-1 22.800 (512688) 22.79999924 kV Bus a. Apply Fault at the GRDA17-1 22.800 (512688) 22.79999924 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA17-1 (512688) 22.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_114 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_115 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_116 | Single Phase Fault with Stuck Breaker on KERR GR5 161.00 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to KERR BRK1 5 (512770) 161.0 kV Transmission Circuit #z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_117 | Single Phase Fault with Stuck Breaker on KERR GR5 161.00 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 b.2. KERR GR5 (512635) 161.0 kV to KERR BRK4 5 (512771) 161.0 kV Transmission Circuit #z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_118 | Single Phase Fault with Stuck Breaker on NWMAID5 161.00 (512757) 161 kV Bus a. Apply Fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_119 | Single Phase Fault with Stuck Breaker on NWMAID5 161.00 (512757) 161 kV Bus a. Apply Fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_120 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_121 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_122 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_123 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_124 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_125 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_126 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_127 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV1 5 (513593) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_128 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV2 5 (513595) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_129 | Single Phase Fault with Stuck Breaker on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER1 1 (512833) 13.8 kV Three Winding #1 b.4. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_130 | Single Phase Fault with Stuck Breaker on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER2 1 (512834) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_131 | Single Phase Fault with Stuck Breaker on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_132 | Single Phase Fault with Stuck Breaker on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_133 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_134 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_135 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_136 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_137 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_138 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_139 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_140 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_141 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_142 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_143 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_144 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_145 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_146 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_147 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_148 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.3. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_149 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_150 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_151 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE5 (512751) 161.0 kV to TONNEC2 (512753) 69.0 kV to TONNEC1 (512754) 13.2 kV Three Winding #1 b.4. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_152 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. SILMCTY5 (512643) 161.0 kV to TONECE5 (512751) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_153 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 b.4. FARML 4 (512734) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_154 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.4. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.7. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_155 | Single Phase Fault with Stuck Breaker on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 b.4. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR2 (512815) 13.8 kV Three Winding #2 b.5. CLARMR 5 (512651) 161.0 kV to CLARMR 4 (512707) 138.0 kV to CLARMR4 (512813) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_156 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_157 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_158 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_159 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECSTG_1 (512615) 17.5 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_160 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECCTG_1 (512614) 20.0 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_161 | Single Phase Fault with Stuck Breaker on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_162 | Single Phase Fault with Stuck Breaker on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply Fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 b.3. DRYGULCH5 (512629) 161.0 kV to GEN-2017-073 (589110) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_163 | Single Phase Fault with Stuck Breaker on GERALDGAY5 161.00 (512760) 161 kV Bus a. Apply Fault at the GERALDGAY5 161.00 (512760) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_164 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_165 | Single Phase Fault with Stuck Breaker on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.4. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_166 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_167 | Single Phase Fault with Stuck Breaker on KERR GR5 161.00 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_168 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_169 | Single Phase Fault with Stuck Breaker on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_170 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_171 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.3. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_172 | Single Phase Fault with Stuck Breaker on KERR GR5 161.00 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_173 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_174 | Single Phase Fault with Stuck Breaker on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply Fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_175 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_176 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_177 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_178 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_179 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_180 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_181 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_182 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_183 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_184 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_185 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_186 | Single Phase Fault with Stuck Breaker on PAWN-ED3 115.00 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 115.00 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.4. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to GEN-2016-016 (587120) 115.0 kV Transmission Circuit #1 b.6. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.7. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.8. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.9. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.10. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.11. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_187 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_188 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_189 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_190 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_191 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.5. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_192 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_193 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_194 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_195 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_196 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_197 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_198 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_199 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_200 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_201 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_202 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_203 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_204 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_205 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_206 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_207 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_208 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_209 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_210 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_211 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_212 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_213 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_214 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_215 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_216 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_217 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_218 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_219 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_220 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_221 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_222 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_223 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_224 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_225 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_226 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_227 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_228 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_229 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_230 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_231 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_232 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_233 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_234 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_235 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_236 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_237 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_238 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_239 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_240 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_241 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_242 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.5. S1216 5 (646216) 161.0 kV to S916 8 (647916) 69.0 kV Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_243 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.5. S1216 5 (646216) 161.0 kV to S916 8 (647916) 69.0 kV Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_244 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.5. S1216 5 (646216) 161.0 kV to S916 8 (647916) 69.0 kV Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_245 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_246 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_247 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_248 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_249 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_250 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_251 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_252 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_253 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_254 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_255 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_256 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_257 | Single Phase Fault with Stuck Breaker on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_258 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_259 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_260 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_261 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_262 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_263 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_264 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_265 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_266 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_267 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_268 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.6. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_269 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_270 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_271 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_272 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_273 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_274 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_275 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_276 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_277 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_278 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to RCKFALL4 (515427) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_279 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_280 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_281 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_282 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_283 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_284 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 b.4. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_285 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_286 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.3. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 b.4. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #1 b.5. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.6. WOODWRD4 (514785) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #2 b.7. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.8. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.10. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_287 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_288 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_289 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_290 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_291 | Single Phase Fault with Stuck Breaker on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_292 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_293 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_294 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_295 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_296 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_297 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_298 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_299 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_300 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_301 | Single Phase Fault with Stuck Breaker on G07621119-20345.00 (515599) 345 kV Bus a. Apply Fault at the G07621119-20345.00 (515599) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G07621119-20 (515599) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. G07621119-20 (515599) 345.0 kV to GREAT_WESTRN (585410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_302 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_303 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND4 (520999) 138.0 kV to PIC4 (520425) 138.0 kV Transmission Circuit #1 b.2. MOORLND4 (520999) 138.0 kV to ASPEN 4 (520462) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_304 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_305 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_306 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_307 | Single Phase Fault with Stuck Breaker on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply Fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 b.2. SCOTCTY3 (531433) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_308 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_309 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_310 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_311 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to GEARY 7 (532767) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_312 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to GEN-2017-125 (761901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_313 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_314 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_315 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_316 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_317 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_318 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_319 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_320 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_321 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_322 | Single Phase Fault with Stuck Breaker on REFINRY3 115.00 (533427) 115 kV Bus a. Apply Fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REFINRY3 (533427) 115.0 kV to EMCPHER3 (533417) 115.0 kV Transmission Circuit #1 b.2. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_323 | Single Phase Fault with Stuck Breaker on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply Fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUNDRG3 (533429) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. MOUNDRG3 (533429) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_324 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_325 | Single Phase Fault with Stuck Breaker on MED-LDG3 115.00 (539673) 115 kV Bus a. Apply Fault at the MED-LDG3 115.00 (539673) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. MED-LDG3 (539673) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_326 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_327 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_328 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_329 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_330 | Single Phase Fault with Stuck Breaker on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 b.2. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_331 | Single Phase Fault with Stuck Breaker on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply Fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_332 | Single Phase Fault with Stuck Breaker on TWA 5 161.00 (541214) 161 kV Bus a. Apply Fault at the TWA 5 161.00 (541214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 b.2. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_333 | Single Phase Fault with Stuck Breaker on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply Fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 b.2. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_334 | Single Phase Fault with Stuck Breaker on FROSTRD5 161.00 (541220) 161 kV Bus a. Apply Fault at the FROSTRD5 161.00 (541220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 b.2. FROSTRD5 (541220) 161.0 kV to FROSTRD_CAP5 (541139) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_335 | Single Phase Fault with Stuck Breaker on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply Fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to WSTELEC_CAP5 (541149) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_336 | Single Phase Fault with Stuck Breaker on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply Fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 b.2. GRDVWE 5 (541223) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_337 | Single Phase Fault with Stuck Breaker on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply Fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 b.2. LNGVW 5 (541224) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_338 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HSNVL 5 (541239) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_339 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_340 | Single Phase Fault with Stuck Breaker on G18-054-TAP 161.00 (541231) 161 kV Bus a. Apply Fault at the G18-054-TAP 161.00 (541231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-054-TAP (541231) 161.0 kV to NRAYMORE (541317) 161.0 kV Transmission Circuit #1 b.2. G18-054-TAP (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_341 | Single Phase Fault with Stuck Breaker on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply Fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWINBG5 (541243) 161.0 kV to PHILL 5 (541225) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_342 | Single Phase Fault with Stuck Breaker on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply Fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. LBRTYST5 (541248) 161.0 kV to LIBRTYS2 (543095) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_343 | Single Phase Fault with Stuck Breaker on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply Fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 b.2. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_344 | Single Phase Fault with Stuck Breaker on BRMALL 2 69.000 (541283) 69 kV Bus a. Apply Fault at the BRMALL 2 69.000 (541283) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMALL 2 (541283) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 b.2. BRMALL 2 (541283) 69.0 kV to LNGVW 2 (541282) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_345 | Single Phase Fault with Stuck Breaker on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply Fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDVWTP2 (541284) 69.0 kV to LNGVW 2 (541282) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_346 | Single Phase Fault with Stuck Breaker on GRDWCTY2 69.000 (541285) 69 kV Bus a. Apply Fault at the GRDWCTY2 69.000 (541285) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDWCTY2 (541285) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDWCTY2 (541285) 69.0 kV to GRDWST 2 (541286) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_347 | Single Phase Fault with Stuck Breaker on GRDWST 2 69.000 (541286) 69 kV Bus a. Apply Fault at the GRDWST 2 69.000 (541286) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDWST 2 (541286) 69.0 kV to MARTCTY2 (541287) 69.0 kV Transmission Circuit #1 b.2. GRDWST 2 (541286) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_348 | Single Phase Fault with Stuck Breaker on NRAYMORE 161.00 (541317) 161 kV Bus a. Apply Fault at the NRAYMORE 161.00 (541317) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRAYMORE (541317) 161.0 kV to G18-054-TAP (541231) 161.0 kV Transmission Circuit #1 b.2. NRAYMORE (541317) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_349 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_350 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_351 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_352 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 b.2. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_353 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 b.2. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_354 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_355 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_356 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_357 | Single Phase Fault with Stuck Breaker on TROOST 5 161.00 (542986) 161 kV Bus a. Apply Fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_358 | Single Phase Fault with Stuck Breaker on GRAND 5 161.00 (542987) 161 kV Bus a. Apply Fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_359 | Single Phase Fault with Stuck Breaker on GRAND W5 161.00 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_360 | Single Phase Fault with Stuck Breaker on NAVY 5 161.00 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_361 | Single Phase Fault with Stuck Breaker on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply Fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSTWN5 (542990) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. CROSTWN5 (542990) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_362 | Single Phase Fault with Stuck Breaker on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply Fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_363 | Single Phase Fault with Stuck Breaker on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply Fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHTOWN5 (542993) 161.0 kV to BENDIX 5 (542992) 161.0 kV Transmission Circuit #1 b.2. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_364 | Single Phase Fault with Stuck Breaker on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply Fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDTOWN5 (542996) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 b.2. MIDTOWN5 (542996) 161.0 kV to ROEPARK5 (543040) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_365 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_366 | Single Phase Fault with Stuck Breaker on LVISTA 5 161.00 (542998) 161 kV Bus a. Apply Fault at the LVISTA 5 161.00 (542998) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_367 | Single Phase Fault with Stuck Breaker on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply Fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_368 | Single Phase Fault with Stuck Breaker on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply Fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_369 | Single Phase Fault with Stuck Breaker on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_370 | Single Phase Fault with Stuck Breaker on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 b.2. GLADSTN5 (543016) 161.0 kV to GLADSTN_CAP5 (542946) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_371 | Single Phase Fault with Stuck Breaker on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply Fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 b.2. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_372 | Single Phase Fault with Stuck Breaker on BARRY 5 161.00 (543019) 161 kV Bus a. Apply Fault at the BARRY 5 161.00 (543019) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRY 5 (543019) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_373 | Single Phase Fault with Stuck Breaker on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply Fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMGHAM5 (543020) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. BRMGHAM5 (543020) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_374 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 b.2. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_375 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_376 | Single Phase Fault with Stuck Breaker on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply Fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.2. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_377 | Single Phase Fault with Stuck Breaker on COURTNY2 69.000 (543085) 69 kV Bus a. Apply Fault at the COURTNY2 69.000 (543085) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_378 | Single Phase Fault with Stuck Breaker on IND WTR2 69.000 (543086) 69 kV Bus a. Apply Fault at the IND WTR2 69.000 (543086) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IND WTR2 (543086) 69.0 kV to BYPASJT2 (543084) 69.0 kV Transmission Circuit #1 b.2. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_379 | Single Phase Fault with Stuck Breaker on LAFJCT 2 69.000 (543104) 69 kV Bus a. Apply Fault at the LAFJCT 2 69.000 (543104) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAFJCT 2 (543104) 69.0 kV to IND WTR2 (543086) 69.0 kV Transmission Circuit #1 b.2. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_380 | Single Phase Fault with Stuck Breaker on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply Fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILCKJT2 (543110) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. MILCKJT2 (543110) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_381 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_W269.000 (543164) 69 kV Bus a. Apply Fault at the SUGRCK_TP_W269.000 (543164) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_W2 (543164) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_382 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply Fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_383 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_384 | Single Phase Fault with Stuck Breaker on SUB I 69.000 (548800) 69 kV Bus a. Apply Fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 b.2. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_385 | Single Phase Fault with Stuck Breaker on SUB K 69.000 (548801) 69 kV Bus a. Apply Fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_386 | Single Phase Fault with Stuck Breaker on SUB H 69.000 (548802) 69 kV Bus a. Apply Fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB H (548802) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_387 | Single Phase Fault with Stuck Breaker on SUB F 69.000 (548803) 69 kV Bus a. Apply Fault at the SUB F 69.000 (548803) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB F (548803) 69.0 kV to HAWTH 2 (543080) 69.0 kV Transmission Circuit #1 b.2. SUB F (548803) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_388 | Single Phase Fault with Stuck Breaker on SUB E 69.000 (548804) 69 kV Bus a. Apply Fault at the SUB E 69.000 (548804) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 b.2. SUB E (548804) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_389 | Single Phase Fault with Stuck Breaker on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply Fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_390 | Single Phase Fault with Stuck Breaker on SUB J 69.000 (548811) 69 kV Bus a. Apply Fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB J (548811) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_391 | Single Phase Fault with Stuck Breaker on SUB N-161 161.00 (548820) 161 kV Bus a. Apply Fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_392 | Single Phase Fault with Stuck Breaker on SUB C 69.000 (548825) 69 kV Bus a. Apply Fault at the SUB C 69.000 (548825) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB C (548825) 69.0 kV to SUB I (548800) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_393 | Single Phase Fault with Stuck Breaker on G15-052T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15-052T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15-052T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_394 | Single Phase Fault with Stuck Breaker on G16-003-TAP 345.00 (560071) 345 kV Bus a. Apply Fault at the G16-003-TAP 345.00 (560071) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #2 b.2. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_395 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_396 | Single Phase Fault with Stuck Breaker on G14-001-TAP 345.00 (562476) 345 kV Bus a. Apply Fault at the G14-001-TAP 345.00 (562476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G14-001-TAP (562476) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. G14-001-TAP (562476) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_397 | Single Phase Fault with Stuck Breaker on GEN-2016-111345.00 (587880) 345 kV Bus a. Apply Fault at the GEN-2016-111345.00 (587880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-111 (587880) 345.0 kV to G16-111XFMR1 (587881) 34.5 kV Two Winding #1 b.2. GEN-2016-111 (587880) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_398 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR1 (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_399 | Single Phase Fault with Stuck Breaker on GEN-2017-022138.00 (588660) 138 kV Bus a. Apply Fault at the GEN-2017-022138.00 (588660) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-022 (588660) 138.0 kV to G17-022XFMR1 (588661) 34.5 kV Two Winding #1 b.2. GEN-2017-022 (588660) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_400 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_401 | Single Phase Fault with Stuck Breaker on GI94_POI 345.00 (709400) 345 kV Bus a. Apply Fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 b.2. GI94_POI (709400) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_402 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_403 | Single Phase Fault with Stuck Breaker on GEN-2017-209345.00 (760914) 345 kV Bus a. Apply Fault at the GEN-2017-209345.00 (760914) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-209 (760914) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-209 (760914) 345.0 kV to G17-209XFMR1 (760915) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_404 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 b.2. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_405 | Single Phase Fault with Stuck Breaker on FLINTCR5 161.00 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 161.00 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to GENTRY 5 (504201) 161.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to TONTITN5 (506957) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_406 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_407 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_408 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM6 (511557) 230.0 kV to ELKCITY6 (511490) 230.0 kV Transmission Circuit #1 b.2. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_409 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to 5CHOTEAU1 (300069) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_410 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_411 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_412 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to DELWARE4 (510379) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to SCOFCTY4 (510378) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_413 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_414 | Single Phase Fault with Stuck Breaker on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IGLOOV 7 (513596) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_415 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_416 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to IODINE-4 (514796) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_417 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_418 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_419 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_420 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 b.2. SETAB 3 (531464) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_421 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR3 (531510) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_422 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 7 (532769) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_423 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to JEC N 7 (532766) 345.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_424 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_425 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to BENTON 7 (532791) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_426 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_427 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_428 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 b.2. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_429 | Single Phase Fault with Stuck Breaker on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply Fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDIAN 4 (532990) 138.0 kV to BENTON 4 (532986) 138.0 kV Transmission Circuit #1 b.2. MIDIAN 4 (532990) 138.0 kV to BUTLER 4 (532987) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_430 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_431 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUND 4 (533013) 138.0 kV to MOUND 2 (533742) 69.0 kV to MOUND1X1 (533095) 13.2 kV Three Winding #1 b.2. MOUND 4 (533013) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_432 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.2. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_433 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.2. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_434 | Single Phase Fault with Stuck Breaker on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_435 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_436 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_437 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_438 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_439 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS4 (533050) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_440 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOEASTE4 (533060) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_441 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOEASTW4 (533061) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. NOEASTW4 (533061) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_442 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_443 | Single Phase Fault with Stuck Breaker on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply Fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. DAVIS 3 (533415) 115.0 kV to CITIES 3 (533414) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_444 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEC 3 (533419) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_445 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_446 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 b.2. LIBERT-2 (533697) 69.0 kV to SUNFLRS2 (533670) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_447 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 3 (539760) 115.0 kV to SAWYER 3 (539649) 115.0 kV Transmission Circuit #1 b.2. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_448 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_449 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_450 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_451 | Single Phase Fault with Stuck Breaker on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply Fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCTY2 (541287) 69.0 kV to MARTCTY5 (541210) 161.0 kV Two Winding #1 b.2. MARTCTY2 (541287) 69.0 kV to GRDWST 2 (541286) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_452 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_453 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_454 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_455 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_456 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_457 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_458 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to MIAMI 5 (512631) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_459 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_460 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_461 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_462 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_463 | Single Phase Fault with Stuck Breaker on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply Fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. EDWARVL3 (533238) 115.0 kV to EDWRDVL5 (532912) 161.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_464 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARSONS2 (533704) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.2. PARSONS2 (533704) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_465 | Single Phase Fault with Stuck Breaker on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply Fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_466 | Single Phase Fault with Stuck Breaker on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply Fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHERIDN2 (533841) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV to CANALS 2 (533784) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_467 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_468 | Single Phase Fault with Stuck Breaker on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply Fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KCSOUTH5 (541245) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 b.2. KCSOUTH5 (541245) 161.0 kV to G18-054-TAP (541231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_469 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 b.2. SUB M (548815) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_470 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU2 (301348) 161.0 kV to 5SPORTSMAN (300741) 161.0 kV Transmission Circuit #1 b.2. 5CHOTEAU2 (301348) 161.0 kV to 5CHOTEAU1 (300069) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_471 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_472 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDBORDT (755000) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. WWDBORDT (755000) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_473 | Single Phase Fault with Stuck Breaker on GEN-2017-203345.00 (760809) 345 kV Bus a. Apply Fault at the GEN-2017-203345.00 (760809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-203 (760809) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-203 (760809) 345.0 kV to G17-203XFMR1 (760810) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_474 | Single Phase Fault with Stuck Breaker on PRSIMN_CRK1 345.00 (585430) 345 kV Bus a. Apply Fault at the PRSIMN_CRK1 345.00 (585430) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRSIMN_CRK1 (585430) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit #1 b.2. PRSIMN_CRK1 (585430) 345.0 kV to PRSIMN_CRK2 (585440) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_475 | Single Phase Fault with Stuck Breaker on GEN-2015-095138.00 (585300) 138 kV Bus a. Apply Fault at the GEN-2015-095138.00 (585300) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-095 (585300) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. GEN-2015-095 (585300) 138.0 kV to G15-095-XF-1 (585301) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_476 | Single Phase Fault with Stuck Breaker on GEN-2016-020138.00 (587140) 138 kV Bus a. Apply Fault at the GEN-2016-020138.00 (587140) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-020 (587140) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. GEN-2016-020 (587140) 138.0 kV to G16-020XFMR1 (587141) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_477 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_478 | Single Phase Fault with Stuck Breaker on G17-004-TAP 345.00 (588494) 345 kV Bus a. Apply Fault at the G17-004-TAP 345.00 (588494) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-004-TAP (588494) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. G17-004-TAP (588494) 345.0 kV to ELMCREEK7 (539805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_479 | Single Phase Fault with Stuck Breaker on GEN-2017-125345.00 (761901) 345 kV Bus a. Apply Fault at the GEN-2017-125345.00 (761901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-125 (761901) 345.0 kV to GEN-2017-128 (761922) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-125 (761901) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_480 | Single Phase Fault with Stuck Breaker on GEN-2017-191345.00 (761943) 345 kV Bus a. Apply Fault at the GEN-2017-191345.00 (761943) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-191 (761943) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-191 (761943) 345.0 kV to G17-191XFM1 (761944) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_481 | Single Phase Fault with Stuck Breaker on GEN-2016-073345.00 (587500) 345 kV Bus a. Apply Fault at the GEN-2016-073345.00 (587500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-073 (587500) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-073 (587500) 345.0 kV to G16-073XFMR1 (587501) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_482 | Single Phase Fault with Stuck Breaker on GEN-2017-220345.00 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220345.00 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-220 (760284) 345.0 kV to G17-220-XFM1 (760285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_483 | Single Phase Fault with Stuck Breaker on G17-209-TAP 345.00 (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP 345.00 (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. G17-209-TAP (760921) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_484 | Single Phase Fault with Stuck Breaker on GEN-2017-086345.00 (589240) 345 kV Bus a. Apply Fault at the GEN-2017-086345.00 (589240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-086 (589240) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #2 b.2. GEN-2017-086 (589240) 345.0 kV to G17-086XFMR1 (589241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_485 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_486 | Single Phase Fault with Stuck Breaker on GEN-2017-226138.00 (760641) 138 kV Bus a. Apply Fault at the GEN-2017-226138.00 (760641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-226 (760641) 138.0 kV to G17-226XFMR1 (760642) 34.5 kV Two Winding #1 b.2. GEN-2017-226 (760641) 138.0 kV to G17-227XFMR1 (760662) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_487 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_488 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_489 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 4 (539674) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_490 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_491 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_492 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_493 | Single Phase Fault with Stuck Breaker on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. SMTHVL 5 (541204) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_494 | Single Phase Fault with Stuck Breaker on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply Fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCONGRS5 (541318) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 b.2. NCONGRS5 (541318) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_495 | Single Phase Fault with Stuck Breaker on STROTHR5 161.00 (541246) 161 kV Bus a. Apply Fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR5 (541246) 161.0 kV to PRALEE 5 (541206) 161.0 kV Transmission Circuit #1 b.2. STROTHR5 (541246) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_496 | Single Phase Fault with Stuck Breaker on HOOKRD 5 161.00 (541249) 161 kV Bus a. Apply Fault at the HOOKRD 5 161.00 (541249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOKRD 5 (541249) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. HOOKRD 5 (541249) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_497 | Single Phase Fault with Stuck Breaker on TIFFANY5 161.00 (543026) 161 kV Bus a. Apply Fault at the TIFFANY5 161.00 (543026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIFFANY5 (543026) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. TIFFANY5 (543026) 161.0 kV to WETHRBY5 (543017) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_498 | Single Phase Fault with Stuck Breaker on RGAFBTP2 69.000 (541322) 69 kV Bus a. Apply Fault at the RGAFBTP2 69.000 (541322) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RGAFBTP2 (541322) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. RGAFBTP2 (541322) 69.0 kV to BELTON 2 (541289) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_499 | Single Phase Fault with Stuck Breaker on GEN-2017-115345.00 (760746) 345 kV Bus a. Apply Fault at the GEN-2017-115345.00 (760746) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-115 (760746) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-115 (760746) 345.0 kV to G17-115XFMR1 (760747) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_500 | Single Phase Fault with Stuck Breaker on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply Fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MERRIAM5 (543032) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. MERRIAM5 (543032) 161.0 kV to OVERLPK5 (543047) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_501 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_502 | Single Phase Fault with Stuck Breaker on GEN-2016-157345.00 (588300) 345 kV Bus a. Apply Fault at the GEN-2016-157345.00 (588300) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-157 (588300) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-157 (588300) 345.0 kV to GEN-2016-158 (588310) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_503 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_504 | Single Phase Fault with Stuck Breaker on BNSF 5 161.00 (543132) 161 kV Bus a. Apply Fault at the BNSF 5 161.00 (543132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BNSF 5 (543132) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. BNSF 5 (543132) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_505 | Single Phase Fault with Stuck Breaker on HICKMAN5 161.00 (542994) 161 kV Bus a. Apply Fault at the HICKMAN5 161.00 (542994) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HICKMAN5 (542994) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. HICKMAN5 (542994) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_506 | Single Phase Fault with Stuck Breaker on ANTIOCH5 161.00 (543050) 161 kV Bus a. Apply Fault at the ANTIOCH5 161.00 (543050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. ANTIOCH5 (543050) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_507 | Single Phase Fault with Stuck Breaker on REDEL 5 161.00 (543053) 161 kV Bus a. Apply Fault at the REDEL 5 161.00 (543053) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDEL 5 (543053) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. REDEL 5 (543053) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_508 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_509 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_510 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_511 | Single Phase Fault with Stuck Breaker on TERRACE5 161.00 (542991) 161 kV Bus a. Apply Fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_512 | Single Phase Fault with Stuck Breaker on TOMHAWK5 161.00 (543035) 161 kV Bus a. Apply Fault at the TOMHAWK5 161.00 (543035) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOMHAWK5 (543035) 161.0 kV to BENDIX 5 (542992) 161.0 kV Transmission Circuit #1 b.2. TOMHAWK5 (543035) 161.0 kV to INDIAN_CK_5 (543127) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_513 | Single Phase Fault with Stuck Breaker on FOREST 5 161.00 (543001) 161 kV Bus a. Apply Fault at the FOREST 5 161.00 (543001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOREST 5 (543001) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. FOREST 5 (543001) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_514 | Single Phase Fault with Stuck Breaker on BUNKRDG5 161.00 (543008) 161 kV Bus a. Apply Fault at the BUNKRDG5 161.00 (543008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUNKRDG5 (543008) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 b.2. BUNKRDG5 (543008) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_515 | Single Phase Fault with Stuck Breaker on WINJT S5 161.00 (543010) 161 kV Bus a. Apply Fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT S5 (543010) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT S5 (543010) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_516 | Single Phase Fault with Stuck Breaker on WINJT N5 161.00 (543009) 161 kV Bus a. Apply Fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT N5 (543009) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT N5 (543009) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_517 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 b.2. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_518 | Single Phase Fault with Stuck Breaker on SHOLCRK5 161.00 (543029) 161 kV Bus a. Apply Fault at the SHOLCRK5 161.00 (543029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHOLCRK5 (543029) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. SHOLCRK5 (543029) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_519 | Single Phase Fault with Stuck Breaker on LINECRK5 161.00 (543025) 161 kV Bus a. Apply Fault at the LINECRK5 161.00 (543025) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINECRK5 (543025) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 b.2. LINECRK5 (543025) 161.0 kV to RIVRSID5 (543021) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_520 | Single Phase Fault with Stuck Breaker on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_521 | Single Phase Fault with Stuck Breaker on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply Fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_522 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STL439 5 (547498) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. STL439 5 (547498) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_523 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_524 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_525 | Single Phase Fault with Stuck Breaker on SUB R 69.000 (548830) 69 kV Bus a. Apply Fault at the SUB R 69.000 (548830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB R (548830) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SUB R (548830) 69.0 kV to SUB K (548801) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_526 | Single Phase Fault with Stuck Breaker on KCPL JCT 69.000 (548832) 69 kV Bus a. Apply Fault at the KCPL JCT 69.000 (548832) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KCPL JCT (548832) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.2. KCPL JCT (548832) 69.0 kV to SUB E (548804) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_527 | Single Phase Fault with Stuck Breaker on STRLNGRD 69.000 (548826) 69 kV Bus a. Apply Fault at the STRLNGRD 69.000 (548826) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRLNGRD (548826) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 b.2. STRLNGRD (548826) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_528 | Single Phase Fault with Stuck Breaker on GEN-2015-052345.00 (584900) 345 kV Bus a. Apply Fault at the GEN-2015-052345.00 (584900) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-052 (584900) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-052 (584900) 345.0 kV to G15-052XFMR1 (584901) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_529 | Single Phase Fault with Stuck Breaker on GEN-2016-003345.00 (587020) 345 kV Bus a. Apply Fault at the GEN-2016-003345.00 (587020) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-003 (587020) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-003 (587020) 345.0 kV to G16-003XFMR1 (587021) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_530 | Single Phase Fault with Stuck Breaker on GEN-2017-011345.00 (588560) 345 kV Bus a. Apply Fault at the GEN-2017-011345.00 (588560) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-011 (588560) 345.0 kV to G17-011XFMR1 (588561) 34.5 kV Two Winding #1 b.2. GEN-2017-011 (588560) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_531 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to G14-001XFMR2 (583854) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_532 | Single Phase Fault with Stuck Breaker on G17-022-TAP 138.00 (588664) 138 kV Bus a. Apply Fault at the G17-022-TAP 138.00 (588664) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-022-TAP (588664) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 b.2. G17-022-TAP (588664) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_533 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWT11_2 (543663) 69.0 kV to HAWTHS_XF5 (543130) 161.0 kV Two Winding #11 b.2. HAWT11_2 (543663) 69.0 kV to HAWTH 2 (543080) 69.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_534 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWT12_2 (543664) 69.0 kV to HAWTHS_XF5 (543130) 161.0 kV Two Winding #12 b.2. HAWT12_2 (543664) 69.0 kV to HAWTH 2 (543080) 69.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_535 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_536 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to T.NO.2-4 (509895) 138.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_537 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_538 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 2 (512626) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_539 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 2 (512727) 69.0 kV to MAIDTP2 (512625) 69.0 kV Transmission Circuit #1 b.2. GRDA1 2 (512727) 69.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_540 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE5 (512751) 161.0 kV to TONECE7 (512750) 345.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.2. TONECE5 (512751) 161.0 kV to SILMCTY5 (512643) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_541 | Single Phase Fault with Stuck Breaker on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IGLOOV1 5 (513593) 161.0 kV to HERRON 5 (513591) 161.0 kV Transmission Circuit #1 b.2. IGLOOV1 5 (513593) 161.0 kV to IGLOOV 7 (513596) 345.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_542 | Single Phase Fault with Stuck Breaker on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IGLOOV2 5 (513595) 161.0 kV to HERRON 5 (513591) 161.0 kV Transmission Circuit #1 b.2. IGLOOV2 5 (513595) 161.0 kV to IGLOOV 7 (513596) 345.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_543 | Single Phase Fault with Stuck Breaker on KNOBHIL2 69.000 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 69.000 (514794) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL2 (514794) 69.0 kV to ALVAOGE2 (514792) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_544 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_545 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND2 (520995) 69.0 kV to CRTSJCT2 (521197) 69.0 kV Transmission Circuit #1 b.2. MOORLND2 (520995) 69.0 kV to MOORLND4 (520999) 138.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_546 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_547 | Single Phase Fault with Stuck Breaker on G06-44 115.00 (560577) 115 kV Bus a. Apply Fault at the G06-44 115.00 (560577) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G06-44 (560577) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 b.2. G06-44 (560577) 115.0 kV to G06-44-3 (560582) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_548 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_549 | Single Phase Fault with Stuck Breaker on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_550 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_551 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_552 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to LANG 7 (532769) 345.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 b.2. LANG 3 (533304) 115.0 kV to EAST ST3 (533301) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_553 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to MORRIS 7 (532770) 345.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 b.2. MORRIS 6 (532863) 230.0 kV to UNIONRG6 (532874) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_554 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to TECHILL6 (532857) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_555 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 3 (533283) 115.0 kV to 87TH 7 (532775) 345.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 b.2. 87TH 3 (533283) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_556 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_557 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_558 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 b.2. CIRCLE 3 (533413) 115.0 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_559 | Single Phase Fault with Stuck Breaker on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply Fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 5 (532937) 161.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_560 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLERS2 (533609) 69.0 kV to FRNTR N2 (533593) 69.0 kV Transmission Circuit #1 b.2. BUTLERS2 (533609) 69.0 kV to BUTLERS4 (532989) 138.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_561 | Single Phase Fault with Stuck Breaker on MIDIANW2 69.000 (533597) 69 kV Bus a. Apply Fault at the MIDIANW2 69.000 (533597) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDIANW2 (533597) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #z1 b.2. MIDIANW2 (533597) 69.0 kV to THUNBRD2 (533603) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_562 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTED2 (533736) 69.0 kV to MUDCRKJ2 (533744) 69.0 kV Transmission Circuit #1 b.2. HALSTED2 (533736) 69.0 kV to HALSTD 4 (533011) 138.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_563 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.2. NEOSHOS2 (533778) 69.0 kV to BAKER 2 (532926) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_564 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_565 | Single Phase Fault with Stuck Breaker on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply Fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM2 (533786) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 b.2. CHISHLM2 (533786) 69.0 kV to GRANT 2 (533799) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_566 | Single Phase Fault with Stuck Breaker on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply Fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_567 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 b.2. GILL W 2 (533796) 69.0 kV to GILL E 4 (533044) 138.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_568 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_569 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 b.2. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_570 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOEASTE2 (533823) 69.0 kV to NOEASTE4 (533060) 138.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 b.2. NOEASTE2 (533823) 69.0 kV to NOEASTW2 (533822) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_571 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOEASTW2 (533822) 69.0 kV to NOEASTW4 (533061) 138.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 b.2. NOEASTW2 (533822) 69.0 kV to INNOVAT2 (533811) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_572 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #z1 b.2. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_573 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_574 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_575 | Single Phase Fault with Stuck Breaker on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply Fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_576 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_577 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 5 (541202) 161.0 kV to SIBLEY 7 (541201) 345.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_578 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_579 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_580 | Single Phase Fault with Stuck Breaker on LAC3_STAR7 345.00 (543667) 345 kV Bus a. Apply Fault at the LAC3_STAR7 345.00 (543667) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC3_STAR7 (543667) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h b.2. LAC3_STAR7 (543667) 345.0 kV to LAC3_X1 (543661) 6.9 kV Two Winding #x | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_581 | Single Phase Fault with Stuck Breaker on LAC8_STAR7 345.00 (543669) 345 kV Bus a. Apply Fault at the LAC8_STAR7 345.00 (543669) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC8_STAR7 (543669) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h b.2. LAC8_STAR7 (543669) 345.0 kV to LAC8_Z1 (543672) 4.0 kV Two Winding #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_582 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_583 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 2 (547534) 69.0 kV to ORO110 5 (547467) 161.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 b.2. ORO110 2 (547534) 69.0 kV to WEB436 2 (547527) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_584 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 4 (547486) 138.0 kV to VINTAJC4 (510417) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_585 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 2 (547601) 69.0 kV to HOC404 5 (547487) 161.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 2 (547601) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_586 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_587 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to 7FAIRPT (300039) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_588 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Transfer | GROUP3_FAULT_655 | 3 Phase fault on S3458 3345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3345.00 (645458) 345 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Leave Fault on for 5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Oscillatory Response observed in the response of number of units. Steady state voltage at numerous busbars did not recover to 0.9 p.u. | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles)
03 - Central | 25S | Transfer | GROUP3_FAULT_656 | 3 Phase fault onHOLT 7345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7345.00 (645458) 345 kV Bus b. Clear fault after 5 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Leave Fault on for 5 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | No | Yes | No | Yes | Oscillatory Response observed in the response of number of units. Steady state voltage at numerous busbars did not recover to 0.9 p.u. | Build a new 345 kV line from Holt to Atchison (KCPL/MEC) (22.24 miles)
01 - North | 25W | Transfer | GROUP1_FAULT_1 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_2 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_3 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_4 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_5 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_6 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_7 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_8 | 3 Phase fault on ELLENDL4 230.00 (661026) 230 kV Bus a. Apply fault at the ELLENDL4 230.00 (661026) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_9 | 3 Phase fault on MERRCRT4 230.00 (661093) 230 kV Bus a. Apply fault at the MERRCRT4 230.00 (661093) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRCRT4 (661093) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_10 | 3 Phase fault on STANLEY7 115.00 (661080) 115 kV Bus a. Apply fault at the STANLEY7 115.00 (661080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. STANLEY7 (661080) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_11 | 3 Phase fault on KENMARE7 115.00 (661052) 115 kV Bus a. Apply fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV to LIGNITE7 (661281) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_12 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_13 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_14 | 3 Phase fault on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_15 | 3 Phase fault on KENMARE7 115.00 (661052) 115 kV Bus a. Apply fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KENMARE7 (661052) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_16 | 3 Phase fault on TIOGA4 7 115.00 (661085) 115 kV Bus a. Apply fault at the TIOGA4 7 115.00 (661085) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 7 (661085) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_17 | 3 Phase fault on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA7 7 (661086) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_18 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_19 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to MAPLE R4 (657754) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_20 | 3 Phase fault on MALLARD7 115.00 (603023) 115 kV Bus a. Apply fault at the MALLARD7 115.00 (603023) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MALLARD7 (603023) 115.0 kV to LOGAN___-BE7 (659155) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_21 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB14 (615604) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_22 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_23 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_24 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_25 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_26 | 3 Phase fault on GRE-STANTON4230.00 (615901) 230 kV Bus a. Apply fault at the GRE-STANTON4230.00 (615901) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_27 | 3 Phase fault on JAMESTN3 345.00 (620369) 345 kV Bus a. Apply fault at the JAMESTN3 345.00 (620369) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JAMESTN3 (620369) 345.0 kV to CENTER 3 (657791) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_28 | 3 Phase fault on CENTER 4 230.00 (657751) 230 kV Bus a. Apply fault at the CENTER 4 230.00 (657751) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTER 4 (657751) 230.0 kV to SQBUTTE4 (657756) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_29 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to COYOTE 3 (661016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_30 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_31 | 3 Phase fault on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHEYNNE4 (602006) 230.0 kV to SHEYNNE7 (603018) 115.0 kV to SHEYENNE6 9 (605730) 13.8 kV Three Winding #6 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_32 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_33 | 3 Phase fault on CENTER 3 345.00 (657791) 345 kV Bus a. Apply fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CENTER 3 (657791) 345.0 kV to SQBUTTE4 (657756) 230.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_34 | 3 Phase fault on GRE-COALFB14230.00 (615604) 230 kV Bus a. Apply fault at the GRE-COALFB14230.00 (615604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB14 (615604) 230.0 kV Fixed Shunt Device #bp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_35 | 3 Phase fault on GRE-COALFB14230.00 (615604) 230 kV Bus a. Apply fault at the GRE-COALFB14230.00 (615604) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB14 (615604) 230.0 kV Fixed Shunt Device #hp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_36 | 3 Phase fault on GRE-COALFB24230.00 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24230.00 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Fixed Shunt Device #bp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_37 | 3 Phase fault on GRE-COALFB24230.00 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24230.00 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Fixed Shunt Device #hp c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_38 | 3 Phase fault on GRE-COALFB24230.00 (615605) 230 kV Bus a. Apply fault at the GRE-COALFB24230.00 (615605) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB24 (615605) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_39 | 3 Phase fault on GRE-COALFB34230.00 (615606) 230 kV Bus a. Apply fault at the GRE-COALFB34230.00 (615606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COALFB34 (615606) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_40 | 3 Phase fault on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 b.3. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_41 | 3 Phase fault on GRE-MCHENRY4230.00 (615347) 230 kV Bus a. Apply fault at the GRE-MCHENRY4230.00 (615347) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1754 POI (47544) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. MAGIC CITY 4 (602052) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.3. GRE-MCHENRY4 (615347) 230.0 kV to GRE-BALTA 4 (615903) 230.0 kV Transmission Circuit #1 b.4. GRE-MCHENRY4 (615347) 230.0 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRYT (615349) 12.5 kV Three Winding #1 b.5. GRE-MCHENRYT (615349) 12.5 kV to GRE-MCHENRY7 (615348) 115.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_42 | 3 Phase fault on CNTSHNT3 345.00 (657951) 345 kV Bus a. Apply fault at the CNTSHNT3 345.00 (657951) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MPC03839POI (67020) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_43 | 3 Phase fault on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. J1456 POI (44568) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 b.3. UNDERWD4 (620381) 230.0 kV to UNDERWOD-CP9 (655608) 41.6 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_44 | 3 Phase fault on JAMETAP7 115.00 (620273) 115 kV Bus a. Apply fault at the JAMETAP7 115.00 (620273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMSTWN7 (620269) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 b.2. JAMESPK7 (620272) 115.0 kV to JAMETAP7 (620273) 115.0 kV Transmission Circuit #1 b.3. JAMETAP7 (620273) 115.0 kV to JAMSDTN7 (620274) 115.0 kV Transmission Circuit #1 b.4. JAMETAP7 (620273) 115.0 kV to NJAMES 7 (620275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_45 | 3 Phase fault on AVIKO 7 115.00 (620271) 115 kV Bus a. Apply fault at the AVIKO 7 115.00 (620271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPIRITWD 7 (620270) 115.0 kV to AVIKO 7 (620271) 115.0 kV Transmission Circuit #1 b.2. AVIKO 7 (620271) 115.0 kV to JAMESPK7 (620272) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_46 | 3 Phase fault on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.3. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_47 | 3 Phase fault on FORMAN 4 230.00 (620363) 230 kV Bus a. Apply fault at the FORMAN 4 230.00 (620363) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGE SS9 (620159) 41.6 kV to OAKES 9 (620162) 41.6 kV Transmission Circuit #1 b.2. HANKSON4 (620327) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.3. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #1 b.4. OAKES 4 (620362) 230.0 kV to OAKES 9 (620162) 41.6 kV Two Winding #2 b.5. OAKES 4 (620362) 230.0 kV to FORMAN 4 (620363) 230.0 kV Transmission Circuit #1 b.6. OAKES 4 (620362) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #1 b.7. FORMN 9 (620163) 41.6 kV to FORMAN 4 (620363) 230.0 kV to FORMN 7 (620263) 115.0 kV Three Winding #1 b.8. FORMN 7 (620263) 115.0 kV to FORMAN 4 (620363) 230.0 kV to FORMN 9 (620163) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_48 | 3 Phase fault on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_49 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_50 | 3 Phase fault on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_51 | 3 Phase fault on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_52 | 3 Phase fault on BARLOW -CP7115.00 (655610) 115 kV Bus a. Apply fault at the BARLOW -CP7115.00 (655610) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_53 | 3 Phase fault on PICKERT4 230.00 (657759) 230 kV Bus a. Apply fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. PICKERT9 (620167) 41.6 kV to PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV Three Winding #1 b.5. PICKERT8 (657923) 69.0 kV to PICKERT4 (657759) 230.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_54 | 3 Phase fault on ENDERLIN 7 115.00 (652638) 115 kV Bus a. Apply fault at the ENDERLIN 7 115.00 (652638) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_55 | 3 Phase fault on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_56 | 3 Phase fault on DICKEYTP-CP869.000 (655625) 69 kV Bus a. Apply fault at the DICKEYTP-CP869.000 (655625) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.3. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_57 | 3 Phase fault on OMEGATAP-CP869.000 (655626) 69 kV Bus a. Apply fault at the OMEGATAP-CP869.000 (655626) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.2. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 b.3. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_58 | 3 Phase fault on LAMOURTP-CP869.000 (655627) 69 kV Bus a. Apply fault at the LAMOURTP-CP869.000 (655627) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 b.2. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 b.3. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_59 | 3 Phase fault on WESTOAKS-CP869.000 (655628) 69 kV Bus a. Apply fault at the WESTOAKS-CP869.000 (655628) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 b.2. WESTOAKS-CP8 (655628) 69.0 kV to NRTHOAKS-CP8 (655629) 69.0 kV Transmission Circuit #1 b.3. NRTHOAKS-CP8 (655629) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_60 | 3 Phase fault on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 b.3. KENASTON-BE7 (659308) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_61 | 3 Phase fault on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_62 | 3 Phase fault on FARMVL_T-MW7115.00 (655943) 115 kV Bus a. Apply fault at the FARMVL_T-MW7115.00 (655943) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.2. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 b.3. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_63 | 3 Phase fault on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_64 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_65 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_66 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_67 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_68 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_69 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_70 | 3 Phase fault on EDGELEY8 69.000 (652433) 69 kV Bus a. Apply fault at the EDGELEY8 69.000 (652433) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. FORMAN 8 (652439) 69.0 kV to COGSWELL-CP8 (655630) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_71 | 3 Phase fault on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.3. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.4. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_72 | 3 Phase fault on ABERDN JCT 7115.00 (660000) 115 kV Bus a. Apply fault at the ABERDN JCT 7115.00 (660000) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RICHMOND-ER7 (655522) 115.0 kV to ABERDN JCT 7 (660000) 115.0 kV Transmission Circuit #1 b.2. ABERDN JCT 7 (660000) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.3. ABERDN JCT 7 (660000) 115.0 kV to ABERDNCITY7 (660022) 115.0 kV Transmission Circuit #1 b.4. ABERDN JCT 7 (660000) 115.0 kV to ELLENDL7 (661027) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_73 | 3 Phase fault on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to REDFIELD 7 (660002) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_74 | 3 Phase fault on HURON WPARK7115.00 (660003) 115 kV Bus a. Apply fault at the HURON WPARK7115.00 (660003) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON WPARK7 (660003) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_75 | 3 Phase fault on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_76 | 3 Phase fault on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_77 | 3 Phase fault on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_78 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_79 | 3 Phase fault on BLAISDEL-BE7115.00 (659144) 115 kV Bus a. Apply fault at the BLAISDEL-BE7115.00 (659144) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_80 | 3 Phase fault on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_81 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_82 | 3 Phase fault on LOGAN___-BE7115.00 (659155) 115 kV Bus a. Apply fault at the LOGAN___-BE7115.00 (659155) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE7 (659155) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_83 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_84 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_85 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_86 | 3 Phase fault on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC7 (652454) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_87 | 3 Phase fault on JAMESTN7 115.00 (652445) 115 kV Bus a. Apply fault at the JAMESTN7 115.00 (652445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN7 (652445) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_88 | 3 Phase fault on STATELIN-MW7115.00 (655924) 115 kV Bus a. Apply fault at the STATELIN-MW7115.00 (655924) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STATELIN-MW7 (655924) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_89 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_90 | 3 Phase fault on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_91 | 3 Phase fault on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.4. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_92 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_93 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_94 | 3 Phase fault on NORMANLK-BD7115.00 (655780) 115 kV Bus a. Apply fault at the NORMANLK-BD7115.00 (655780) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORMANLK-BD7 (655780) 115.0 kV to LINDAHLS-MW7 (655910) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_95 | 3 Phase fault on MOE -MW7115.00 (655900) 115 kV Bus a. Apply fault at the MOE -MW7115.00 (655900) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.2. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.3. MOE -MW7 (655900) 115.0 kV to E.NESSON-MW7 (655965) 115.0 kV Transmission Circuit #1 b.4. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 b.5. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.6. ROSS -MW7 (655903) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.7. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_96 | 3 Phase fault on PALERMO -MW7115.00 (655916) 115 kV Bus a. Apply fault at the PALERMO -MW7115.00 (655916) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to PALGASPL-MW7 (655918) 115.0 kV Transmission Circuit #1 b.3. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_97 | 3 Phase fault on FINSTAD345 345.00 (659060) 345 kV Bus a. Apply fault at the FINSTAD345 345.00 (659060) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to RBNSNLAK-MW7 (655905) 115.0 kV Transmission Circuit #1 b.2. RBNSNLAK-MW7 (655905) 115.0 kV to FINSTAD -MW7 (655906) 115.0 kV Transmission Circuit #1 b.3. FINSTAD -MW7 (655906) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.4. FINSTAD -MW7 (655906) 115.0 kV to VANHOOK -MW7 (655920) 115.0 kV Transmission Circuit #1 b.5. E.NEWTWN-MW7 (655907) 115.0 kV to OSBORN -MW7 (655919) 115.0 kV Transmission Circuit #1 b.6. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #1 b.7. FINSTAD345 (659060) 345.0 kV to FINSTAD -MW7 (655906) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_98 | 3 Phase fault on ROSEGLEN-CP7115.00 (655662) 115 kV Bus a. Apply fault at the ROSEGLEN-CP7115.00 (655662) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLS.C-CP7 (655661) 115.0 kV to ROSEGLEN-CP7 (655662) 115.0 kV Transmission Circuit #1 b.2. ROSEGLEN-CP7 (655662) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.3. RAUB TAP-CP7 (655663) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 b.4. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_99 | 3 Phase fault on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN-LNX3 (652829) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_100 | 3 Phase fault on WILISTN7 115.00 (652421) 115 kV Bus a. Apply fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN7 (652421) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_101 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_102 | 3 Phase fault on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_103 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to GARRISN7 (652442) 115.0 kV to GARRISON 9 (652642) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_104 | 3 Phase fault on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_105 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_106 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_107 | 3 Phase fault on GARRISN4 230.00 (652441) 230 kV Bus a. Apply fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_108 | 3 Phase fault on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_109 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_110 | 3 Phase fault on SATTER -MW7115.00 (655967) 115 kV Bus a. Apply fault at the SATTER -MW7115.00 (655967) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SATTER -MW7 (655967) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_111 | 3 Phase fault on JAMESPK9 41.600 (620172) 41.59999847 kV Bus a. Apply fault at the JAMESPK9 41.600 (620172) 41.59999847 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESPK9 (620172) 41.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_112 | 3 Phase fault on JAMESPK9 41.600 (620172) 41.59999847 kV Bus a. Apply fault at the JAMESPK9 41.600 (620172) 41.59999847 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESPK9 (620172) 41.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_113 | 3 Phase fault on ANTELP_1-BEG23.000 (659103) 23 kV Bus a. Apply fault at the ANTELP_1-BEG23.000 (659103) 23 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELP_1-BEG (659103) 23.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_114 | 3 Phase fault on ANTELP_2-BEG23.000 (659107) 23 kV Bus a. Apply fault at the ANTELP_2-BEG23.000 (659107) 23 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELP_2-BEG (659107) 23.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_115 | 3 Phase fault on LELAND_1-BEG22.000 (659110) 22 kV Bus a. Apply fault at the LELAND_1-BEG22.000 (659110) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_1-BEG (659110) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_116 | 3 Phase fault on LELAND_2-BEG20.000 (659111) 20 kV Bus a. Apply fault at the LELAND_2-BEG20.000 (659111) 20 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_2-BEG (659111) 20.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_117 | 3 Phase fault on GROTON_2-BEG13.800 (659272) 13.80000019 kV Bus a. Apply fault at the GROTON_2-BEG13.800 (659272) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON_2-BEG (659272) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_118 | 3 Phase fault on GROTON_1-BEG13.800 (659274) 13.80000019 kV Bus a. Apply fault at the GROTON_1-BEG13.800 (659274) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON_1-BEG (659274) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_119 | 3 Phase fault on POMONA__-PPW0.6900 (659290) 0.689999998 kV Bus a. Apply fault at the POMONA__-PPW0.6900 (659290) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POMONA__-PPW (659290) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_120 | 3 Phase fault on BEPCPXCTG1X218.000 (659581) 18 kV Bus a. Apply fault at the BEPCPXCTG1X218.000 (659581) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEPCPXCTG1X2 (659581) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_121 | 3 Phase fault on BEPCPXCTG2X218.000 (659582) 18 kV Bus a. Apply fault at the BEPCPXCTG2X218.000 (659582) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEPCPXCTG2X2 (659582) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_122 | 3 Phase fault on AS17-013GEN10.6900 (762353) 0.689999998 kV Bus a. Apply fault at the AS17-013GEN10.6900 (762353) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AS17-013GEN1 (762353) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_123 | 3 Phase fault on G18-010-GEN10.6300 (762485) 0.629999995 kV Bus a. Apply fault at the G18-010-GEN10.6300 (762485) 0.629999995 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-010-GEN1 (762485) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_124 | 3 Phase fault on G18-008-GEN10.6900 (762540) 0.689999998 kV Bus a. Apply fault at the G18-008-GEN10.6900 (762540) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-008-GEN1 (762540) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_125 | 3 Phase fault on G18-039GEN1 0.6600 (762738) 0.660000026 kV Bus a. Apply fault at the G18-039GEN1 0.6600 (762738) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-039GEN1 (762738) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_126 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_127 | 3 Phase fault on SQBP1DC4 230.00 (608597) 230 kV Bus a. Apply fault at the SQBP1DC4 230.00 (608597) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBP1DC4 (608597) 230.0 kV to SQBEAST4 (608602) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_128 | 3 Phase fault on SQBP2DC4 230.00 (608599) 230 kV Bus a. Apply fault at the SQBP2DC4 230.00 (608599) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBP2DC4 (608599) 230.0 kV to SQBEAST4 (608602) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_129 | 3 Phase fault on VALLEYC8 69.000 (652204) 69 kV Bus a. Apply fault at the VALLEYC8 69.000 (652204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC8 (652204) 69.0 kV to MPC-VCY8 (657804) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_130 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_131 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFRDSOUTH4 (661003) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_132 | 3 Phase fault on GROTON18 69.000 (652250) 69 kV Bus a. Apply fault at the GROTON18 69.000 (652250) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to NWPS509-ER8 (655395) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_133 | 3 Phase fault on HURON 8 69.000 (652284) 69 kV Bus a. Apply fault at the HURON 8 69.000 (652284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to SW-HURN2-ER8 (655066) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_134 | 3 Phase fault on HURON 8 69.000 (652284) 69 kV Bus a. Apply fault at the HURON 8 69.000 (652284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 8 (652284) 69.0 kV to SW-HURN3-ER8 (655067) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_135 | 3 Phase fault on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_136 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to JUDSON__-BE4 (659334) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_137 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_138 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_139 | 3 Phase fault on CARNGTN7 115.00 (652428) 115 kV Bus a. Apply fault at the CARNGTN7 115.00 (652428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_140 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_141 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_142 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_143 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_144 | 3 Phase fault on JAMESTN7 115.00 (652445) 115 kV Bus a. Apply fault at the JAMESTN7 115.00 (652445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_145 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_146 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_147 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_148 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_149 | 3 Phase fault on HURON 7 115.00 (652515) 115 kV Bus a. Apply fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_150 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_151 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_152 | 3 Phase fault on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_153 | 3 Phase fault on MOS-MILR-ER869.000 (655053) 69 kV Bus a. Apply fault at the MOS-MILR-ER869.000 (655053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-MILR-ER8 (655053) 69.0 kV to SW-HURN4-ER8 (655064) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_154 | 3 Phase fault on MOS-HRON-ER869.000 (655058) 69 kV Bus a. Apply fault at the MOS-HRON-ER869.000 (655058) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-HRON-ER8 (655058) 69.0 kV to HURON-ER8 (655231) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_155 | 3 Phase fault on SW-HURN4-ER869.000 (655064) 69 kV Bus a. Apply fault at the SW-HURN4-ER869.000 (655064) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-HURN4-ER8 (655064) 69.0 kV to SW-HURN2-ER8 (655066) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_156 | 3 Phase fault on MOS-YLTI-ER869.000 (655065) 69 kV Bus a. Apply fault at the MOS-YLTI-ER869.000 (655065) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-YLTI-ER8 (655065) 69.0 kV to MORNINGS-ER8 (655236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_157 | 3 Phase fault on SW-HURN3-ER869.000 (655067) 69 kV Bus a. Apply fault at the SW-HURN3-ER869.000 (655067) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-HURN3-ER8 (655067) 69.0 kV to MORNINGS-ER8 (655236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_158 | 3 Phase fault on MOS-WOLS-ER869.000 (655069) 69 kV Bus a. Apply fault at the MOS-WOLS-ER869.000 (655069) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-WOLS-ER8 (655069) 69.0 kV to VIRGIL-ER8 (655241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_159 | 3 Phase fault on MOS-VRCV-ER869.000 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER869.000 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to MOS-DAK-ER8 (655071) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_160 | 3 Phase fault on MOS-VRCV-ER869.000 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER869.000 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to VIRGIL-ER8 (655241) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_161 | 3 Phase fault on MOS-VRCV-ER869.000 (655070) 69 kV Bus a. Apply fault at the MOS-VRCV-ER869.000 (655070) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-VRCV-ER8 (655070) 69.0 kV to CAVOUR-ER8 (655242) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_162 | 3 Phase fault on MOS-DAK-ER8 69.000 (655071) 69 kV Bus a. Apply fault at the MOS-DAK-ER8 69.000 (655071) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-DAK-ER8 (655071) 69.0 kV to DAKOTA-ER8 (655244) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_163 | 3 Phase fault on MOS-CLRM-ER869.000 (655082) 69 kV Bus a. Apply fault at the MOS-CLRM-ER869.000 (655082) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-CLRM-ER8 (655082) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_164 | 3 Phase fault on MOS-SWAB-ER869.000 (655085) 69 kV Bus a. Apply fault at the MOS-SWAB-ER869.000 (655085) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-SWAB-ER8 (655085) 69.0 kV to BATH-ER8 (655269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_165 | 3 Phase fault on MOS-IPAB-ER869.000 (655086) 69 kV Bus a. Apply fault at the MOS-IPAB-ER869.000 (655086) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-IPAB-ER8 (655086) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_166 | 3 Phase fault on MOS-ABDN-ER869.000 (655087) 69 kV Bus a. Apply fault at the MOS-ABDN-ER869.000 (655087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOS-ABDN-ER8 (655087) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_167 | 3 Phase fault on SW-IPABD-ER869.000 (655089) 69 kV Bus a. Apply fault at the SW-IPABD-ER869.000 (655089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-IPABD-ER8 (655089) 69.0 kV to IPABRDEN-ER8 (655264) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_168 | 3 Phase fault on SW-IPABD-ER869.000 (655089) 69 kV Bus a. Apply fault at the SW-IPABD-ER869.000 (655089) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SW-IPABD-ER8 (655089) 69.0 kV to BATH-ER8 (655269) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_169 | 3 Phase fault on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_170 | 3 Phase fault on BATH-ER8 69.000 (655269) 69 kV Bus a. Apply fault at the BATH-ER8 69.000 (655269) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATH-ER8 (655269) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_171 | 3 Phase fault on BERTHOLD-CP7115.00 (655641) 115 kV Bus a. Apply fault at the BERTHOLD-CP7115.00 (655641) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_172 | 3 Phase fault on PLSNTV_T-MW7115.00 (655902) 115 kV Bus a. Apply fault at the PLSNTV_T-MW7115.00 (655902) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to PLSNTVAL-MW7 (655913) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_173 | 3 Phase fault on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN -MW7 (655904) 115.0 kV to AUSTIN -MW7 (655912) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_174 | 3 Phase fault on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_175 | 3 Phase fault on W.BANK__-MW7115.00 (655922) 115 kV Bus a. Apply fault at the W.BANK__-MW7115.00 (655922) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_176 | 3 Phase fault on TWELVE_M-MW7115.00 (655939) 115 kV Bus a. Apply fault at the TWELVE_M-MW7115.00 (655939) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_177 | 3 Phase fault on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV to BLAISDEL-MW7 (655949) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_178 | 3 Phase fault on BLAISDEL-MW7115.00 (655949) 115 kV Bus a. Apply fault at the BLAISDEL-MW7115.00 (655949) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_179 | 3 Phase fault on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_180 | 3 Phase fault on W.BANK_T-MW7115.00 (655953) 115 kV Bus a. Apply fault at the W.BANK_T-MW7115.00 (655953) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. W.BANK_T-MW7 (655953) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_181 | 3 Phase fault on HESSRAIL-MW7115.00 (655961) 115 kV Bus a. Apply fault at the HESSRAIL-MW7115.00 (655961) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HESSRAIL-MW7 (655961) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_182 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_183 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_184 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_185 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_186 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_187 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_188 | 3 Phase fault on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_189 | 3 Phase fault on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_190 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_191 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_192 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_193 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_194 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_195 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_196 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_197 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_198 | 3 Phase fault on COTEAU_1-RR869.000 (659222) 69 kV Bus a. Apply fault at the COTEAU_1-RR869.000 (659222) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to DGC UREA-BE8 (659236) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_199 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_200 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_201 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_202 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_203 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU17A-BE7 (659466) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_204 | 3 Phase fault on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to PG.KU19A-BE7 (659467) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_205 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_206 | 3 Phase fault on BD 4230.00 (672601) 230 kV Bus a. Apply fault at the BD 4230.00 (672601) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BD 4 (672601) 230.0 kV to SHAND 4 (672621) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_207 | 3 Phase fault on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM1T (615602) 12.5 kV Three Winding #1 b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COAL FM8 (615601) 69.0 kV to GRE-COALFM2T (615603) 12.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_208 | 3 Phase fault on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VALLEYC8 (652204) 69.0 kV to VALLEYC7 (652454) 115.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_209 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_210 | 3 Phase fault on WATFORD4 230.00 (652216) 230 kV Bus a. Apply fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_211 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_212 | 3 Phase fault on GROTON 7 115.00 (652512) 115 kV Bus a. Apply fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_213 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_214 | 3 Phase fault on WILISTN4 230.00 (652400) 230 kV Bus a. Apply fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_215 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_216 | 3 Phase fault on BISMARK4 230.00 (652426) 230 kV Bus a. Apply fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_217 | 3 Phase fault on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_218 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_219 | 3 Phase fault on FARGO 4 230.00 (652435) 230 kV Bus a. Apply fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_220 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_221 | 3 Phase fault on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_222 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_223 | 3 Phase fault on HURON 4 230.00 (652514) 230 kV Bus a. Apply fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_224 | 3 Phase fault on WATERTN3 345.00 (652529) 345 kV Bus a. Apply fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_225 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_226 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_227 | 3 Phase fault on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to BRISTOL-ER8 (655458) 69.0 kV to BRISTOL-ER9 (655459) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_228 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_229 | 3 Phase fault on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_230 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_231 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_232 | 3 Phase fault on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_233 | 3 Phase fault on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_234 | 3 Phase fault on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_235 | 3 Phase fault on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_236 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE7 (659187) 115.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_237 | 3 Phase fault on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GROTON__-BE3 (659160) 345.0 kV to GROTON__-BE8 (659198) 115.0 kV to GRT.KU2A-BE8 (659699) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_238 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV3A-BE9 (659318) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_239 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE4 (659302) 230.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_240 | 3 Phase fault on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to CHARL_CK-BE7 (659182) 115.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_241 | 3 Phase fault on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV to BAL.KY1A-BE9 (659200) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_242 | 3 Phase fault on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGC_____-BE3 (659212) 345.0 kV to DGC_____-BE4 (659233) 230.0 kV to DGC_____-BE9 (659232) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_243 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_244 | 3 Phase fault on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_245 | 3 Phase fault on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to JUDSON__-BE4 (659334) 230.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_246 | 3 Phase fault on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_247 | 3 Phase fault on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_248 | 3 Phase fault on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ROUNDUP_-MK7 (659385) 115.0 kV to RP.KU3A_-BE9 (659386) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_249 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_250 | 3 Phase fault on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_251 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU17A-BE7 (659466) 115.0 kV to PG.KU17A-BE9 (659392) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_252 | 3 Phase fault on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to PG.KU19A-BE7 (659467) 115.0 kV to PG.KU19A-BE9 (659393) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_253 | 3 Phase fault on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA4 4 (661084) 230.0 kV to TIOGA4 7 (661085) 115.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_254 | 3 Phase fault on ELLENDL345 3345.00 (661097) 345 kV Bus a. Apply fault at the ELLENDL345 3345.00 (661097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ELLENDL345 3 (661097) 345.0 kV to ELLENDL345 4 (661098) 230.0 kV to ELLENDL345 9 (661907) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_255 | 3 Phase fault on BDX 4230.00 (672602) 230 kV Bus a. Apply fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_256 | 3 Phase fault on BDV 4230.00 (672603) 230 kV Bus a. Apply fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_257 | 3 Phase fault on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SQBEAST4 (608602) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_258 | 3 Phase fault on WATERTN4 230.00 (652530) 230 kV Bus a. Apply fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WATERTN4 (652530) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_259 | 3 Phase fault on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA -MW7 (655944) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_260 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_261 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_262 | 3 Phase fault on ELLENDL345 4230.00 (661098) 230 kV Bus a. Apply fault at the ELLENDL345 4230.00 (661098) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELLENDL345 4 (661098) 230.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_1 | Single Phase Fault with Stuck Breaker on ELLENDL4 230.00 (661026) 230 kV Bus a. Apply Fault at the ELLENDL4 230.00 (661026) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL4 (661026) 230.0 kV to ELLENDL345 4 (661098) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_2 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_3 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_4 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_5 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_6 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_7 | Single Phase Fault with Stuck Breaker on FAIRVIEW 7 115.00 (652651) 115 kV Bus a. Apply Fault at the FAIRVIEW 7 115.00 (652651) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.2. FAIRVIEW 7 (652651) 115.0 kV to SPRINGLK-LY7 (655791) 115.0 kV Transmission Circuit #1 b.3. FAIRVIEW 7 (652651) 115.0 kV to NOHLEY -LY7 (655792) 115.0 kV Transmission Circuit #1 b.4. FAIRVIEW 7 (652651) 115.0 kV to RICHLAND-BE7 (659151) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_8 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_9 | Single Phase Fault with Stuck Breaker on BASIN___-BE4230.00 (659199) 230 kV Bus a. Apply Fault at the BASIN___-BE4230.00 (659199) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-STANTON4 (615901) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.4. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.5. LELAND_O-BE4 (659106) 230.0 kV to BASIN___-BE4 (659199) 230.0 kV Transmission Circuit #1 b.6. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 b.7. LELAND_O-BE4 (659106) 230.0 kV to LELAND_O-BE3 (659105) 345.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 b.8. LELAND_O-BE4 (659106) 230.0 kV to LELAND_1-BEG (659110) 22.0 kV Two Winding #1 b.9. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.10. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 b.11. BAL.KY1A-BE9 (659200) 13.8 kV to BASIN___-BE4 (659199) 230.0 kV to BASIN___-BE7 (659109) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_10 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.10. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.11. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.12. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_11 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.8. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.9. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.10. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.11. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.12. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.13. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_12 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to GEN-2018-039 (762735) 115.0 kV Transmission Circuit #1 b.5. EDGELEY9 (652322) 41.8 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.6. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_13 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 b.6. LEEDS 7 (652447) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_14 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 b.6. DEVILSE7 (620265) 115.0 kV to DEVIL J7 (620267) 115.0 kV Transmission Circuit #1 b.7. DEVIL J7 (620267) 115.0 kV to DEVIL S7 (620268) 115.0 kV Transmission Circuit #1 b.8. DEVILSE7 (620265) 115.0 kV to RAMSEY 7 (620266) 115.0 kV Transmission Circuit #1 b.9. DEVILSE7 (620265) 115.0 kV to SWEETWA7 (657720) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_15 | Single Phase Fault with Stuck Breaker on CULB_GEN-BE7115.00 (659269) 115 kV Bus a. Apply Fault at the CULB_GEN-BE7115.00 (659269) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 b.7. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.9. CULBSN.E-BE7 (659262) 115.0 kV to CULB_GEN-BE7 (659269) 115.0 kV Transmission Circuit #1 b.10. CULB_GEN-BE7 (659269) 115.0 kV to CULBRTSN-BEG (659270) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_16 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_17 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_18 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_19 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_20 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD9 (652221) 13.8 kV to BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV Three Winding #1 b.2. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_21 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_22 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_23 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_24 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.3. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_25 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.10. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.11. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_26 | Single Phase Fault with Stuck Breaker on ENDERLIN 7 115.00 (652638) 115 kV Bus a. Apply Fault at the ENDERLIN 7 115.00 (652638) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_27 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.5. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_28 | Single Phase Fault with Stuck Breaker on ENDERLIN 7 115.00 (652638) 115 kV Bus a. Apply Fault at the ENDERLIN 7 115.00 (652638) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_29 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.5. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_30 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_31 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_32 | Single Phase Fault with Stuck Breaker on ECKLUND_-PP4230.00 (659284) 230 kV Bus a. Apply Fault at the ECKLUND_-PP4230.00 (659284) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_33 | Single Phase Fault with Stuck Breaker on ECKLUND_-PP4230.00 (659284) 230 kV Bus a. Apply Fault at the ECKLUND_-PP4230.00 (659284) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.3. HILKEN 4 (652466) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #1 b.4. ECKLUND_-PP4 (659284) 230.0 kV to BALDWIN_-PP4 (659365) 230.0 kV Transmission Circuit #z b.5. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND1-PP9 (659322) 34.5 kV Two Winding #1 b.6. ECKLUND_-PP4 (659284) 230.0 kV to ECKLUND2-PP9 (659323) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_34 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_35 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_36 | Single Phase Fault with Stuck Breaker on WARD 4 230.00 (652296) 230 kV Bus a. Apply Fault at the WARD 4 230.00 (652296) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. WARD 4 (652296) 230.0 kV to MANDAN 4 (661053) 230.0 kV Transmission Circuit #1 b.3. WARD 4 (652296) 230.0 kV to WARD -CP7 (655647) 115.0 kV to WARD TRT-CP9 (655642) 12.5 kV Three Winding #1 b.4. WARD 4 (652296) 230.0 kV to WARD_SPR-CP7 (655693) 115.0 kV to WARD____-CP9 (655692) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_37 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.5. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.6. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_38 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.5. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.6. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_39 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.5. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.6. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.8. JAMEST29 (652207) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 b.9. JAMEST19 (652208) 13.2 kV to JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_40 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD9 (652221) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_41 | Single Phase Fault with Stuck Breaker on BELFELD3 345.00 (652424) 345 kV Bus a. Apply Fault at the BELFELD3 345.00 (652424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELFELD3 (652424) 345.0 kV to BELFELD4 (652425) 230.0 kV to BELFELD29 (652220) 13.8 kV Three Winding #1 b.4. BELFELD3 (652424) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_42 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_43 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_44 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_45 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #z b.2. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.3. ANTELOPE-BE3 (659101) 345.0 kV to COTEAU__-RR3 (659218) 345.0 kV Transmission Circuit #z b.4. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.5. COTEAU__-RR3 (659218) 345.0 kV to COTEAU_1-RR8 (659222) 69.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_46 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to ANTELP_2-BEG (659107) 23.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_47 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_48 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_49 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_50 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_51 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 b.3. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_52 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to LOGAN___-BE4 (659108) 230.0 kV Transmission Circuit #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to BLAISDEL-BE4 (659143) 230.0 kV Transmission Circuit #1 b.3. LOGAN___-BE4 (659108) 230.0 kV to GEN-2017-214 (760998) 230.0 kV Transmission Circuit #1 b.4. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_53 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_54 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_55 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_56 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_57 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 b.6. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_58 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_59 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_60 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_61 | Single Phase Fault with Stuck Breaker on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.3. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_62 | Single Phase Fault with Stuck Breaker on DAKOTACCESS7115.00 (660040) 115 kV Bus a. Apply Fault at the DAKOTACCESS7115.00 (660040) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDFIELD 7 (660002) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.2. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_63 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_64 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_65 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_66 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_67 | Single Phase Fault with Stuck Breaker on GARRISN4 230.00 (652441) 230 kV Bus a. Apply Fault at the GARRISN4 230.00 (652441) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_68 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_69 | Single Phase Fault with Stuck Breaker on SW561-ER7 115.00 (655419) 115 kV Bus a. Apply Fault at the SW561-ER7 115.00 (655419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.2. CRANDALL-ER7 (655411) 115.0 kV to SW561-ER7 (655419) 115.0 kV Transmission Circuit #1 b.3. SW561-ER7 (655419) 115.0 kV to DAY_CNTY-PP7 (659288) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_70 | Single Phase Fault with Stuck Breaker on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_71 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to POMONA__-PP7 (659280) 115.0 kV Transmission Circuit #1 b.3. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 b.4. EDGELEY7 (652432) 115.0 kV to GEN-2018-039 (762735) 115.0 kV Transmission Circuit #1 b.5. EDGELEY9 (652322) 41.8 kV to EDGELEY7 (652432) 115.0 kV Two Winding #1 b.6. EDGELEY7 (652432) 115.0 kV to EDGELEY8 (652433) 69.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_72 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_73 | Single Phase Fault with Stuck Breaker on GARRISN7 115.00 (652442) 115 kV Bus a. Apply Fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_74 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_75 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_76 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_77 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_78 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_79 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_80 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_81 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_82 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_83 | Single Phase Fault with Stuck Breaker on CARNGTN7 115.00 (652428) 115 kV Bus a. Apply Fault at the CARNGTN7 115.00 (652428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.3. CARNGTN9 (652321) 41.8 kV to CARNGTN7 (652428) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_84 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_85 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_86 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_87 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.4. WATFORD7 (652408) 115.0 kV to CHRRYCRK-MK7 (655840) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_88 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_89 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_90 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_91 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_92 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_93 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_94 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_95 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.5. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.6. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 b.8. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.9. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.10. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.11. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_96 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_97 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.7. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_98 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_99 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_100 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.5. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_101 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.3. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.5. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_102 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.3. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.5. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_103 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.3. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.5. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_104 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.3. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.5. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_105 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.3. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.5. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_106 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.3. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.5. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_107 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z2 b.3. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. GROTON 7 (652512) 115.0 kV to ABERDN SIEB7 (660001) 115.0 kV Transmission Circuit #1 b.5. GROTON18 (652250) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.6. GROTON2 8 (652253) 69.0 kV to GROTON 7 (652512) 115.0 kV Two Winding #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.8. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.9. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_108 | Single Phase Fault with Stuck Breaker on SUMMIT-7 115.00 (652522) 115 kV Bus a. Apply Fault at the SUMMIT-7 115.00 (652522) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.3. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. SUMMIT-7 (652522) 115.0 kV to GEN-2018-007 (762449) 115.0 kV Two Winding #1 b.5. SUMMIT-8 (652209) 69.0 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 b.6. SUMMIT-9 (652326) 43.8 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_109 | Single Phase Fault with Stuck Breaker on SUMMIT-7 115.00 (652522) 115 kV Bus a. Apply Fault at the SUMMIT-7 115.00 (652522) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROBERTSCTY7 (652455) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 b.2. SUMMIT-7 (652522) 115.0 kV to WATERTN7 (652531) 115.0 kV Transmission Circuit #1 b.3. SUMMIT-7 (652522) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 b.4. SUMMIT-7 (652522) 115.0 kV to GEN-2018-007 (762449) 115.0 kV Two Winding #1 b.5. SUMMIT-8 (652209) 69.0 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 b.6. SUMMIT-9 (652326) 43.8 kV to SUMMIT-7 (652522) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_110 | Single Phase Fault with Stuck Breaker on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. CARPENTER 4 (652614) 230.0 kV to CARPENTR-ER8 (655499) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_111 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_112 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_113 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_114 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_115 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_116 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.2. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_117 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_118 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_119 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT29 (652239) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_120 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_121 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_122 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_123 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_124 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERT39 (652240) 13.2 kV to WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV Three Winding #1 b.2. WATERT19 (652237) 13.8 kV to WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV Three Winding #1 b.3. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.6. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.7. WATERTN4 (652530) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_125 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_126 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 b.2. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. WATERTN4 (652530) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 b.4. WATERTN4 (652530) 230.0 kV to WATERTNCAP 4 (652630) 230.0 kV Transmission Circuit #z b.5. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.6. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.7. WATERTN4 (652530) 230.0 kV to WATERSVC (652539) 20.0 kV Two Winding #1 b.8. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 b.9. WATERTN4 (652530) 230.0 kV to WATERTN7 (652531) 115.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_127 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_128 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_129 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_130 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_131 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_132 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z b.2. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. WATERTN3 (652529) 345.0 kV to WATERTN4 (652530) 230.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 b.4. WHITE 3 (652537) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_133 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_134 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_135 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_136 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_137 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_138 | Single Phase Fault with Stuck Breaker on APPLEDORN 4 230.00 (652582) 230 kV Bus a. Apply Fault at the APPLEDORN 4 230.00 (652582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. GRANITF4 (652550) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.3. APPLEDORN 4 (652582) 230.0 kV to APPLEDORN 8 (652604) 69.0 kV to APPLEDORN 9 (652605) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_139 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_140 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_141 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_142 | Single Phase Fault with Stuck Breaker on BLAIR-ER4 230.00 (655465) 230 kV Bus a. Apply Fault at the BLAIR-ER4 230.00 (655465) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANITF4 (652550) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to BLAIR-ER4 (655465) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_143 | Single Phase Fault with Stuck Breaker on DEVILSL7 115.00 (652431) 115 kV Bus a. Apply Fault at the DEVILSL7 115.00 (652431) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DEVIL J7 (620267) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to LAKOTA 7 (652448) 115.0 kV Transmission Circuit #1 b.3. DEVILSL7 (652431) 115.0 kV to PENN 7 (652465) 115.0 kV Transmission Circuit #1 b.4. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.5. DEVILSL9 (652319) 41.8 kV to DEVILSL7 (652431) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_144 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 b.2. WILISTN7 (652421) 115.0 kV to FAIRVIEW 7 (652651) 115.0 kV Transmission Circuit #1 b.3. WILISTN7 (652421) 115.0 kV to MARLEY -LY7 (655793) 115.0 kV Transmission Circuit #1 b.4. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 b.5. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.6. WILISTN7 (652421) 115.0 kV to WILISTN4 (652400) 230.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_145 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_146 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_147 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_148 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_149 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_150 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_151 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_152 | Single Phase Fault with Stuck Breaker on WILLISTON27 115.00 (652391) 115 kV Bus a. Apply Fault at the WILLISTON27 115.00 (652391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to WILISTN7 (652421) 115.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_153 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_154 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_155 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WILLISTON27 (652391) 115.0 kV to WILISTN29 (652622) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_156 | Single Phase Fault with Stuck Breaker on STANTN.T-BE7115.00 (659300) 115 kV Bus a. Apply Fault at the STANTN.T-BE7115.00 (659300) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_157 | Single Phase Fault with Stuck Breaker on GARRISN7 115.00 (652442) 115 kV Bus a. Apply Fault at the GARRISN7 115.00 (652442) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN7 (652442) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.2. STANTN.T-BE7 (659300) 115.0 kV to PICKCITY-RR7 (659543) 115.0 kV Transmission Circuit #1 b.3. BASIN___-BE7 (659109) 115.0 kV to STANTN.T-BE7 (659300) 115.0 kV Transmission Circuit #1 b.4. STANTN.T-BE7 (659300) 115.0 kV to BEULAH27 (661011) 115.0 kV Transmission Circuit #1 b.5. GARRISN7 (652442) 115.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_158 | Single Phase Fault with Stuck Breaker on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON WPARK7 (660003) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.6. HURON BTAP 7 (660009) 115.0 kV to DAKOTACCESS7 (660040) 115.0 kV Transmission Circuit #1 b.7. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_159 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.6. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.7. REDFELD-ER7 (655481) 115.0 kV to REDFELD-ER8 (655482) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_160 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 7 (652515) 115.0 kV to HURON BTAP 7 (660009) 115.0 kV Transmission Circuit #1 b.5. HURON 7 (652515) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_161 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.5. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.6. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 b.7. WOONSKT7 (652528) 115.0 kV to WOONSKT-ER8 (655355) 69.0 kV Two Winding #2 b.8. WOONSKT7 (652528) 115.0 kV to WOONSOCKET W (660306) 34.5 kV Two Winding #1 b.9. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_162 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.5. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_163 | Single Phase Fault with Stuck Breaker on HURON 7 115.00 (652515) 115 kV Bus a. Apply Fault at the HURON 7 115.00 (652515) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 8 (652284) 69.0 kV to HURON 7 (652515) 115.0 kV Two Winding #1 b.2. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.5. HURON 7 (652515) 115.0 kV to WOONSKT7 (652528) 115.0 kV Transmission Circuit #1 b.6. HURON 7 (652515) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_164 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_165 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.5. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_166 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_167 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_168 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_169 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_170 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_171 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.4. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_172 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_173 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_174 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_175 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.5. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.6. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.7. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_176 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_177 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_178 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_179 | Single Phase Fault with Stuck Breaker on ELLIOTT7 115.00 (652462) 115 kV Bus a. Apply Fault at the ELLIOTT7 115.00 (652462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_180 | Single Phase Fault with Stuck Breaker on ELLIOTT7 115.00 (652462) 115 kV Bus a. Apply Fault at the ELLIOTT7 115.00 (652462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_181 | Single Phase Fault with Stuck Breaker on ELLIOTT7 115.00 (652462) 115 kV Bus a. Apply Fault at the ELLIOTT7 115.00 (652462) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FORMAN 7 (652438) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 b.2. ELLIOTT7 (652462) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_182 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. FARGO 4 (652435) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.6. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.7. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.10. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_183 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_184 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.7. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_185 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_186 | Single Phase Fault with Stuck Breaker on FARGOSVC 13.200 (652434) 13.19999981 kV Bus a. Apply Fault at the FARGOSVC 13.200 (652434) 13.19999981 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 b.4. FARGOSVC (652434) 13.2 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_187 | Single Phase Fault with Stuck Breaker on GRNDFKS4 230.00 (652437) 230 kV Bus a. Apply Fault at the GRNDFKS4 230.00 (652437) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_188 | Single Phase Fault with Stuck Breaker on GRNDFKS4 230.00 (652437) 230 kV Bus a. Apply Fault at the GRNDFKS4 230.00 (652437) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_189 | Single Phase Fault with Stuck Breaker on GRNDFKS4 230.00 (652437) 230 kV Bus a. Apply Fault at the GRNDFKS4 230.00 (652437) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRNDFKS4 (652437) 230.0 kV to PRAIRIE4 (657755) 230.0 kV Transmission Circuit #1 b.2. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.3. GRNDFKS4 (652437) 230.0 kV to GRNDFKS7 (652443) 115.0 kV to GRNDFKS9 (652201) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_190 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_191 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_192 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_193 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-007 (587050) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.3. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.4. VALLEYC7 (652454) 115.0 kV to VALLEYC8 (652204) 69.0 kV to VALLEYC9 (652613) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_194 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_195 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_196 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.3. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_197 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.3. JAMESTN7 (652445) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.4. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #1 b.5. JAMESTN9 (652320) 43.8 kV to JAMESTN7 (652445) 115.0 kV Two Winding #2 b.6. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. JAMESTN7 (652445) 115.0 kV to JAMESTN4 (652444) 230.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_198 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_199 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_200 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.3. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_201 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.7. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.8. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.9. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_202 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.3. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.4. GARRISN4 (652441) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.5. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.6. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.7. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST19 (652208) 13.2 kV Three Winding #1 b.8. JAMESTN4 (652444) 230.0 kV to JAMESTN7 (652445) 115.0 kV to JAMEST29 (652207) 13.2 kV Three Winding #1 b.10. GRNDFKS4 (652437) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.11. PICKERT4 (657759) 230.0 kV to PICKERT8 (657923) 69.0 kV to PICKERT9 (620167) 41.6 kV Three Winding #1 b.12. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_203 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WINCHESTER4 (652496) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 b.4. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 b.7. JAMESTN4 (652444) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_204 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WARD 4 (652296) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.3. BISMARK4 (652426) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.4. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.5. WASHBRN9 (652325) 41.8 kV to WASHBRN4 (652456) 230.0 kV Two Winding #1 b.6. BISMARK4 (652426) 230.0 kV to BISMARK7 (652427) 115.0 kV to BISMARK29 (652467) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_205 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_206 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_207 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.9. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_208 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_209 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.9. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_210 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_211 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_212 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_213 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_214 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_215 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_216 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_217 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONT -MW7 (655940) 115.0 kV to STRNDAHL-MW7 (655941) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_218 | Single Phase Fault with Stuck Breaker on MONT -MW7115.00 (655940) 115 kV Bus a. Apply Fault at the MONT -MW7115.00 (655940) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.2. WILLISTON27 (652391) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_219 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_220 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_221 | Single Phase Fault with Stuck Breaker on N.MISRDG-MW7115.00 (655933) 115 kV Bus a. Apply Fault at the N.MISRDG-MW7115.00 (655933) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.2. N.MISRDG-MW7 (655933) 115.0 kV to MONT -MW7 (655940) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to EASTFORK-MW7 (655957) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.5. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_222 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILLISTON27 (652391) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.2. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_223 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_224 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_225 | Single Phase Fault with Stuck Breaker on N.WLST_T-MW7115.00 (655934) 115 kV Bus a. Apply Fault at the N.WLST_T-MW7115.00 (655934) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.WLST_T-MW7 (655934) 115.0 kV to N.WILSTN-MW7 (655936) 115.0 kV Transmission Circuit #1 b.2. N.WILSTN-MW7 (655936) 115.0 kV to NE.WLSTN-MW7 (655937) 115.0 kV Transmission Circuit #1 b.3. N.MISRDG-MW7 (655933) 115.0 kV to N.WLST_T-MW7 (655934) 115.0 kV Transmission Circuit #1 b.4. N.WLST_T-MW7 (655934) 115.0 kV to NW.WLSTN-MW7 (655935) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_226 | Single Phase Fault with Stuck Breaker on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply Fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_227 | Single Phase Fault with Stuck Breaker on SE.WLSTN-MW7115.00 (655938) 115 kV Bus a. Apply Fault at the SE.WLSTN-MW7115.00 (655938) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_228 | Single Phase Fault with Stuck Breaker on TWELVE_M-MW7115.00 (655939) 115 kV Bus a. Apply Fault at the TWELVE_M-MW7115.00 (655939) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to SLETTE -MW7 (655964) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_229 | Single Phase Fault with Stuck Breaker on TWELVE_M-MW7115.00 (655939) 115 kV Bus a. Apply Fault at the TWELVE_M-MW7115.00 (655939) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to SLETTE -MW7 (655964) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_230 | Single Phase Fault with Stuck Breaker on TWELVE_M-MW7115.00 (655939) 115 kV Bus a. Apply Fault at the TWELVE_M-MW7115.00 (655939) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SE.WLSTN-MW7 (655938) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.3. TWELVE_M-MW7 (655939) 115.0 kV to SLETTE -MW7 (655964) 115.0 kV Transmission Circuit #1 b.4. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.5. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_231 | Single Phase Fault with Stuck Breaker on EPPING -MW7115.00 (655959) 115 kV Bus a. Apply Fault at the EPPING -MW7115.00 (655959) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_232 | Single Phase Fault with Stuck Breaker on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply Fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARMVL_T-MW7 (655943) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.2. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.3. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.4. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 b.5. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.6. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 b.7. FARMVALE-MW7 (655923) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_233 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 b.4. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_234 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to WHEELOCK-BE7 (659363) 115.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_235 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_236 | Single Phase Fault with Stuck Breaker on NESET___-BE7115.00 (659139) 115 kV Bus a. Apply Fault at the NESET___-BE7115.00 (659139) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.3. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_237 | Single Phase Fault with Stuck Breaker on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply Fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.3. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.4. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.5. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_238 | Single Phase Fault with Stuck Breaker on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply Fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.2. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.3. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_239 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. NESET___-BE4 (659138) 230.0 kV to NESET___-BE7 (659139) 115.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_240 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_241 | Single Phase Fault with Stuck Breaker on NORMANLK-BD7115.00 (655780) 115 kV Bus a. Apply Fault at the NORMANLK-BD7115.00 (655780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMANLK-BD7 (655780) 115.0 kV to LARSON -BD7 (655781) 115.0 kV Transmission Circuit #1 b.2. NORMANLK-BD7 (655780) 115.0 kV to LINDAHLS-MW7 (655910) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_242 | Single Phase Fault with Stuck Breaker on NORMANLK-BD7115.00 (655780) 115 kV Bus a. Apply Fault at the NORMANLK-BD7115.00 (655780) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORMANLK-BD7 (655780) 115.0 kV to LARSON -BD7 (655781) 115.0 kV Transmission Circuit #1 b.2. NORMANLK-BD7 (655780) 115.0 kV to LINDAHLS-MW7 (655910) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_243 | Single Phase Fault with Stuck Breaker on LINDAHLS-MW7115.00 (655910) 115 kV Bus a. Apply Fault at the LINDAHLS-MW7115.00 (655910) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINDAHLS-MW7 (655910) 115.0 kV to SIMPSON -MW7 (655911) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_244 | Single Phase Fault with Stuck Breaker on PWRSLKTP-MW7115.00 (655947) 115 kV Bus a. Apply Fault at the PWRSLKTP-MW7115.00 (655947) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POWERSLK-MW7 (655946) 115.0 kV to PWRSLKTP-MW7 (655947) 115.0 kV Transmission Circuit #1 b.2. PWRSLKTP-MW7 (655947) 115.0 kV to LIBERTY -MW7 (655948) 115.0 kV Transmission Circuit #1 b.3. PWRSLKTP-MW7 (655947) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_245 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_246 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_247 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_248 | Single Phase Fault with Stuck Breaker on CARNGTN7 115.00 (652428) 115 kV Bus a. Apply Fault at the CARNGTN7 115.00 (652428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.2. DEVILSL7 (652431) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 b.3. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.4. CARNGTN9 (652321) 41.8 kV to CARNGTN7 (652428) 115.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_249 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_250 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_251 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_252 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_253 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD9 (652471) 13.2 kV Three Winding #1 b.4. WATFORD4 (652216) 230.0 kV to WATFORD7 (652408) 115.0 kV to WATFORD29 (652472) 13.2 kV Three Winding #1 b.7. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_254 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_255 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_256 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_257 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WILISTN7 (652421) 115.0 kV to WILISTN9 (652621) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_258 | Single Phase Fault with Stuck Breaker on MOORHED4 230.00 (658172) 230 kV Bus a. Apply Fault at the MOORHED4 230.00 (658172) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to FARGO 7 (652436) 115.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #1 b.4. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 b.5. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #2 b.6. MOORHED4 (658172) 230.0 kV to MOORHDE4 (658208) 230.0 kV Transmission Circuit #1 b.7. MOORHED4 (658172) 230.0 kV to MOORHDW4 (658209) 230.0 kV Transmission Circuit #1 b.8. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #1 b.9. MOORHED4 (658172) 230.0 kV to MOORHED7 (658170) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_259 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_260 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_261 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_262 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_263 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_264 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_265 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON__-BE7 (659187) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_266 | Single Phase Fault with Stuck Breaker on NBCS_10_-PPR12.500 (659278) 12.5 kV Bus a. Apply Fault at the NBCS_10_-PPR12.500 (659278) 12.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to REDFELD-ER7 (655481) 115.0 kV Transmission Circuit #1 b.2. NBCS_10_-PPR (659278) 12.5 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_267 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_268 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_269 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_270 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_271 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_272 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.3. G09_001IST (659165) 345.0 kV to CROCKER_-UA3 (659472) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_273 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_274 | Single Phase Fault with Stuck Breaker on OLIVER -MW7115.00 (655966) 115 kV Bus a. Apply Fault at the OLIVER -MW7115.00 (655966) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 b.2. OLIVER -MW7 (655966) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_275 | Single Phase Fault with Stuck Breaker on ELLISVIL-MW7115.00 (655954) 115 kV Bus a. Apply Fault at the ELLISVIL-MW7115.00 (655954) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLISVIL-MW7 (655954) 115.0 kV to ZAHL -MW7 (655955) 115.0 kV Transmission Circuit #1 b.2. ELLISVIL-MW7 (655954) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_276 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to NRTSHORE-BE4 (659140) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_277 | Single Phase Fault with Stuck Breaker on J1456 POI 230.00 (44568) 230 kV Bus a. Apply Fault at the J1456 POI 230.00 (44568) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1456 POI (44568) 230.0 kV to HARVEY 4 (620290) 230.0 kV Transmission Circuit #1 b.2. J1456 POI (44568) 230.0 kV to UNDERWD4 (620381) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_278 | Single Phase Fault with Stuck Breaker on J1754 POI 230.00 (47544) 230 kV Bus a. Apply Fault at the J1754 POI 230.00 (47544) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J1754 POI (47544) 230.0 kV to GRE-MCHENRY4 (615347) 230.0 kV Transmission Circuit #1 b.2. J1754 POI (47544) 230.0 kV to GRE-COAL TP4 (615900) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_279 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_280 | Single Phase Fault with Stuck Breaker on SQBEAST4 230.00 (608602) 230 kV Bus a. Apply Fault at the SQBEAST4 230.00 (608602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQBEAST4 (608602) 230.0 kV to SQBP2DC4 (608599) 230.0 kV Transmission Circuit #z1 b.2. SQBEAST4 (608602) 230.0 kV to SQBP1DC4 (608597) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_281 | Single Phase Fault with Stuck Breaker on WATFORD4 230.00 (652216) 230 kV Bus a. Apply Fault at the WATFORD4 230.00 (652216) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATFORD4 (652216) 230.0 kV to CHARL_CK-BE4 (659302) 230.0 kV Transmission Circuit #1 b.2. WATFORD4 (652216) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_282 | Single Phase Fault with Stuck Breaker on WILISTN4 230.00 (652400) 230 kV Bus a. Apply Fault at the WILISTN4 230.00 (652400) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN4 (652400) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. WILISTN4 (652400) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_283 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK4 (652426) 230.0 kV to HILKEN 4 (652466) 230.0 kV Transmission Circuit #1 b.2. BISMARK4 (652426) 230.0 kV to HERBERTW-KM4 (659128) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_284 | Single Phase Fault with Stuck Breaker on CARNGTN7 115.00 (652428) 115 kV Bus a. Apply Fault at the CARNGTN7 115.00 (652428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARNGTN7 (652428) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. CARNGTN7 (652428) 115.0 kV to BARLOW -CP7 (655610) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_285 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY7 (652432) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 b.2. EDGELEY7 (652432) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_286 | Single Phase Fault with Stuck Breaker on EDGELEY7 115.00 (652432) 115 kV Bus a. Apply Fault at the EDGELEY7 115.00 (652432) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDGELEY8 (652433) 69.0 kV to EDGELEY7 (652432) 115.0 kV to EDGELEY 19 (652328) 13.2 kV Three Winding #1 b.2. EDGELEY8 (652433) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_287 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 4 (652435) 230.0 kV to SHEYNNE4 (602006) 230.0 kV Transmission Circuit #1 b.2. FARGO 4 (652435) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_288 | Single Phase Fault with Stuck Breaker on JAMESTN4 230.00 (652444) 230 kV Bus a. Apply Fault at the JAMESTN4 230.00 (652444) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN4 (652444) 230.0 kV to PICKERT4 (657759) 230.0 kV Transmission Circuit #1 b.2. JAMESTN4 (652444) 230.0 kV to GARRISN4 (652441) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_289 | Single Phase Fault with Stuck Breaker on JAMESTN7 115.00 (652445) 115 kV Bus a. Apply Fault at the JAMESTN7 115.00 (652445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JAMESTN7 (652445) 115.0 kV to EDGELEY7 (652432) 115.0 kV Transmission Circuit #1 b.2. JAMESTN7 (652445) 115.0 kV to CARNGTN7 (652428) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_290 | Single Phase Fault with Stuck Breaker on VALLEYC7 115.00 (652454) 115 kV Bus a. Apply Fault at the VALLEYC7 115.00 (652454) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VALLEYC7 (652454) 115.0 kV to ENDERLIN 7 (652638) 115.0 kV Transmission Circuit #1 b.2. VALLEYC7 (652454) 115.0 kV to JAMESTN7 (652445) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_291 | Single Phase Fault with Stuck Breaker on WASHBRN4 230.00 (652456) 230 kV Bus a. Apply Fault at the WASHBRN4 230.00 (652456) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WASHBRN4 (652456) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 b.2. WASHBRN4 (652456) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_292 | Single Phase Fault with Stuck Breaker on GROTON 7 115.00 (652512) 115 kV Bus a. Apply Fault at the GROTON 7 115.00 (652512) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON 7 (652512) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #z b.2. GROTON 7 (652512) 115.0 kV to BRISTOL-ER7 (655457) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_293 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to BROADLND-BE4 (659205) 230.0 kV Transmission Circuit #1 b.2. HURON 4 (652514) 230.0 kV to CARPENTER 4 (652614) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_294 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON429 (652282) 13.3 kV Three Winding #2 b.2. HURON 7 (652515) 115.0 kV to HURON 4 (652514) 230.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_295 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN3 (652529) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. WATERTN3 (652529) 345.0 kV to WATERTN-LNX3 (652829) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_296 | Single Phase Fault with Stuck Breaker on WATERTN3 345.00 (652529) 345 kV Bus a. Apply Fault at the WATERTN3 345.00 (652529) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN4 (652530) 230.0 kV to APPLEDORN 4 (652582) 230.0 kV Transmission Circuit #1 b.2. WATERTN4 (652530) 230.0 kV to WATERTN3 (652529) 345.0 kV to WATERT19 (652237) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_297 | Single Phase Fault with Stuck Breaker on GROTONSOUTH7115.00 (652568) 115 kV Bus a. Apply Fault at the GROTONSOUTH7115.00 (652568) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTONSOUTH7 (652568) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #z b.2. GROTONSOUTH7 (652568) 115.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_298 | Single Phase Fault with Stuck Breaker on MOS-IPAB-ER869.000 (655086) 69 kV Bus a. Apply Fault at the MOS-IPAB-ER869.000 (655086) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-IPAB-ER8 (655086) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 b.2. MOS-IPAB-ER8 (655086) 69.0 kV to SW-IPABD-ER8 (655089) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_299 | Single Phase Fault with Stuck Breaker on MOS-ABDN-ER869.000 (655087) 69 kV Bus a. Apply Fault at the MOS-ABDN-ER869.000 (655087) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOS-ABDN-ER8 (655087) 69.0 kV to ABERDEEN-ER8 (655262) 69.0 kV Transmission Circuit #1 b.2. MOS-ABDN-ER8 (655087) 69.0 kV to MCSINCRK-ER8 (655516) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_300 | Single Phase Fault with Stuck Breaker on ABERDEEN-ER869.000 (655262) 69 kV Bus a. Apply Fault at the ABERDEEN-ER869.000 (655262) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ABERDEEN-ER8 (655262) 69.0 kV to ORDWAY-ER8 (655491) 69.0 kV Transmission Circuit #1 b.2. ABERDEEN-ER8 (655262) 69.0 kV to MOS-ABDN-ER8 (655087) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_301 | Single Phase Fault with Stuck Breaker on DICKEYTP-CP869.000 (655625) 69 kV Bus a. Apply Fault at the DICKEYTP-CP869.000 (655625) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DICKEYTP-CP8 (655625) 69.0 kV to EDGELEY8 (652433) 69.0 kV Transmission Circuit #1 b.2. DICKEYTP-CP8 (655625) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_302 | Single Phase Fault with Stuck Breaker on OMEGATAP-CP869.000 (655626) 69 kV Bus a. Apply Fault at the OMEGATAP-CP869.000 (655626) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OMEGATAP-CP8 (655626) 69.0 kV to DICKEYTP-CP8 (655625) 69.0 kV Transmission Circuit #1 b.2. OMEGATAP-CP8 (655626) 69.0 kV to LAMOURTP-CP8 (655627) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_303 | Single Phase Fault with Stuck Breaker on BERTHOLD-CP7115.00 (655641) 115 kV Bus a. Apply Fault at the BERTHOLD-CP7115.00 (655641) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BERTHOLD-CP7 (655641) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. BERTHOLD-CP7 (655641) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_304 | Single Phase Fault with Stuck Breaker on MAKOTI -CP7115.00 (655664) 115 kV Bus a. Apply Fault at the MAKOTI -CP7115.00 (655664) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAKOTI -CP7 (655664) 115.0 kV to RAUB TAP-CP7 (655663) 115.0 kV Transmission Circuit #1 b.2. MAKOTI -CP7 (655664) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_305 | Single Phase Fault with Stuck Breaker on MOE -MW7115.00 (655900) 115 kV Bus a. Apply Fault at the MOE -MW7115.00 (655900) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOE -MW7 (655900) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 b.2. MOE -MW7 (655900) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_306 | Single Phase Fault with Stuck Breaker on BROOKBNK-MW7115.00 (655901) 115 kV Bus a. Apply Fault at the BROOKBNK-MW7115.00 (655901) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROOKBNK-MW7 (655901) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.2. BROOKBNK-MW7 (655901) 115.0 kV to BELDEN -MW7 (655904) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_307 | Single Phase Fault with Stuck Breaker on PLSNTV_T-MW7115.00 (655902) 115 kV Bus a. Apply Fault at the PLSNTV_T-MW7115.00 (655902) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLSNTV_T-MW7 (655902) 115.0 kV to MOE -MW7 (655900) 115.0 kV Transmission Circuit #1 b.2. PLSNTV_T-MW7 (655902) 115.0 kV to WHTEARTH-MW7 (655930) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_308 | Single Phase Fault with Stuck Breaker on BELDEN -MW7115.00 (655904) 115 kV Bus a. Apply Fault at the BELDEN -MW7115.00 (655904) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN -MW7 (655904) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. BELDEN -MW7 (655904) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_309 | Single Phase Fault with Stuck Breaker on HESS GAS-MW7115.00 (655909) 115 kV Bus a. Apply Fault at the HESS GAS-MW7115.00 (655909) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESS GAS-MW7 (655909) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. HESS GAS-MW7 (655909) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_310 | Single Phase Fault with Stuck Breaker on PALERMO -MW7115.00 (655916) 115 kV Bus a. Apply Fault at the PALERMO -MW7115.00 (655916) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PALERMO -MW7 (655916) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 b.2. PALERMO -MW7 (655916) 115.0 kV to STANLEY -MW7 (655917) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_311 | Single Phase Fault with Stuck Breaker on W.BANK__-MW7115.00 (655922) 115 kV Bus a. Apply Fault at the W.BANK__-MW7115.00 (655922) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.BANK__-MW7 (655922) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 b.2. W.BANK__-MW7 (655922) 115.0 kV to FARMVL_T-MW7 (655943) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_312 | Single Phase Fault with Stuck Breaker on RATLAKE -MW7115.00 (655929) 115 kV Bus a. Apply Fault at the RATLAKE -MW7115.00 (655929) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RATLAKE -MW7 (655929) 115.0 kV to NRTSHORE-BE7 (659141) 115.0 kV Transmission Circuit #1 b.2. RATLAKE -MW7 (655929) 115.0 kV to MOE -MW7 (655900) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_313 | Single Phase Fault with Stuck Breaker on WHTEARTH-MW7115.00 (655930) 115 kV Bus a. Apply Fault at the WHTEARTH-MW7115.00 (655930) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHTEARTH-MW7 (655930) 115.0 kV to PLSNTV_T-MW7 (655902) 115.0 kV Transmission Circuit #1 b.2. WHTEARTH-MW7 (655930) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_314 | Single Phase Fault with Stuck Breaker on TWELVE_M-MW7115.00 (655939) 115 kV Bus a. Apply Fault at the TWELVE_M-MW7115.00 (655939) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWELVE_M-MW7 (655939) 115.0 kV to SE.WLSTN-MW7 (655938) 115.0 kV Transmission Circuit #1 b.2. TWELVE_M-MW7 (655939) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_315 | Single Phase Fault with Stuck Breaker on N.TWELVE-MW7115.00 (655942) 115 kV Bus a. Apply Fault at the N.TWELVE-MW7115.00 (655942) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. N.TWELVE-MW7 (655942) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. N.TWELVE-MW7 (655942) 115.0 kV to TWELVE_M-MW7 (655939) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_316 | Single Phase Fault with Stuck Breaker on PLAZA -MW7115.00 (655944) 115 kV Bus a. Apply Fault at the PLAZA -MW7115.00 (655944) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLAZA -MW7 (655944) 115.0 kV to MAKOTI -CP7 (655664) 115.0 kV Transmission Circuit #1 b.2. PLAZA -MW7 (655944) 115.0 kV to PARSHALL-MW7 (655908) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_317 | Single Phase Fault with Stuck Breaker on WHEELS_T-MW7115.00 (655945) 115 kV Bus a. Apply Fault at the WHEELS_T-MW7115.00 (655945) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELS_T-MW7 (655945) 115.0 kV to EPPING -MW7 (655959) 115.0 kV Transmission Circuit #1 b.2. WHEELS_T-MW7 (655945) 115.0 kV to WHEELOCK-BE7 (659363) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_318 | Single Phase Fault with Stuck Breaker on BLAISDEL-MW7115.00 (655949) 115 kV Bus a. Apply Fault at the BLAISDEL-MW7115.00 (655949) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-MW7 (655949) 115.0 kV to PLAZA -MW7 (655944) 115.0 kV Transmission Circuit #1 b.2. BLAISDEL-MW7 (655949) 115.0 kV to BLAISDEL-BE7 (659144) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_319 | Single Phase Fault with Stuck Breaker on TIOGA.N_-MW7115.00 (655952) 115 kV Bus a. Apply Fault at the TIOGA.N_-MW7115.00 (655952) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA.N_-MW7 (655952) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 b.2. TIOGA.N_-MW7 (655952) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_320 | Single Phase Fault with Stuck Breaker on W.BANK_T-MW7115.00 (655953) 115 kV Bus a. Apply Fault at the W.BANK_T-MW7115.00 (655953) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.BANK_T-MW7 (655953) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #1 b.2. W.BANK_T-MW7 (655953) 115.0 kV to HESSRTAP-MW7 (655962) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_321 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_322 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to FINSTAD345 (659060) 345.0 kV Transmission Circuit #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_323 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_324 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE4 (659108) 230.0 kV to LOGAN___-BE7 (659155) 115.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE4 (659108) 230.0 kV to LELAND_O-BE4 (659106) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_325 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE3 (659120) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #z b.2. BROADLND-BE3 (659120) 345.0 kV to BROADLND-BE4 (659205) 230.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_326 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.2. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_327 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE4 (659138) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #z b.2. NESET___-BE4 (659138) 230.0 kV to TANDE___-BE4 (659337) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_328 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE7115.00 (659141) 115 kV Bus a. Apply Fault at the NRTSHORE-BE7115.00 (659141) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE7 (659141) 115.0 kV to BROOKBNK-MW7 (655901) 115.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE7 (659141) 115.0 kV to RATLAKE -MW7 (655929) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_329 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE4 (659143) 230.0 kV to BLAISDEL-BE7 (659144) 115.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE4 (659143) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_330 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE3 (659160) 345.0 kV to G09_001IST (659165) 345.0 kV Transmission Circuit #1 b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_331 | Single Phase Fault with Stuck Breaker on G09_001IST 345.00 (659165) 345 kV Bus a. Apply Fault at the G09_001IST 345.00 (659165) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G09_001IST (659165) 345.0 kV to WATERTN3 (652529) 345.0 kV Transmission Circuit #1 b.2. G09_001IST (659165) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_332 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE3 (659183) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE3 (659183) 345.0 kV to BELFELD3 (652424) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_333 | Single Phase Fault with Stuck Breaker on COTEAU__-RR3345.00 (659218) 345 kV Bus a. Apply Fault at the COTEAU__-RR3345.00 (659218) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 1-RR9 (659219) 13.8 kV Three Winding #1 b.2. COTEAU_1-RR8 (659222) 69.0 kV to COTEAU__-RR3 (659218) 345.0 kV to COTEAU 2-RR9 (659231) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_334 | Single Phase Fault with Stuck Breaker on KENASTON-BE7115.00 (659308) 115 kV Bus a. Apply Fault at the KENASTON-BE7115.00 (659308) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENASTON-BE7 (659308) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 b.2. KENASTON-BE7 (659308) 115.0 kV to KENMARE7 (661052) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_335 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE3 (659333) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 b.2. JUDSON__-BE3 (659333) 345.0 kV to PATENTGT-BE3 (659390) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_336 | Single Phase Fault with Stuck Breaker on TANDE___-BE3345.00 (659336) 345 kV Bus a. Apply Fault at the TANDE___-BE3345.00 (659336) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TANDE___-BE3 (659336) 345.0 kV to TN.LS-JD-BE3 (659427) 345.0 kV Transmission Circuit #z b.2. TANDE___-BE3 (659336) 345.0 kV to TANDE___-BE4 (659337) 230.0 kV to TND.KU3A-BE9 (659338) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_337 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE4 (659362) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. WHEELOCK-BE4 (659362) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_338 | Single Phase Fault with Stuck Breaker on ROUNDUP_-BE3345.00 (659384) 345 kV Bus a. Apply Fault at the ROUNDUP_-BE3345.00 (659384) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROUNDUP_-BE3 (659384) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. ROUNDUP_-BE3 (659384) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_339 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-BE3 (659387) 345.0 kV to ROUNDUP_-BE3 (659384) 345.0 kV Transmission Circuit #1 b.2. KUMMERDG-BE3 (659387) 345.0 kV to KUMMERDG-MK7 (659388) 115.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_340 | Single Phase Fault with Stuck Breaker on PATENTGT-MK7115.00 (659391) 115 kV Bus a. Apply Fault at the PATENTGT-MK7115.00 (659391) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #1 b.2. PATENTGT-MK7 (659391) 115.0 kV to LC_SWY.N-BE7 (659349) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_341 | Single Phase Fault with Stuck Breaker on AV.LS-BD-BE3345.00 (659420) 345 kV Bus a. Apply Fault at the AV.LS-BD-BE3345.00 (659420) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AV.LS-BD-BE3 (659420) 345.0 kV to BD.LS-AV-BE3 (659421) 345.0 kV Transmission Circuit #1 b.2. AV.LS-BD-BE3 (659420) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_342 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.2. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_343 | Single Phase Fault with Stuck Breaker on GR.LS-LO-BE3345.00 (659423) 345 kV Bus a. Apply Fault at the GR.LS-LO-BE3345.00 (659423) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR.LS-LO-BE3 (659423) 345.0 kV to GROTON__-BE3 (659160) 345.0 kV Transmission Circuit #z b.2. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_344 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_345 | Single Phase Fault with Stuck Breaker on HURON WPARK7115.00 (660003) 115 kV Bus a. Apply Fault at the HURON WPARK7115.00 (660003) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON WPARK7 (660003) 115.0 kV to MITCHELL NW7 (660008) 115.0 kV Transmission Circuit #1 b.2. HURON WPARK7 (660003) 115.0 kV to HURON 7 (652515) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_346 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 4 (661084) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #z b.2. TIOGA4 4 (661084) 230.0 kV to WHEELOCK-BE4 (659362) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_347 | Single Phase Fault with Stuck Breaker on TIOGA4 4 230.00 (661084) 230 kV Bus a. Apply Fault at the TIOGA4 4 230.00 (661084) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA4 7 (661085) 115.0 kV to TIOGA4 4 (661084) 230.0 kV to TIOGA4 9 (661900) 13.8 kV Three Winding #1 b.2. TIOGA4 7 (661085) 115.0 kV to NESET___-BE7 (659139) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_348 | Single Phase Fault with Stuck Breaker on TIOGA7 7 115.00 (661086) 115 kV Bus a. Apply Fault at the TIOGA7 7 115.00 (661086) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIOGA7 7 (661086) 115.0 kV to TIOGA4 7 (661085) 115.0 kV Transmission Circuit #1 b.2. TIOGA7 7 (661086) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_349 | Single Phase Fault with Stuck Breaker on RAY JCT7 115.00 (661087) 115 kV Bus a. Apply Fault at the RAY JCT7 115.00 (661087) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAY JCT7 (661087) 115.0 kV to TIOGA7 7 (661086) 115.0 kV Transmission Circuit #1 b.2. RAY JCT7 (661087) 115.0 kV to LTLMUDY7 (661089) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_350 | Single Phase Fault with Stuck Breaker on BD 4230.00 (672601) 230 kV Bus a. Apply Fault at the BD 4230.00 (672601) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD 4 (672601) 230.0 kV to AUBURNTON 4 (672613) 230.0 kV Transmission Circuit #1 b.2. BD 4 (672601) 230.0 kV to KISBEY TAP 4 (673601) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_351 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE4 (602006) 230.0 kV to LAKE PARK T4 (620337) 230.0 kV Transmission Circuit #1 b.2. SHEYNNE4 (602006) 230.0 kV to FARGO 4 (652435) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_352 | Single Phase Fault with Stuck Breaker on GRE-COAL CR4230.00 (615600) 230 kV Bus a. Apply Fault at the GRE-COAL CR4230.00 (615600) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB24 (615605) 230.0 kV Transmission Circuit #z b.2. GRE-COAL CR4 (615600) 230.0 kV to GRE-COALFB34 (615606) 230.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_353 | Single Phase Fault with Stuck Breaker on BRISTOL-ER7 115.00 (655457) 115 kV Bus a. Apply Fault at the BRISTOL-ER7 115.00 (655457) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRISTOL-ER7 (655457) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #1 b.2. BRISTOL-ER7 (655457) 115.0 kV to SUMMIT-7 (652522) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_354 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY__-BE7 (659310) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. ORDWAY__-BE7 (659310) 115.0 kV to ORDWAY-ER8 (655491) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_355 | Single Phase Fault with Stuck Breaker on PICKERT4 230.00 (657759) 230 kV Bus a. Apply Fault at the PICKERT4 230.00 (657759) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PICKERT4 (657759) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 b.2. PICKERT4 (657759) 230.0 kV to GRNDFKS4 (652437) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_356 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CENTER 3 (657791) 345.0 kV to JAMESTN3 (620369) 345.0 kV Transmission Circuit #1 b.2. CENTER 3 (657791) 345.0 kV to CNTSHNT3 (657951) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_357 | Single Phase Fault with Stuck Breaker on NRTSHORE-BE4230.00 (659140) 230 kV Bus a. Apply Fault at the NRTSHORE-BE4230.00 (659140) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRTSHORE-BE4 (659140) 230.0 kV to NESET___-BE4 (659138) 230.0 kV Transmission Circuit #1 b.2. NRTSHORE-BE4 (659140) 230.0 kV to NRTSHORE-BE7 (659141) 115.0 kV to NRTSHORE-BE9 (659142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_358 | Single Phase Fault with Stuck Breaker on DGC_____-BE3345.00 (659212) 345 kV Bus a. Apply Fault at the DGC_____-BE3345.00 (659212) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #1 b.2. DGC_____-BE3 (659212) 345.0 kV to ANTELOPE-BE3 (659101) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_359 | Single Phase Fault with Stuck Breaker on PATENTGT-BE3345.00 (659390) 345 kV Bus a. Apply Fault at the PATENTGT-BE3345.00 (659390) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PATENTGT-BE3 (659390) 345.0 kV to CHARL_CK-BE3 (659183) 345.0 kV Transmission Circuit #1 b.2. PATENTGT-BE3 (659390) 345.0 kV to KUMMERDG-BE3 (659387) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_360 | Single Phase Fault with Stuck Breaker on ELLENDL345 3345.00 (661097) 345 kV Bus a. Apply Fault at the ELLENDL345 3345.00 (661097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL345 3 (661097) 345.0 kV to ELN345SHNT 3 (661950) 345.0 kV Transmission Circuit #z b.2. ELLENDL345 3 (661097) 345.0 kV to ELLENDL345 4 (661098) 230.0 kV to ELLENDL345 9 (661907) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_361 | Single Phase Fault with Stuck Breaker on BDX 4230.00 (672602) 230 kV Bus a. Apply Fault at the BDX 4230.00 (672602) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDX 4 (672602) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #2 b.2. BDX 4 (672602) 230.0 kV to BDV 4 (672603) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_362 | Single Phase Fault with Stuck Breaker on BDV 4230.00 (672603) 230 kV Bus a. Apply Fault at the BDV 4230.00 (672603) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BDV 4 (672603) 230.0 kV to TIOGA4 4 (661084) 230.0 kV Transmission Circuit #1 b.2. BDV 4 (672603) 230.0 kV to BDX 4 (672602) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_363 | Single Phase Fault with Stuck Breaker on WILISTN7 115.00 (652421) 115 kV Bus a. Apply Fault at the WILISTN7 115.00 (652421) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WILISTN7 (652421) 115.0 kV to CULBSN.E-BE7 (659262) 115.0 kV Transmission Circuit #1 b.2. WILISTN7 (652421) 115.0 kV to JUDSON -MW7 (655925) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_364 | Single Phase Fault with Stuck Breaker on WATERTN-LNX3345.00 (652829) 345 kV Bus a. Apply Fault at the WATERTN-LNX3345.00 (652829) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN-LNX3 (652829) 345.0 kV to WATERTN3 (652529) 345.0 kV Transmission Circuit #z b.2. WATERTN-LNX3 (652829) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_365 | Single Phase Fault with Stuck Breaker on BLAISDEL-BE4230.00 (659143) 230 kV Bus a. Apply Fault at the BLAISDEL-BE4230.00 (659143) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLAISDEL-BE7 (659144) 115.0 kV to BLAISDEL-BE4 (659143) 230.0 kV to BLS.T1__-BE9 (659164) 13.8 kV Three Winding #1 b.2. BLAISDEL-BE7 (659144) 115.0 kV to BERTHOLD-CP7 (655641) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_366 | Single Phase Fault with Stuck Breaker on BD.LS-AV-BE3345.00 (659421) 345 kV Bus a. Apply Fault at the BD.LS-AV-BE3345.00 (659421) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BD.LS-AV-BE3 (659421) 345.0 kV to AV.LS-BD-BE3 (659420) 345.0 kV Transmission Circuit #1 b.2. BD.LS-AV-BE3 (659421) 345.0 kV to BROADLND-BE3 (659120) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_367 | Single Phase Fault with Stuck Breaker on TN.LS-JD-BE3345.00 (659427) 345 kV Bus a. Apply Fault at the TN.LS-JD-BE3345.00 (659427) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TN.LS-JD-BE3 (659427) 345.0 kV to TANDE___-BE3 (659336) 345.0 kV Transmission Circuit #z b.2. TN.LS-JD-BE3 (659427) 345.0 kV to EFORK_-BE334 (659600) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_368 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 b.2. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_369 | Single Phase Fault with Stuck Breaker on KENMARE7 115.00 (661052) 115 kV Bus a. Apply Fault at the KENMARE7 115.00 (661052) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KENMARE7 (661052) 115.0 kV to STANLEY7 (661080) 115.0 kV Transmission Circuit #1 b.2. KENMARE7 (661052) 115.0 kV to KENASTON-BE7 (659308) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_370 | Single Phase Fault with Stuck Breaker on ELLENDL345 4230.00 (661098) 230 kV Bus a. Apply Fault at the ELLENDL345 4230.00 (661098) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ELLENDL345 4 (661098) 230.0 kV to OAKES 4 (620362) 230.0 kV Transmission Circuit #1 b.2. ELLENDL345 4 (661098) 230.0 kV to FOXTAIL 4 (661092) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_371 | Single Phase Fault with Stuck Breaker on UNDERWD4 230.00 (620381) 230 kV Bus a. Apply Fault at the UNDERWD4 230.00 (620381) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UNDERWD4 (620381) 230.0 kV to GRE-COAL CR4 (615600) 230.0 kV Transmission Circuit #1 b.2. UNDERWD4 (620381) 230.0 kV to J1456 POI (44568) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_372 | Single Phase Fault with Stuck Breaker on GRE-COAL TP4230.00 (615900) 230 kV Bus a. Apply Fault at the GRE-COAL TP4230.00 (615900) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRE-COAL TP4 (615900) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 b.2. GRE-COAL TP4 (615900) 230.0 kV to J1754 POI (47544) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_373 | Single Phase Fault with Stuck Breaker on CENTER 3 345.00 (657791) 345 kV Bus a. Apply Fault at the CENTER 3 345.00 (657791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR1TE (657947) 13.8 kV Three Winding #1 b.2. SQBUTTE4 (657756) 230.0 kV to CENTER 3 (657791) 345.0 kV to CENTR2TE (657948) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_374 | Single Phase Fault with Stuck Breaker on JUDSON__-BE3345.00 (659333) 345 kV Bus a. Apply Fault at the JUDSON__-BE3345.00 (659333) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JUDSON__-BE4 (659334) 230.0 kV to WILISTN4 (652400) 230.0 kV Transmission Circuit #1 b.2. JUDSON__-BE4 (659334) 230.0 kV to JUDSON__-BE3 (659333) 345.0 kV to JDS.KU6A-BE9 (659335) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_375 | Single Phase Fault with Stuck Breaker on HERBERTW-KM4230.00 (659128) 230 kV Bus a. Apply Fault at the HERBERTW-KM4230.00 (659128) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HERBERTW-KM4 (659128) 230.0 kV to BISMARK4 (652426) 230.0 kV Transmission Circuit #1 b.2. HERBERTW-KM4 (659128) 230.0 kV to JAMESTN4 (652444) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_376 | Single Phase Fault with Stuck Breaker on BARLOW -CP7115.00 (655610) 115 kV Bus a. Apply Fault at the BARLOW -CP7115.00 (655610) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARLOW -CP7 (655610) 115.0 kV to CARNGTN7 (652428) 115.0 kV Transmission Circuit #1 b.2. BARLOW -CP7 (655610) 115.0 kV to DEVILSL7 (652431) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_377 | Single Phase Fault with Stuck Breaker on ENDERLIN 7 115.00 (652638) 115 kV Bus a. Apply Fault at the ENDERLIN 7 115.00 (652638) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ENDERLIN 7 (652638) 115.0 kV to VALLEYC7 (652454) 115.0 kV Transmission Circuit #1 b.2. ENDERLIN 7 (652638) 115.0 kV to ELLIOTT7 (652462) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_378 | Single Phase Fault with Stuck Breaker on ABERDN SIEB7115.00 (660001) 115 kV Bus a. Apply Fault at the ABERDN SIEB7115.00 (660001) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ABERDN SIEB7 (660001) 115.0 kV to ABERDNINDPK7 (660021) 115.0 kV Transmission Circuit #1 b.2. ABERDN SIEB7 (660001) 115.0 kV to GROTON 7 (652512) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_379 | Single Phase Fault with Stuck Breaker on CARPENTER 4 230.00 (652614) 230 kV Bus a. Apply Fault at the CARPENTER 4 230.00 (652614) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 4 (652614) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. CARPENTER 4 (652614) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_380 | Single Phase Fault with Stuck Breaker on BROADLND-BE3345.00 (659120) 345 kV Bus a. Apply Fault at the BROADLND-BE3345.00 (659120) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BROADLND-BE4 (659205) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. BROADLND-BE4 (659205) 230.0 kV to BROADLND-BE3 (659120) 345.0 kV to BD.KU2A_-BE9 (659204) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_381 | Single Phase Fault with Stuck Breaker on WOONSKT7 115.00 (652528) 115 kV Bus a. Apply Fault at the WOONSKT7 115.00 (652528) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOONSKT7 (652528) 115.0 kV to HURON 7 (652515) 115.0 kV Transmission Circuit #1 b.2. WOONSKT7 (652528) 115.0 kV to STORLA__-BE7 (659123) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_382 | Single Phase Fault with Stuck Breaker on REDFELD-ER7 115.00 (655481) 115 kV Bus a. Apply Fault at the REDFELD-ER7 115.00 (655481) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDFELD-ER7 (655481) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. REDFELD-ER7 (655481) 115.0 kV to HURON 7 (652515) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_383 | Single Phase Fault with Stuck Breaker on HURON BTAP 7115.00 (660009) 115 kV Bus a. Apply Fault at the HURON BTAP 7115.00 (660009) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON BTAP 7 (660009) 115.0 kV to HURON 7 (652515) 115.0 kV Transmission Circuit #1 b.2. HURON BTAP 7 (660009) 115.0 kV to HURON WPARK7 (660003) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_384 | Single Phase Fault with Stuck Breaker on GROTON__-BE3345.00 (659160) 345 kV Bus a. Apply Fault at the GROTON__-BE3345.00 (659160) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GROTON__-BE7 (659187) 115.0 kV to GROTONSOUTH7 (652568) 115.0 kV Transmission Circuit #1 b.2. GROTON__-BE7 (659187) 115.0 kV to GROTON__-BE3 (659160) 345.0 kV to GRT.KU2A-BE9 (659161) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_385 | Single Phase Fault with Stuck Breaker on ORDWAY__-BE7115.00 (659310) 115 kV Bus a. Apply Fault at the ORDWAY__-BE7115.00 (659310) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #1 b.2. ORDWAY-ER8 (655491) 69.0 kV to ORDWAY__-BE7 (659310) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_386 | Single Phase Fault with Stuck Breaker on LAMOURTP-CP869.000 (655627) 69 kV Bus a. Apply Fault at the LAMOURTP-CP869.000 (655627) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAMOURTP-CP8 (655627) 69.0 kV to OMEGATAP-CP8 (655626) 69.0 kV Transmission Circuit #1 b.2. LAMOURTP-CP8 (655627) 69.0 kV to WESTOAKS-CP8 (655628) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_387 | Single Phase Fault with Stuck Breaker on HESSRTAP-MW7115.00 (655962) 115 kV Bus a. Apply Fault at the HESSRTAP-MW7115.00 (655962) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HESSRTAP-MW7 (655962) 115.0 kV to W.BANK_T-MW7 (655953) 115.0 kV Transmission Circuit #1 b.2. HESSRTAP-MW7 (655962) 115.0 kV to W.BANK__-MW7 (655922) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_388 | Single Phase Fault with Stuck Breaker on NESET___-BE4230.00 (659138) 230 kV Bus a. Apply Fault at the NESET___-BE4230.00 (659138) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NESET___-BE7 (659139) 115.0 kV to NESET___-BE4 (659138) 230.0 kV to NES.KV2A-BE9 (659146) 13.8 kV Three Winding #1 b.2. NESET___-BE7 (659139) 115.0 kV to TIOGA.N_-MW7 (655952) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_389 | Single Phase Fault with Stuck Breaker on EPPING -MW7115.00 (655959) 115 kV Bus a. Apply Fault at the EPPING -MW7115.00 (655959) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EPPING -MW7 (655959) 115.0 kV to WHEELS_T-MW7 (655945) 115.0 kV Transmission Circuit #1 b.2. EPPING -MW7 (655959) 115.0 kV to N.TWELVE-MW7 (655942) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_390 | Single Phase Fault with Stuck Breaker on WHEELOCK-BE4230.00 (659362) 230 kV Bus a. Apply Fault at the WHEELOCK-BE4230.00 (659362) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WHEELOCK-BE7 (659363) 115.0 kV to WHEELOCK-BE4 (659362) 230.0 kV to WEL.T1__-BE9 (659364) 13.8 kV Three Winding #1 b.2. WHEELOCK-BE7 (659363) 115.0 kV to OLIVER -MW7 (655966) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_391 | Single Phase Fault with Stuck Breaker on GEN-2017-214230.00 (760998) 230 kV Bus a. Apply Fault at the GEN-2017-214230.00 (760998) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-214 (760998) 230.0 kV to G17-235XFMR1 (761062) 34.5 kV Two Winding #1 b.2. GEN-2017-214 (760998) 230.0 kV to G17-236XFMR1 (761083) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_392 | Single Phase Fault with Stuck Breaker on CROCKER_-UA3345.00 (659472) 345 kV Bus a. Apply Fault at the CROCKER_-UA3345.00 (659472) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROCKER_-UA3 (659472) 345.0 kV to CROCKR1_-UA9 (659473) 34.5 kV Two Winding #1 b.2. CROCKER_-UA3 (659472) 345.0 kV to CROCKR1_-UA9 (659476) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_393 | Single Phase Fault with Stuck Breaker on G18-008-TAP 345.00 (762544) 345 kV Bus a. Apply Fault at the G18-008-TAP 345.00 (762544) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-008-TAP (762544) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #1 b.2. G18-008-TAP (762544) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_394 | Single Phase Fault with Stuck Breaker on LTLMUDY7 115.00 (661089) 115 kV Bus a. Apply Fault at the LTLMUDY7 115.00 (661089) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LTLMUDY7 (661089) 115.0 kV to WILLISTON27 (652391) 115.0 kV Transmission Circuit #1 b.2. LTLMUDY7 (661089) 115.0 kV to RAY JCT7 (661087) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_395 | Single Phase Fault with Stuck Breaker on SHAND 4230.00 (672621) 230 kV Bus a. Apply Fault at the SHAND 4230.00 (672621) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHAND 4 (672621) 230.0 kV to PEEBLES 4 (672616) 230.0 kV Transmission Circuit #1 b.2. SHAND 4 (672621) 230.0 kV to BD 4 (672601) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_396 | Single Phase Fault with Stuck Breaker on SHEYNNE4 230.00 (602006) 230 kV Bus a. Apply Fault at the SHEYNNE4 230.00 (602006) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHEYNNE7 (603018) 115.0 kV to MODEROW7 (657704) 115.0 kV Transmission Circuit #1 b.2. SHEYNNE7 (603018) 115.0 kV to SHEYNNE4 (602006) 230.0 kV to SHEYENNE5 9 (605724) 13.8 kV Three Winding #5 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_397 | Single Phase Fault with Stuck Breaker on BISMARK4 230.00 (652426) 230 kV Bus a. Apply Fault at the BISMARK4 230.00 (652426) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BISMARK7 (652427) 115.0 kV to E.BISMRK-CP7 (655652) 115.0 kV Transmission Circuit #1 b.2. BISMARK7 (652427) 115.0 kV to BISMARK4 (652426) 230.0 kV to BISMARK9 (652392) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Oscillations due to Low voltage in the area | Operational steady state fixes (existing caps/taps/gen set points)
01 - North | 25W | Transfer | GROUP1_FAULT_398 | Single Phase Fault with Stuck Breaker on FARGO 4 230.00 (652435) 230 kV Bus a. Apply Fault at the FARGO 4 230.00 (652435) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARGO 7 (652436) 115.0 kV to FARGO 8 (652203) 69.0 kV Two Winding #2 b.2. FARGO 7 (652436) 115.0 kV to FARGO 4 (652435) 230.0 kV to FARGOSVC (652434) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_399 | Single Phase Fault with Stuck Breaker on WATERTN4 230.00 (652530) 230 kV Bus a. Apply Fault at the WATERTN4 230.00 (652530) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT39 (652240) 13.2 kV Three Winding #1 b.2. WATERTN7 (652531) 115.0 kV to WATERTN4 (652530) 230.0 kV to WATERT29 (652239) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_400 | Single Phase Fault with Stuck Breaker on LOGAN___-BE4230.00 (659108) 230 kV Bus a. Apply Fault at the LOGAN___-BE4230.00 (659108) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LOGAN___-BE7 (659155) 115.0 kV to LOGAN___-BE4 (659108) 230.0 kV to LGN.KW1A-BE9 (659208) 13.8 kV Three Winding #1 b.2. LOGAN___-BE7 (659155) 115.0 kV to MALLARD7 (603023) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_401 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE4 (659302) 230.0 kV to WATFORD4 (652216) 230.0 kV Transmission Circuit #1 b.2. CHARL_CK-BE4 (659302) 230.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV4A-BE9 (659319) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_402 | Single Phase Fault with Stuck Breaker on CHARL_CK-BE3345.00 (659183) 345 kV Bus a. Apply Fault at the CHARL_CK-BE3345.00 (659183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHARL_CK-BE7 (659182) 115.0 kV to CHARL_CK-BE3 (659183) 345.0 kV to CCR.KV2A-BE9 (659211) 13.8 kV Three Winding #1 b.2. CHARL_CK-BE7 (659182) 115.0 kV to ROUGHRDR-BE7 (659184) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
01 - North | 25W | Transfer | GROUP1_FAULT_403 | Single Phase Fault with Stuck Breaker on KUMMERDG-BE3345.00 (659387) 345 kV Bus a. Apply Fault at the KUMMERDG-BE3345.00 (659387) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU4A_-BE9 (659389) 13.8 kV Three Winding #1 b.2. KUMMERDG-MK7 (659388) 115.0 kV to KUMMERDG-BE3 (659387) 345.0 kV to KR.KU6A_-BE9 (659394) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_1 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_2 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_3 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_4 | 3 Phase fault on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.6. 33SUPERIOR7 (650233) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_5 | 3 Phase fault on 56&Q 7 115.00 (650260) 115 kV Bus a. Apply fault at the 56&Q 7 115.00 (650260) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_6 | 3 Phase fault on 57&GARLAND7 115.00 (650262) 115 kV Bus a. Apply fault at the 57&GARLAND7 115.00 (650262) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_7 | 3 Phase fault on 93&O 7 115.00 (650273) 115 kV Bus a. Apply fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_8 | 3 Phase fault on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_9 | 3 Phase fault on 84LEIGHTON7 115.00 (650267) 115 kV Bus a. Apply fault at the 84LEIGHTON7 115.00 (650267) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_10 | 3 Phase fault on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_11 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_12 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_13 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_14 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_15 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_16 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_17 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_18 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_19 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_20 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_21 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_22 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_23 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_24 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_25 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_26 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_27 | 3 Phase fault on RIVRBND5 161.00 (635030) 161 kV Bus a. Apply fault at the RIVRBND5 161.00 (635030) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to RIVRBND5 (635030) 161.0 kV Transmission Circuit #1 b.2. RIVRBND5 (635030) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_28 | 3 Phase fault on OBRIEN 3 345.00 (635368) 345 kV Bus a. Apply fault at the OBRIEN 3 345.00 (635368) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OBRIEN 3 (635368) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. OBRIEN 3 (635368) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_29 | 3 Phase fault on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_30 | 3 Phase fault on HASTING5 161.00 (635032) 161 kV Bus a. Apply fault at the HASTING5 161.00 (635032) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNGE 5 (635031) 161.0 kV to HASTING5 (635032) 161.0 kV Transmission Circuit #1 b.2. HASTING5 (635032) 161.0 kV to HASTING8 (635033) 69.0 kV Two Winding #1 b.3. HASTING5 (635032) 161.0 kV to CLRNDA 5 (635034) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_31 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to KELLOGG8 (635222) 69.0 kV Two Winding #1 b.2. KELLOGG5 (635221) 161.0 kV to AIRPORT 5 (635229) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_32 | 3 Phase fault on MONONA 5 161.00 (635300) 161 kV Bus a. Apply fault at the MONONA 5 161.00 (635300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to MONONA 5 (635300) 161.0 kV Transmission Circuit #1 b.2. MONONA 5 (635300) 161.0 kV to MONONA 8 (635301) 69.0 kV Two Winding #1 b.3. MONONA 5 (635300) 161.0 kV to CRWFRD 5 (635330) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_33 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_34 | 3 Phase fault on LEHIGH 3 345.00 (636010) 345 kV Bus a. Apply fault at the LEHIGH 3 345.00 (636010) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LEHIGH 3 (636010) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_35 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_36 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to NOBLES 3 (601034) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_37 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_38 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.81 (605036) 13.8 kV Three Winding #10 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_39 | 3 Phase fault on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SPLT RK7 (603016) 115.0 kV to SPK13.82 (605037) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_40 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_41 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_42 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_43 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_44 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_45 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_46 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_47 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to S1211 5 (646211) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_48 | 3 Phase fault on QUICK 5 161.00 (635012) 161 kV Bus a. Apply fault at the QUICK 5 161.00 (635012) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUICK 5 (635012) 161.0 kV to OVRLND 5 (635015) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_49 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_50 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_51 | 3 Phase fault on PNYCRK 3 345.00 (635013) 345 kV Bus a. Apply fault at the PNYCRK 3 345.00 (635013) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PNYCRK 3 (635013) 345.0 kV to RLHILLS3 (635100) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_52 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to FALLOW 3 (635590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_53 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_54 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_55 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_56 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL S 5 (635202) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_57 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_58 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_59 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to INTCHG 5 (635220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_60 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_61 | 3 Phase fault on INTCHG 5 161.00 (635220) 161 kV Bus a. Apply fault at the INTCHG 5 161.00 (635220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. INTCHG 5 (635220) 161.0 kV to KELLOGG5 (635221) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_62 | 3 Phase fault on KELLOGG5 161.00 (635221) 161 kV Bus a. Apply fault at the KELLOGG5 161.00 (635221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLOGG5 (635221) 161.0 kV to LEEDS 5 (635226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_63 | 3 Phase fault on MORNSD 5 161.00 (635225) 161 kV Bus a. Apply fault at the MORNSD 5 161.00 (635225) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORNSD 5 (635225) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_64 | 3 Phase fault on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_65 | 3 Phase fault on WEBSTER3 345.00 (636000) 345 kV Bus a. Apply fault at the WEBSTER3 345.00 (636000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEBSTER3 (636000) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_66 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS8 (635002) 69.0 kV to CBLUFFS5 (635001) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_67 | 3 Phase fault on CBLUFFS5 161.00 (635001) 161 kV Bus a. Apply fault at the CBLUFFS5 161.00 (635001) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS8 (635002) 69.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_68 | 3 Phase fault on OVRLND 3 345.00 (635014) 345 kV Bus a. Apply fault at the OVRLND 3 345.00 (635014) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. OVRLND 3 (635014) 345.0 kV to OVRLND 5 (635015) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_69 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_70 | 3 Phase fault on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 5 (635203) 161.0 kV to NEAL N 8 (635204) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_71 | 3 Phase fault on SALIX 5 161.00 (635235) 161 kV Bus a. Apply fault at the SALIX 5 161.00 (635235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALIX 5 (635235) 161.0 kV to SALIX 8 (635236) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_72 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_73 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_74 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to RAUN 5 (635201) 161.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_75 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_76 | 3 Phase fault on MANAWA 5 161.00 (635010) 161 kV Bus a. Apply fault at the MANAWA 5 161.00 (635010) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB702 5 (635005) 161.0 kV to MANAWA 5 (635010) 161.0 kV Transmission Circuit #1 b.2. MANAWA 5 (635010) 161.0 kV to INDNCRK5 (635011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_77 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 5 (635003) 161.0 kV to SUB701 8 (635004) 69.0 kV Two Winding #1 b.2. SUB701 5 (635003) 161.0 kV to SUB702 5 (635005) 161.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_78 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_79 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_80 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_81 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_82 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_83 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_84 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_85 | 3 Phase fault on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_86 | 3 Phase fault on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.6. 70&CALVERT7 (650270) 115.0 kV Switched Shunt Device # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_87 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_88 | 3 Phase fault on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_89 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_90 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations; GEN-2018-056 | Build a 50 MVAR STATCOM at GR PRAIRIE 345 kV | Tuned (if applicable) GEN-2018-056 developer model that provides VAR support
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_91 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_92 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_93 | 3 Phase fault on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_94 | 3 Phase fault on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_95 | 3 Phase fault on SALINE 3 115.00 (530551) 115 kV Bus a. Apply fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_96 | 3 Phase fault on OGALATP3 115.00 (530677) 115 kV Bus a. Apply fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_97 | 3 Phase fault on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.2. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_98 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_99 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_100 | 3 Phase fault on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.3. HZRT1 1 (530626) 12.5 kV to HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_101 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_102 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_103 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_104 | 3 Phase fault on S HAYS6 230.00 (530582) 230 kV Bus a. Apply fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_105 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_106 | 3 Phase fault on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHETOLAH3 (530695) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_107 | 3 Phase fault on POSTROCK6 230.00 (530584) 230 kV Bus a. Apply fault at the POSTROCK6 230.00 (530584) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_108 | 3 Phase fault on CALAMS 7 115.00 (640096) 115 kV Bus a. Apply fault at the CALAMS 7 115.00 (640096) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AINSWND7 (640050) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 b.2. CALAMS 7 (640096) 115.0 kV to THEDFRD7 (640381) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_109 | 3 Phase fault on CLRWATR7 115.00 (640113) 115 kV Bus a. Apply fault at the CLRWATR7 115.00 (640113) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLRWATR7 (640113) 115.0 kV to NELIGH 7 (640293) 115.0 kV Transmission Circuit #1 b.2. CLRWATR7 (640113) 115.0 kV to ONEILL 7 (640305) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_110 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_111 | 3 Phase fault on KEAR.NE7 115.00 (640248) 115 kV Bus a. Apply fault at the KEAR.NE7 115.00 (640248) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEAR.NE7 (640248) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 b.2. KEAR.NE7 (640248) 115.0 kV to RIVERDL7 (640331) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_112 | 3 Phase fault on DAVIDCY7 115.00 (640157) 115 kV Bus a. Apply fault at the DAVIDCY7 115.00 (640157) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to DAVIDCY7 (640157) 115.0 kV Transmission Circuit #1 b.2. DAVIDCY7 (640157) 115.0 kV to WAHOO 7 (640402) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_113 | 3 Phase fault on STANTON7 115.00 (640357) 115 kV Bus a. Apply fault at the STANTON7 115.00 (640357) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEEMER 7 (640078) 115.0 kV to STANTON7 (640357) 115.0 kV Transmission Circuit #1 b.2. STANTON7 (640357) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_114 | 3 Phase fault on MADISON7 115.00 (640263) 115 kV Bus a. Apply fault at the MADISON7 115.00 (640263) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESTON7 (640151) 115.0 kV to MADISON7 (640263) 115.0 kV Transmission Circuit #1 b.2. MADISON7 (640263) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_115 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_116 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_117 | 3 Phase fault on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_118 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to KELLY 7 (640134) 115.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 b.4. COLMBS19 (640135) 13.2 kV to KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_119 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_120 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_121 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_122 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_123 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_124 | 3 Phase fault on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_125 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_126 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_127 | 3 Phase fault on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_128 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_129 | 3 Phase fault on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_130 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_131 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_132 | 3 Phase fault on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_133 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_134 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_135 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_136 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREG7 (640224) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_137 | 3 Phase fault on KEARNEY7 115.00 (640250) 115 kV Bus a. Apply fault at the KEARNEY7 115.00 (640250) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KEARNEY7 (640250) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_138 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_139 | 3 Phase fault on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFOLK7 (640298) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_140 | 3 Phase fault on HOSK.T89 34.500 (640230) 34.5 kV Bus a. Apply fault at the HOSK.T89 34.500 (640230) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.3. HOSKINS T2 9 (643082) 13.8 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_141 | 3 Phase fault on HOSK.T89 34.500 (640230) 34.5 kV Bus a. Apply fault at the HOSK.T89 34.500 (640230) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.3. HOSKNS19 (640231) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_142 | 3 Phase fault on HOSK.T89 34.500 (640230) 34.5 kV Bus a. Apply fault at the HOSK.T89 34.500 (640230) 34.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 b.3. HOSKINS T1 9 (643083) 13.8 kV to HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV Three Winding #1 b.4. HOSK.T89 (640230) 34.5 kV Load # | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_143 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_144 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_145 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_146 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_147 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_148 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_149 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_150 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_151 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_152 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_153 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_154 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_155 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_156 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_157 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_158 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_159 | 3 Phase fault on S1216 5 161.00 (646216) 161 kV Bus a. Apply fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_160 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_161 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_162 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_163 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_164 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_165 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_166 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_167 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_168 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_169 | 3 Phase fault on S1299 5 161.00 (646299) 161 kV Bus a. Apply fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1299 5 (646299) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_170 | 3 Phase fault on S1214 5 161.00 (646214) 161 kV Bus a. Apply fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_171 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_172 | 3 Phase fault on S1222 5 161.00 (646222) 161 kV Bus a. Apply fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_173 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_174 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_175 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_176 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_177 | 3 Phase fault on S1226 5 161.00 (646226) 161 kV Bus a. Apply fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_178 | 3 Phase fault on S1227 5 161.00 (646227) 161 kV Bus a. Apply fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_179 | 3 Phase fault on S1231 5 161.00 (646231) 161 kV Bus a. Apply fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_180 | 3 Phase fault on S1232 5 161.00 (646232) 161 kV Bus a. Apply fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_181 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_182 | 3 Phase fault on S1233 5 161.00 (646233) 161 kV Bus a. Apply fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_183 | 3 Phase fault on S1234 5 161.00 (646234) 161 kV Bus a. Apply fault at the S1234 5 161.00 (646234) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_184 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_185 | 3 Phase fault on S1235 5 161.00 (646235) 161 kV Bus a. Apply fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_186 | 3 Phase fault on S1237 5 161.00 (646237) 161 kV Bus a. Apply fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_187 | 3 Phase fault on S1249 5 161.00 (646249) 161 kV Bus a. Apply fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_188 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_189 | 3 Phase fault on S1251 5 161.00 (646251) 161 kV Bus a. Apply fault at the S1251 5 161.00 (646251) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_190 | 3 Phase fault on S1256 5 161.00 (646256) 161 kV Bus a. Apply fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1256 5 (646256) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_191 | 3 Phase fault on S1254 5 161.00 (646254) 161 kV Bus a. Apply fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_192 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_193 | 3 Phase fault on S1255 5 161.00 (646255) 161 kV Bus a. Apply fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_194 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_195 | 3 Phase fault on S1278 5 161.00 (646278) 161 kV Bus a. Apply fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1278 5 (646278) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_196 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_197 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_198 | 3 Phase fault on S1286 5 161.00 (646286) 161 kV Bus a. Apply fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_199 | 3 Phase fault on S1298 5 161.00 (646298) 161 kV Bus a. Apply fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_200 | 3 Phase fault on S1305 5 161.00 (646305) 161 kV Bus a. Apply fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_201 | 3 Phase fault on S1281 5 161.00 (646281) 161 kV Bus a. Apply fault at the S1281 5 161.00 (646281) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_202 | 3 Phase fault on S1259 5 161.00 (646259) 161 kV Bus a. Apply fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_203 | 3 Phase fault on S1253 5 161.00 (646253) 161 kV Bus a. Apply fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_204 | 3 Phase fault on S1367 5 161.00 (646367) 161 kV Bus a. Apply fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1367 5 (646367) 161.0 kV Load # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_205 | 3 Phase fault on FC1A 5 161.00 (645100) 161 kV Bus a. Apply fault at the FC1A 5 161.00 (645100) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FC1A 5 (645100) 161.0 kV to S1251 5 (646251) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_206 | 3 Phase fault on JCT205 8 69.000 (647105) 69 kV Bus a. Apply fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.2. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.3. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_207 | 3 Phase fault on S901 8 69.000 (647901) 69 kV Bus a. Apply fault at the S901 8 69.000 (647901) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_208 | 3 Phase fault on S937 8 69.000 (647937) 69 kV Bus a. Apply fault at the S937 8 69.000 (647937) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_209 | 3 Phase fault on S904 8 69.000 (647904) 69 kV Bus a. Apply fault at the S904 8 69.000 (647904) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_210 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_211 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_212 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_213 | 3 Phase fault on S907 8 69.000 (647907) 69 kV Bus a. Apply fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_214 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_215 | 3 Phase fault on S908 8 69.000 (647908) 69 kV Bus a. Apply fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S908 8 (647908) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_216 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_217 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_218 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_219 | 3 Phase fault on S910 8 69.000 (647910) 69 kV Bus a. Apply fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_220 | 3 Phase fault on S911 8 69.000 (647911) 69 kV Bus a. Apply fault at the S911 8 69.000 (647911) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_221 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_222 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_223 | 3 Phase fault on S918 8 69.000 (647918) 69 kV Bus a. Apply fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_224 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_225 | 3 Phase fault on S919 8 69.000 (647919) 69 kV Bus a. Apply fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_226 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_227 | 3 Phase fault on S921 8 69.000 (647921) 69 kV Bus a. Apply fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_228 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_229 | 3 Phase fault on S912 8 69.000 (647912) 69 kV Bus a. Apply fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_230 | 3 Phase fault on 6815TP38 69.000 (647016) 69 kV Bus a. Apply fault at the 6815TP38 69.000 (647016) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_231 | 3 Phase fault on 6815TP98 69.000 (647017) 69 kV Bus a. Apply fault at the 6815TP98 69.000 (647017) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.2. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.3. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.4. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_232 | 3 Phase fault on S939 8 69.000 (647939) 69 kV Bus a. Apply fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_233 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_234 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_235 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_236 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_237 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_238 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_239 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_240 | 3 Phase fault on S3459 3 345.00 (645459) 345 kV Bus a. Apply fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_241 | 3 Phase fault on S3761 3 345.00 (645761) 345 kV Bus a. Apply fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_242 | 3 Phase fault on S1201 5 161.00 (646201) 161 kV Bus a. Apply fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_243 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_244 | 3 Phase fault on S1210 5 161.00 (646210) 161 kV Bus a. Apply fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_245 | 3 Phase fault on S1211 5 161.00 (646211) 161 kV Bus a. Apply fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1211 5 (646211) 161.0 kV to S911 8 (647911) 69.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_246 | 3 Phase fault on S1221 5 161.00 (646221) 161 kV Bus a. Apply fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_247 | 3 Phase fault on S1250 5 161.00 (646250) 161 kV Bus a. Apply fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_248 | 3 Phase fault on S1217 5 161.00 (646217) 161 kV Bus a. Apply fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_249 | 3 Phase fault on S1366 5 161.00 (646366) 161 kV Bus a. Apply fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.4. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_250 | 3 Phase fault on S1291 5 161.00 (646291) 161 kV Bus a. Apply fault at the S1291 5 161.00 (646291) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1291 5 (646291) 161.0 kV to S991 E 8 (647291) 69.0 kV to S1291T29 (648291) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_251 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_252 | 3 Phase fault on S906 N 8 69.000 (647006) 69 kV Bus a. Apply fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_253 | 3 Phase fault on S906 S 8 69.000 (647906) 69 kV Bus a. Apply fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 S 8 (647906) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_254 | 3 Phase fault on S909 8 69.000 (647909) 69 kV Bus a. Apply fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S909 8 (647909) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_255 | 3 Phase fault on S938 8 69.000 (647938) 69 kV Bus a. Apply fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_256 | 3 Phase fault on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_257 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.3. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_258 | 3 Phase fault on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_259 | 3 Phase fault on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXC19 (652304) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.2. SIOUXC29 (652305) 13.8 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV Three Winding #1 b.3. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_260 | 3 Phase fault on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_261 | 3 Phase fault on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_262 | 3 Phase fault on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_263 | 3 Phase fault on MEADOWGROVE4230.00 (640540) 230 kV Bus a. Apply fault at the MEADOWGROVE4230.00 (640540) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_264 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_265 | 3 Phase fault on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_266 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_267 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 29 (652598) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_268 | 3 Phase fault on OAHE 4 230.00 (652519) 230 kV Bus a. Apply fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV to OAHE 9 (652589) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_269 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_270 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_271 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_272 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_273 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_274 | 3 Phase fault on WSEC 3G 24.000 (635023) 24 kV Bus a. Apply fault at the WSEC 3G 24.000 (635023) 24 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSEC 3G (635023) 24.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_275 | 3 Phase fault on WSEC 4G 26.000 (635024) 26 kV Bus a. Apply fault at the WSEC 4G 26.000 (635024) 26 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSEC 4G (635024) 26.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_276 | 3 Phase fault on NEAL 3G 22.000 (635213) 22 kV Bus a. Apply fault at the NEAL 3G 22.000 (635213) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL 3G (635213) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_277 | 3 Phase fault on NEAL 4G 24.000 (635214) 24 kV Bus a. Apply fault at the NEAL 4G 24.000 (635214) 24 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL 4G (635214) 24.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_278 | 3 Phase fault on COOPER1G 22.000 (640009) 22 kV Bus a. Apply fault at the COOPER1G 22.000 (640009) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER1G (640009) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_279 | 3 Phase fault on NEBCTY1G 18.000 (645011) 18 kV Bus a. Apply fault at the NEBCTY1G 18.000 (645011) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEBCTY1G (645011) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_280 | 3 Phase fault on NEBCTY2G 23.000 (645012) 23 kV Bus a. Apply fault at the NEBCTY2G 23.000 (645012) 23 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEBCTY2G (645012) 23.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_281 | 3 Phase fault on N OMA 4G 15.000 (645024) 15 kV Bus a. Apply fault at the N OMA 4G 15.000 (645024) 15 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N OMA 4G (645024) 15.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_282 | 3 Phase fault on N OMA 5G 20.000 (645025) 20 kV Bus a. Apply fault at the N OMA 5G 20.000 (645025) 20 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. N OMA 5G (645025) 20.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_283 | 3 Phase fault on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARPY 3G (645033) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_284 | 3 Phase fault on SARPY 4G 13.800 (645034) 13.80000019 kV Bus a. Apply fault at the SARPY 4G 13.800 (645034) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARPY 4G (645034) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_285 | 3 Phase fault on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARPY 5G (645035) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_286 | 3 Phase fault on CASS 1G 15.000 (645041) 15 kV Bus a. Apply fault at the CASS 1G 15.000 (645041) 15 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASS 1G (645041) 15.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_287 | 3 Phase fault on CASS 2G 15.000 (645042) 15 kV Bus a. Apply fault at the CASS 2G 15.000 (645042) 15 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASS 2G (645042) 15.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_288 | 3 Phase fault on JONES 1G 13.800 (645051) 13.80000019 kV Bus a. Apply fault at the JONES 1G 13.800 (645051) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 1G (645051) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_289 | 3 Phase fault on JONES 2G 13.800 (645052) 13.80000019 kV Bus a. Apply fault at the JONES 2G 13.800 (645052) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES 2G (645052) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_290 | 3 Phase fault on GRPR11 W 0.6900 (645065) 0.689999998 kV Bus a. Apply fault at the GRPR11 W 0.6900 (645065) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPR11 W (645065) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_291 | 3 Phase fault on GRPR12 W 0.6900 (645066) 0.689999998 kV Bus a. Apply fault at the GRPR12 W 0.6900 (645066) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPR12 W (645066) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_292 | 3 Phase fault on GRPR21 W 0.6900 (645067) 0.689999998 kV Bus a. Apply fault at the GRPR21 W 0.6900 (645067) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPR21 W (645067) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_293 | 3 Phase fault on GRPR22 W 0.6900 (645068) 0.689999998 kV Bus a. Apply fault at the GRPR22 W 0.6900 (645068) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRPR22 W (645068) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_294 | 3 Phase fault on S1297 9 13.800 (649297) 13.80000019 kV Bus a. Apply fault at the S1297 9 13.800 (649297) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1297 9 (649297) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_295 | 3 Phase fault on G18-012-GEN10.6900 (762507) 0.689999998 kV Bus a. Apply fault at the G18-012-GEN10.6900 (762507) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-012-GEN1 (762507) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_296 | 3 Phase fault on G18-025GEN1 0.6600 (762606) 0.660000026 kV Bus a. Apply fault at the G18-025GEN1 0.6600 (762606) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-025GEN1 (762606) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_297 | 3 Phase fault on G18-033GEN1 0.6600 (762694) 0.660000026 kV Bus a. Apply fault at the G18-033GEN1 0.6600 (762694) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-033GEN1 (762694) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_298 | 3 Phase fault on G18-037GEN1 0.6600 (762716) 0.660000026 kV Bus a. Apply fault at the G18-037GEN1 0.6600 (762716) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-037GEN1 (762716) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_299 | 3 Phase fault on G18-043-GEN10.6600 (762783) 0.660000026 kV Bus a. Apply fault at the G18-043-GEN10.6600 (762783) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-043-GEN1 (762783) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_300 | 3 Phase fault on G18-043-GEN20.6600 (762786) 0.660000026 kV Bus a. Apply fault at the G18-043-GEN20.6600 (762786) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-043-GEN2 (762786) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_301 | 3 Phase fault on G18-043-GEN30.6600 (762789) 0.660000026 kV Bus a. Apply fault at the G18-043-GEN30.6600 (762789) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-043-GEN3 (762789) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_302 | 3 Phase fault on G18-056-GEN10.6600 (762914) 0.660000026 kV Bus a. Apply fault at the G18-056-GEN10.6600 (762914) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-056-GEN1 (762914) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_303 | 3 Phase fault on G18-060-GEN10.6300 (762957) 0.629999995 kV Bus a. Apply fault at the G18-060-GEN10.6300 (762957) 0.629999995 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-060-GEN1 (762957) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_304 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_305 | 3 Phase fault on J748POI 345.00 (87487) 345 kV Bus a. Apply fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_306 | 3 Phase fault on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_307 | 3 Phase fault on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_308 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_309 | 3 Phase fault on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_310 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_311 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_312 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_313 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_314 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to EASTOWN7 (541400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_315 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_316 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_317 | 3 Phase fault on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_318 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_319 | 3 Phase fault on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_320 | 3 Phase fault on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_321 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB703 8 (635006) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_322 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB704 8 (635007) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_323 | 3 Phase fault on SUB701 8 69.000 (635004) 69 kV Bus a. Apply fault at the SUB701 8 69.000 (635004) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to HONEYCK8 (635080) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_324 | 3 Phase fault on SUB704 8 69.000 (635007) 69 kV Bus a. Apply fault at the SUB704 8 69.000 (635007) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB704 8 (635007) 69.0 kV to SUB705 8 (635008) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_325 | 3 Phase fault on OVRLND 5 161.00 (635015) 161 kV Bus a. Apply fault at the OVRLND 5 161.00 (635015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OVRLND 5 (635015) 161.0 kV to BUNGE 5 (635031) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_326 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_327 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Divergence of simulation due to low voltage after fault unable to be recovered | Reclosing Removed
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_328 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_329 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_330 | 3 Phase fault on RAUN 5 161.00 (635201) 161 kV Bus a. Apply fault at the RAUN 5 161.00 (635201) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_331 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to NEAL N 5 (635203) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_332 | 3 Phase fault on NEAL S 5 161.00 (635202) 161 kV Bus a. Apply fault at the NEAL S 5 161.00 (635202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL S 5 (635202) 161.0 kV to SALIX 5 (635235) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_333 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_334 | 3 Phase fault on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_335 | 3 Phase fault on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_336 | 3 Phase fault on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_337 | 3 Phase fault on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_338 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_339 | 3 Phase fault on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_340 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to HOLDREG7 (640224) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_341 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to KEARNEY7 (640250) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_342 | 3 Phase fault on AXTELL 7 115.00 (640066) 115 kV Bus a. Apply fault at the AXTELL 7 115.00 (640066) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AXTELL 7 (640066) 115.0 kV to MINDEN 7 (640275) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_343 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_344 | 3 Phase fault on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_345 | 3 Phase fault on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COLMBUS4 (640133) 230.0 kV to SHELCRK4 (640343) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_346 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_347 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_348 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_349 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_350 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_351 | 3 Phase fault on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_352 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_353 | 3 Phase fault on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_354 | 3 Phase fault on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_355 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_356 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_357 | 3 Phase fault on HOSKINS7 115.00 (640228) 115 kV Bus a. Apply fault at the HOSKINS7 115.00 (640228) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_358 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_359 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_360 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_361 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_362 | 3 Phase fault on NORFK.N7 115.00 (640296) 115 kV Bus a. Apply fault at the NORFK.N7 115.00 (640296) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NORFK.N7 (640296) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_363 | 3 Phase fault on PAULINE3 345.00 (640312) 345 kV Bus a. Apply fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_364 | 3 Phase fault on SWEET W3 345.00 (640374) 345 kV Bus a. Apply fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_365 | 3 Phase fault on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_366 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_367 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_368 | 3 Phase fault on S3451 3 345.00 (645451) 345 kV Bus a. Apply fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_369 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_370 | 3 Phase fault on S1209 5 161.00 (646209) 161 kV Bus a. Apply fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_371 | 3 Phase fault on S1236 5 161.00 (646236) 161 kV Bus a. Apply fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_372 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_373 | 3 Phase fault on S1252 5 161.00 (646252) 161 kV Bus a. Apply fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_374 | 3 Phase fault on S1260 5 161.00 (646260) 161 kV Bus a. Apply fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_375 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_376 | 3 Phase fault on S1362 5 161.00 (646362) 161 kV Bus a. Apply fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_377 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_378 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_379 | 3 Phase fault on FTTHOM1-LNX5345.00 (652808) 345 kV Bus a. Apply fault at the FTTHOM1-LNX5345.00 (652808) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM1-LNX5 (652808) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_380 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_381 | 3 Phase fault on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_382 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 1T (541370) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_383 | 3 Phase fault on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ST JOE 7 (541199) 345.0 kV to ST JOE 5 (541253) 161.0 kV to STJOE 2T (541371) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_384 | 3 Phase fault on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EASTOWN7 (541400) 345.0 kV to EASTOWN5 (541401) 161.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_385 | 3 Phase fault on SUB701 5 161.00 (635003) 161 kV Bus a. Apply fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_386 | 3 Phase fault on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BATTLCR8 (640073) 69.0 kV to BATTLCR7 (640072) 115.0 kV to BATTLECRKT19 (643011) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_387 | 3 Phase fault on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELDEN 8 (640081) 69.0 kV to BELDEN 7 (640080) 115.0 kV to BELDEN T1 9 (643016) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_388 | 3 Phase fault on CREITON7 115.00 (640149) 115 kV Bus a. Apply fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CREITON8 (640150) 69.0 kV to CREITON7 (640149) 115.0 kV to CREIGHTONT19 (643045) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_389 | 3 Phase fault on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NELIGH 8 (640294) 69.0 kV to NELIGH 7 (640293) 115.0 kV to NELIGH T2 9 (643108) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_390 | 3 Phase fault on PAULINE7 115.00 (640313) 115 kV Bus a. Apply fault at the PAULINE7 115.00 (640313) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PAULINE8 (640314) 69.0 kV to PAULINE7 (640313) 115.0 kV to PAULINE T2 9 (643121) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_391 | 3 Phase fault on COOPER 5 161.00 (640140) 161 kV Bus a. Apply fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_392 | 3 Phase fault on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOLDREGE 8 (640448) 69.0 kV to HOLDREG7 (640224) 115.0 kV to HOLDREGET3 9 (643177) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_393 | 3 Phase fault on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANTELOPE 8 (640522) 69.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE.T29 (643182) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_394 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_395 | 3 Phase fault on S1206 5 161.00 (646206) 161 kV Bus a. Apply fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_396 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_397 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_398 | 3 Phase fault on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_399 | 3 Phase fault on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_400 | 3 Phase fault on LETCHER4 230.00 (652606) 230 kV Bus a. Apply fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_401 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KU1A_-BE9 (659201) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_402 | 3 Phase fault on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV to LO.KVA2_-BE9 (659202) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_403 | 3 Phase fault on NEAL N 8 69.000 (635204) 69 kV Bus a. Apply fault at the NEAL N 8 69.000 (635204) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEAL N 8 (635204) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_404 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_405 | 3 Phase fault on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_406 | 3 Phase fault on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_407 | 3 Phase fault on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD3 (653571) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_408 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_409 | 3 Phase fault on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_410 | 3 Phase fault on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TRIPLEH__UA3 (659433) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_1 | Single Phase Fault with Stuck Breaker on AIRPORT 5 161.00 (635229) 161 kV Bus a. Apply Fault at the AIRPORT 5 161.00 (635229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AIRPORT 5 (635229) 161.0 kV to LIBERTY5 (635230) 161.0 kV Transmission Circuit #1 b.2. AIRPORT 5 (635229) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_2 | Single Phase Fault with Stuck Breaker on LAKEFLD3 345.00 (631138) 345 kV Bus a. Apply Fault at the LAKEFLD3 345.00 (631138) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAKEFLD3 (631138) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 b.2. LAKEFLD3 (631138) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_3 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_4 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_5 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_6 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 b.2. FT CAL1G (645001) 22.0 kV to FC1A1 9 (645101) 4.2 kV Transmission Circuit #1 b.3. FT CAL1G (645001) 22.0 kV to FC1A2 9 (645102) 4.2 kV Transmission Circuit #1 b.4. S3451 3 (645451) 345.0 kV to FT CAL1G (645001) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_7 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_8 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_9 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_10 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_11 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_12 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_13 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_14 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_15 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_16 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_17 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S1366 5 (646366) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_18 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S1366 5 (646366) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_19 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. S1366 5 (646366) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_20 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_21 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_22 | Single Phase Fault with Stuck Breaker on S994 8 69.000 (647994) 69 kV Bus a. Apply Fault at the S994 8 69.000 (647994) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.8. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_23 | Single Phase Fault with Stuck Breaker on SAC629 8 69.000 (647108) 69 kV Bus a. Apply Fault at the SAC629 8 69.000 (647108) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.6. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.7. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_24 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.5. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.8. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_25 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.5. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.6. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.7. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_26 | Single Phase Fault with Stuck Breaker on S995 8 69.000 (647995) 69 kV Bus a. Apply Fault at the S995 8 69.000 (647995) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S994 8 (647994) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_27 | Single Phase Fault with Stuck Breaker on SAC623 8 69.000 (647107) 69 kV Bus a. Apply Fault at the SAC623 8 69.000 (647107) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.9. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.10. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_28 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_29 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_30 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_31 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_32 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_33 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_34 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_35 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_36 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_37 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_38 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_39 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_40 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW70FAIRFD7 (650210) 115.0 kV to NW68HOLDRG7 (650214) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_41 | Single Phase Fault with Stuck Breaker on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply Fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 33SUPERIOR7 (650233) 115.0 kV to 29LEIGHTON7 (650240) 115.0 kV Transmission Circuit #1 b.2. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.3. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.4. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.7. 33SUPERIOR7 (650233) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_42 | Single Phase Fault with Stuck Breaker on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply Fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 27FLETCHER7 (650228) 115.0 kV to 33SUPERIOR7 (650233) 115.0 kV Transmission Circuit #1 b.2. 19&ALVO 7 (650215) 115.0 kV to 27FLETCHER7 (650228) 115.0 kV Transmission Circuit #1 b.3. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.4. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.5. 27FLETCHER7 (650228) 115.0 kV to 27&FL 9 (650328) 12.5 kV to 281TERTIARY (650528) 9.2 kV Three Winding #1 b.8. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.11. 33SUPERIOR7 (650233) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_43 | Single Phase Fault with Stuck Breaker on 56&Q 7 115.00 (650260) 115 kV Bus a. Apply Fault at the 56&Q 7 115.00 (650260) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&EVERETT7 (650256) 115.0 kV to 56&Q 7 (650260) 115.0 kV Transmission Circuit #1 b.2. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 56&Q 7 (650260) 115.0 kV to 56&Q A9 (650360) 13.2 kV to 601TERTIARY (650560) 7.2 kV Three Winding #1 b.4. 56&Q 7 (650260) 115.0 kV to 56&Q B9 (650460) 13.2 kV to 602TERTIARY (650660) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_44 | Single Phase Fault with Stuck Breaker on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply Fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.4. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.7. 33SUPERIOR7 (650233) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_45 | Single Phase Fault with Stuck Breaker on 33SUPERIOR7 115.00 (650233) 115 kV Bus a. Apply Fault at the 33SUPERIOR7 115.00 (650233) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.2. 59CRNHUSKR7 (650259) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 b.3. 33SUPERIOR7 (650233) 115.0 kV to 59CRNHUSKR7 (650259) 115.0 kV Transmission Circuit #1 b.4. 59CRNHUSKR7 (650259) 115.0 kV to 59&CO 9 (650359) 13.2 kV to 591TERTIARY (650559) 7.2 kV Three Winding #1 b.7. 33SUPERIOR7 (650233) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_46 | Single Phase Fault with Stuck Breaker on 57&GARLAND7 115.00 (650262) 115 kV Bus a. Apply Fault at the 57&GARLAND7 115.00 (650262) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 56&Q 7 (650260) 115.0 kV to 57&GARLAND7 (650262) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_47 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_48 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_49 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_50 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 56&EVERETT7 (650256) 115.0 kV to 56&ELK TAP7 (650257) 115.0 kV Transmission Circuit #1 b.4. 56&ELK TAP7 (650257) 115.0 kV to 40&GERTIE 7 (650258) 115.0 kV Transmission Circuit #1 b.5. 56&ELK TAP7 (650257) 115.0 kV to 70&CALVERT7 (650270) 115.0 kV Transmission Circuit #1 b.6. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.9. 70&CALVERT7 (650270) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_51 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.4. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.5. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.8. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 b.11. 70&CALVERT7 (650270) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_52 | Single Phase Fault with Stuck Breaker on 93&O 7 115.00 (650273) 115 kV Bus a. Apply Fault at the 93&O 7 115.00 (650273) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 b.4. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_53 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to 91&HWY2 7 (650274) 115.0 kV Transmission Circuit #1 b.2. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_54 | Single Phase Fault with Stuck Breaker on 81&OCHENEY7 115.00 (650271) 115 kV Bus a. Apply Fault at the 81&OCHENEY7 115.00 (650271) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 81&OCHENEY7 (650271) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_55 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.2. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.3. 70&BLUFF 7 (650269) 115.0 kV to 84&BLUFF 7 (650275) 115.0 kV Transmission Circuit #1 b.4. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_56 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_57 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_58 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_59 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_60 | Single Phase Fault with Stuck Breaker on HASTING4 230.00 (640214) 230 kV Bus a. Apply Fault at the HASTING4 230.00 (640214) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.6. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 b.7. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.8. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.9. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_61 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.10. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.11. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.12. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_62 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON419 (652281) 13.3 kV to HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV Three Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_63 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_64 | Single Phase Fault with Stuck Breaker on 84FLETCHER7 115.00 (650284) 115 kV Bus a. Apply Fault at the 84FLETCHER7 115.00 (650284) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84&BLUFF 7 (650275) 115.0 kV to TBGS_B 7 (650278) 115.0 kV Transmission Circuit #1 b.2. TBGS_B 7 (650278) 115.0 kV to TBGS 1G (650001) 13.8 kV Two Winding #1 b.3. TBGS_B 7 (650278) 115.0 kV to TBGS 2G (650002) 13.8 kV Two Winding #1 b.4. TBGS_B 7 (650278) 115.0 kV to TBGS 3G (650003) 13.8 kV Two Winding #1 b.5. 84&BLUFF 7 (650275) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.6. 84LEIGHTON7 (650267) 115.0 kV to 84FLETCHER7 (650284) 115.0 kV Transmission Circuit #1 b.7. 84FLETCHER7 (650284) 115.0 kV to 84&FL 9 (650384) 13.2 kV to 841TERTIARY (650584) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_65 | Single Phase Fault with Stuck Breaker on WAVERLY 7 115.00 (650283) 115 kV Bus a. Apply Fault at the WAVERLY 7 115.00 (650283) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.2. 84&BLUFF 7 (650275) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.3. WAVERLY 7 (650283) 115.0 kV to WAVERLY A9 (650383) 13.2 kV to 831TERTIARY (650583) 7.2 kV Three Winding #1 b.4. WAVERLY 7 (650283) 115.0 kV to WAVERLY B9 (650483) 12.5 kV to 832TERTIARY (650683) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_66 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_67 | Single Phase Fault with Stuck Breaker on 120&ALVO 7 115.00 (650279) 115 kV Bus a. Apply Fault at the 120&ALVO 7 115.00 (650279) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAVERLY 7 (650283) 115.0 kV Transmission Circuit #1 b.3. 120&ALVO 7 (650279) 115.0 kV to 120&ALVO 9 (650379) 12.5 kV to 791TERTIARY (650579) 7.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_68 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_69 | Single Phase Fault with Stuck Breaker on WAGENER 7 115.00 (650285) 115 kV Bus a. Apply Fault at the WAGENER 7 115.00 (650285) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 b.2. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_70 | Single Phase Fault with Stuck Breaker on 2&N 7 115.00 (650230) 115 kV Bus a. Apply Fault at the 2&N 7 115.00 (650230) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 b.5. SW27&F 7 (650216) 115.0 kV to 2&N 7 (650230) 115.0 kV Transmission Circuit #1 b.6. SW27&F 7 (650216) 115.0 kV to SW27&F 9 (650316) 12.5 kV to 161TERTIARY (650516) 7.2 kV Three Winding #1 b.9. 2&N 7 (650230) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_71 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 93&O 7 (650273) 115.0 kV Transmission Circuit #1 b.3. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.4. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.5. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.8. 93&O 7 (650273) 115.0 kV to 93&O 9 (650373) 12.5 kV to 731TERTIARY (650573) 9.2 kV Three Winding #1 b.11. 70&CALVERT7 (650270) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_72 | Single Phase Fault with Stuck Breaker on 70&CALVERT7 115.00 (650270) 115 kV Bus a. Apply Fault at the 70&CALVERT7 115.00 (650270) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 84LEIGHTON7 (650267) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.2. 70&CALVERT7 (650270) 115.0 kV to 91&A 7 (650272) 115.0 kV Transmission Circuit #1 b.3. 57&GARLAND7 (650262) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.4. 91&A 7 (650272) 115.0 kV to 91&A 9 (650372) 13.2 kV to 721TERTIARY (650572) 7.2 kV Three Winding #1 b.7. 70&CALVERT7 (650270) 115.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_73 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_74 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.6. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_75 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.6. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_76 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.2. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.3. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.4. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.5. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.6. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_77 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.4. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 b.5. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.6. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.7. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.9. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_78 | Single Phase Fault with Stuck Breaker on HASTING7 115.00 (640215) 115 kV Bus a. Apply Fault at the HASTING7 115.00 (640215) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HASTING7 (640215) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #z1 b.2. E7THST 7 (641085) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.3. EGYCNTR7 (641087) 115.0 kV to HASTCTY7 (641088) 115.0 kV Transmission Circuit #1 b.4. HASTCTY7 (641088) 115.0 kV to HASTING4 (640214) 230.0 kV to HASTINGS T39 (643075) 13.8 kV Three Winding #1 b.5. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #1 b.6. HASTING7 (640215) 115.0 kV to PAULINE7 (640313) 115.0 kV Transmission Circuit #2 b.7. HASTING7 (640215) 115.0 kV to EGYCNTR7 (641087) 115.0 kV Transmission Circuit #1 b.8. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T19 (643076) 13.8 kV Three Winding #1 b.9. HASTING7 (640215) 115.0 kV to HASTING9 (640216) 34.5 kV to HASTINGS T29 (643077) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_79 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.2. RHOADES3 (531373) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.3. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. BEACH 3 (530557) 115.0 kV to HILLCTY3 (531387) 34.5 kV Two Winding #1 b.6. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.7. HOXIE 3 (530556) 115.0 kV to SEGNTP 3 (530682) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_80 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_81 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_82 | Single Phase Fault with Stuck Breaker on BEACH 3 115.00 (530557) 115 kV Bus a. Apply Fault at the BEACH 3 115.00 (530557) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOXIE 3 (530556) 115.0 kV to BEACH 3 (530557) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. BEACH 3 (530557) 115.0 kV to GRHMSUB3 (531386) 115.0 kV Transmission Circuit #1 b.4. BEACH 3 (530557) 115.0 kV to HILLCTY3 (531387) 34.5 kV Two Winding #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_83 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.3. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_84 | Single Phase Fault with Stuck Breaker on GMEC 3 115.00 (530676) 115 kV Bus a. Apply Fault at the GMEC 3 115.00 (530676) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.4. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_85 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to BEMIS 3 (530590) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_86 | Single Phase Fault with Stuck Breaker on SALINE 3 115.00 (530551) 115 kV Bus a. Apply Fault at the SALINE 3 115.00 (530551) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 b.2. SALINE 3 (530551) 115.0 kV to PLAINVL3 (539686) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_87 | Single Phase Fault with Stuck Breaker on KNOLL 3 115.00 (530561) 115 kV Bus a. Apply Fault at the KNOLL 3 115.00 (530561) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. SALINE 3 (530551) 115.0 kV to KNOLL 3 (530561) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_88 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to GMEC 3 (530676) 115.0 kV Transmission Circuit #1 b.2. GMEC 3 (530676) 115.0 kV to GMECG1 1 (530674) 13.8 kV Two Winding #1 b.3. GMEC 3 (530676) 115.0 kV to GMECG2 1 (530675) 13.8 kV Two Winding #2 b.4. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 b.5. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.6. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.7. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_89 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.2. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.3. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.4. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 b.5. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_90 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALXNDR 3 (530606) 115.0 kV to NESCTY 3 (530607) 115.0 kV Transmission Circuit #1 b.2. ALXNDR 3 (530606) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.3. ALXNDR 3 (530606) 115.0 kV to ALEXNDR1 (539702) 34.5 kV to ALEXND-T (539902) 12.5 kV Three Winding #1 b.4. ALEXND-T (539902) 12.5 kV to ALEXNDR1 (539702) 34.5 kV to ALXNDR 3 (530606) 115.0 kV Three Winding #1 b.6. LAXTAP 3 (530602) 115.0 kV to NEKOMA 3 (530608) 115.0 kV Transmission Circuit #1 b.7. NEKOMA 2 (530564) 69.0 kV to NEKOMA 3 (530608) 115.0 kV Two Winding #1 b.8. NEKOMA 3 (530608) 115.0 kV to NEKOMA 2 (530564) 69.0 kV to NKMA2 1 (530630) 12.5 kV Three Winding #2 b.10. HEIZER 3 (530601) 115.0 kV to LAXTAP 3 (530602) 115.0 kV Transmission Circuit #1 b.11. LAXTAP 3 (530602) 115.0 kV to LACROS 3 (530603) 115.0 kV Transmission Circuit #1 b.12. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_91 | Single Phase Fault with Stuck Breaker on VINETAP3 115.00 (530693) 115 kV Bus a. Apply Fault at the VINETAP3 115.00 (530693) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. N HAYS3 (530581) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 b.3. VINETAP3 (530693) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.4. VINETAP3 (530693) 115.0 kV to VINEDE_N (530721) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to N HAYS3 (530581) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_92 | Single Phase Fault with Stuck Breaker on S HAYS 3 115.00 (530553) 115 kV Bus a. Apply Fault at the S HAYS 3 115.00 (530553) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 b.2. SHYS1 1 (530632) 12.5 kV to S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV Three Winding #1 b.3. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.4. S HAYS 3 (530553) 115.0 kV to PFEIFER 3 (530725) 115.0 kV Transmission Circuit #1 b.5. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.6. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.7. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_93 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_94 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_95 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_96 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_97 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_98 | Single Phase Fault with Stuck Breaker on SHAYS_COLLR134.500 (530613) 34.5 kV Bus a. Apply Fault at the SHAYS_COLLR134.500 (530613) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to SHAYS_230 (530610) 230.0 kV Transmission Circuit #1 b.3. SHAYS_230 (530610) 230.0 kV to SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_13.8 (530611) 13.8 kV Three Winding #1 b.5. SHAYS_COLLR2 (530612) 34.5 kV to SHAYS_COLLR1 (530613) 34.5 kV Transmission Circuit #1 b.7. SHAYS_COLLR1 (530613) 34.5 kV to SHAYS_GEN (530614) 0.7 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_99 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_100 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_101 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_102 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.5. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_103 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 b.4. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_104 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_105 | Single Phase Fault with Stuck Breaker on GORHAM 3 115.00 (530552) 115 kV Bus a. Apply Fault at the GORHAM 3 115.00 (530552) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to S HAYS 3 (530553) 115.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.4. GORHAM 3 (530552) 115.0 kV to RUSLPMP3 (530684) 115.0 kV Transmission Circuit #1 b.5. GORHAM 3 (530552) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 b.6. S HAYS 3 (530553) 115.0 kV to ANGUS 3 (530714) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_106 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_107 | Single Phase Fault with Stuck Breaker on OGALATP3 115.00 (530677) 115 kV Bus a. Apply Fault at the OGALATP3 115.00 (530677) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. WKNNY 3 (530560) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to OGALATP3 (530677) 115.0 kV Transmission Circuit #1 b.6. OGALATP3 (530677) 115.0 kV to OG ONEOK (531492) 115.0 kV Transmission Circuit #1 b.7. WKNNY 3 (530560) 115.0 kV to TURKEYR3 (531497) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_108 | Single Phase Fault with Stuck Breaker on REDLIN 3 115.00 (530605) 115 kV Bus a. Apply Fault at the REDLIN 3 115.00 (530605) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.4. BEACH 3 (530557) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 b.5. KNOLL 3 (530561) 115.0 kV to REDLIN 3 (530605) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_109 | Single Phase Fault with Stuck Breaker on HEIZER 3 115.00 (530601) 115 kV Bus a. Apply Fault at the HEIZER 3 115.00 (530601) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 3 (530601) 115.0 kV to HEIZER 2 (530563) 69.0 kV to HZRT2 1 (530627) 12.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_110 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.4. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_111 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_112 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.4. KNOLL N 6 (530558) 230.0 kV to KNOLL 3 (530561) 115.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_113 | Single Phase Fault with Stuck Breaker on KNOLL S 6 230.00 (530720) 230 kV Bus a. Apply Fault at the KNOLL S 6 230.00 (530720) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 b.2. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.3. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_114 | Single Phase Fault with Stuck Breaker on BUCKEYE_W2 34.500 (530707) 34.5 kV Bus a. Apply Fault at the BUCKEYE_W2 34.500 (530707) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #2 b.2. POSTROCK6 (530584) 230.0 kV to BUCKEYE_230 (530702) 230.0 kV Transmission Circuit #1 b.3. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_E1 (530703) 34.5 kV to BUCKE_TERT (530709) 13.8 kV Three Winding #1 b.4. BUCKEYE_230 (530702) 230.0 kV to BUCKEYE_W1 (530710) 34.5 kV to BUCKW_TERT (530706) 13.8 kV Three Winding #1 b.6. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_E2 (530704) 34.5 kV Transmission Circuit #1 b.7. BUCKEYE_E1 (530703) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #z1 b.8. BUCKEYE_E1 (530703) 34.5 kV to GEN-2016-160 (588450) 34.5 kV Transmission Circuit #1 b.10. BUCKE_WTG (530705) 0.7 kV to BUCKEYE_E2 (530704) 34.5 kV Two Winding #1 b.11. BUCKEYE_W2 (530707) 34.5 kV to BUCKEYE_W1 (530710) 34.5 kV Transmission Circuit #1 b.14. BUCKW_WTG (530708) 0.7 kV to BUCKEYE_W2 (530707) 34.5 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_115 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_116 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_117 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to GENTLM2G (640011) 24.0 kV Two Winding #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to G.GENT19 (640185) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_118 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to OGALALA4 (640302) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to GENTLMN3 (640183) 345.0 kV to GENTLEMANT29 (643066) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_119 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_120 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to KEYSTON3 (640252) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.3. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.4. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_121 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_122 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_123 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_124 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_125 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_126 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_127 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.W4 (640131) 230.0 kV to GR ISLD4 (640200) 230.0 kV Transmission Circuit #1 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_128 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_129 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. AXTELL 7 (640066) 115.0 kV to AXTELL 3 (640065) 345.0 kV to AXTELL 9 (640067) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_130 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_131 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_132 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_133 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_134 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_135 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_136 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_137 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_138 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_139 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_140 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_141 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH7 (640378) 115.0 kV to TEKAMAH5 (640377) 161.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_142 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to ANTELOPE 3 (640520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_143 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_144 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_145 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_146 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_147 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.3. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_148 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to STNTN.N7 (640363) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_149 | Single Phase Fault with Stuck Breaker on HOSKINS4 230.00 (640227) 230 kV Bus a. Apply Fault at the HOSKINS4 230.00 (640227) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 b.3. HOSKINS7 (640228) 115.0 kV to HOSKINS4 (640227) 230.0 kV to HOSKINS T1 9 (643083) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_150 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_151 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_152 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD7 (640201) 115.0 kV to GR ISLD4 (640200) 230.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_153 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.3. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_154 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.4. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_155 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_156 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_157 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_158 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_159 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_160 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_161 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_162 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_163 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_164 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_165 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_166 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_167 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_168 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_169 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_170 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_171 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_172 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_173 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_174 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_175 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_176 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_177 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_178 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_179 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_180 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_181 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_182 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_183 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_184 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_185 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_186 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_187 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_188 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_189 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_190 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_191 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_192 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_193 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_194 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_195 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_196 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_197 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 b.4. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_198 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_199 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_200 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_201 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_202 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_203 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_204 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_205 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_206 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_207 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_208 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_209 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S901 8 (647901) 69.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_210 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_211 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1201 5 (646201) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_212 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_213 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_214 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_215 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SCBSD G (645030) 4.2 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 b.3. S1206 5 (646206) 161.0 kV to SARPY 3G (645033) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_216 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_217 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_218 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_219 | Single Phase Fault with Stuck Breaker on SARPY 3G 13.800 (645033) 13.80000019 kV Bus a. Apply Fault at the SARPY 3G 13.800 (645033) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. SARPY 3G (645033) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_220 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_221 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_222 | Single Phase Fault with Stuck Breaker on S1206 5 161.00 (646206) 161 kV Bus a. Apply Fault at the S1206 5 161.00 (646206) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 5G (645035) 13.8 kV Three Winding #1 b.3. SARPY 5G (645035) 13.8 kV to S1206 5 (646206) 161.0 kV to SARPY 4G (645034) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_223 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator # b.3. SARPY 5G (645035) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_224 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator # b.3. SARPY 5G (645035) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_225 | Single Phase Fault with Stuck Breaker on SARPY 5G 13.800 (645035) 13.80000019 kV Bus a. Apply Fault at the SARPY 5G 13.800 (645035) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to S1206 5 (646206) 161.0 kV Transmission Circuit #1 b.2. SARPY 4G (645034) 13.8 kV to Generator # b.3. SARPY 5G (645035) 13.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_226 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_227 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_228 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_229 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_230 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_231 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_232 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_233 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_234 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_235 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_236 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_237 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_238 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_239 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_240 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_241 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_242 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_243 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_244 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_245 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_246 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_247 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_248 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S909 8 (647909) 69.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.4. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_249 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_250 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_251 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_252 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_253 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_254 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S910 8 (647910) 69.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_255 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.4. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_256 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.4. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_257 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. N OMA 2G (645022) 13.8 kV to NO2 AUX9 (645122) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 2G (645022) 13.8 kV Two Winding #1 b.4. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_258 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.4. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_259 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.4. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_260 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. N OMA 3G (645023) 13.8 kV to NO3 AUX9 (645123) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 3G (645023) 13.8 kV Two Winding #1 b.4. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_261 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_262 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_263 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. N OMA 4G (645024) 15.0 kV to NO4 AUX9 (645124) 2.4 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 4G (645024) 15.0 kV Two Winding #1 b.4. S1299 5 (646299) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_264 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_265 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_266 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. N OMA 5G (645025) 20.0 kV to NO5 AUX9 (645125) 4.2 kV Two Winding #1 b.3. S1211 5 (646211) 161.0 kV to N OMA 5G (645025) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_267 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_268 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_269 | Single Phase Fault with Stuck Breaker on S1214 5 161.00 (646214) 161 kV Bus a. Apply Fault at the S1214 5 161.00 (646214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1214 5 (646214) 161.0 kV to 70&BLUFF 5 (650169) 161.0 kV Transmission Circuit #1 b.3. S1214 5 (646214) 161.0 kV to S914A 8 (647014) 69.0 kV to S1214T19 (648214) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_270 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_271 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_272 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_273 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_274 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_275 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_276 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_277 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_278 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_279 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_280 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_281 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_282 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.3. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.4. S1217 5 (646217) 161.0 kV to S917 8 (647917) 69.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_283 | Single Phase Fault with Stuck Breaker on S1220 5 161.00 (646220) 161 kV Bus a. Apply Fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_284 | Single Phase Fault with Stuck Breaker on S1220 5 161.00 (646220) 161 kV Bus a. Apply Fault at the S1220 5 161.00 (646220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1220 5 (646220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_285 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_286 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_287 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_288 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_289 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_290 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_291 | Single Phase Fault with Stuck Breaker on S1222 5 161.00 (646222) 161 kV Bus a. Apply Fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_292 | Single Phase Fault with Stuck Breaker on S1222 5 161.00 (646222) 161 kV Bus a. Apply Fault at the S1222 5 161.00 (646222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_293 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_294 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_295 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_296 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_297 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_298 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1291 5 (646291) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_299 | Single Phase Fault with Stuck Breaker on S1227 5 161.00 (646227) 161 kV Bus a. Apply Fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_300 | Single Phase Fault with Stuck Breaker on S1227 5 161.00 (646227) 161 kV Bus a. Apply Fault at the S1227 5 161.00 (646227) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_301 | Single Phase Fault with Stuck Breaker on S1229 5 161.00 (646229) 161 kV Bus a. Apply Fault at the S1229 5 161.00 (646229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_302 | Single Phase Fault with Stuck Breaker on S1229 5 161.00 (646229) 161 kV Bus a. Apply Fault at the S1229 5 161.00 (646229) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 b.2. S1222 5 (646222) 161.0 kV to S1229 5 (646229) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_303 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_304 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_305 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_306 | Single Phase Fault with Stuck Breaker on S1231 5 161.00 (646231) 161 kV Bus a. Apply Fault at the S1231 5 161.00 (646231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1227 5 (646227) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S1231 5 (646231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_307 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_308 | Single Phase Fault with Stuck Breaker on S1232 5 161.00 (646232) 161 kV Bus a. Apply Fault at the S1232 5 161.00 (646232) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1232 5 (646232) 161.0 kV Transmission Circuit #1 b.2. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_309 | Single Phase Fault with Stuck Breaker on S1233 5 161.00 (646233) 161 kV Bus a. Apply Fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_310 | Single Phase Fault with Stuck Breaker on S1233 5 161.00 (646233) 161 kV Bus a. Apply Fault at the S1233 5 161.00 (646233) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1233 5 (646233) 161.0 kV to S1234 5 (646234) 161.0 kV Transmission Circuit #1 b.2. S1233 5 (646233) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_311 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_312 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_313 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.3. S1235 5 (646235) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_314 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.3. S1235 5 (646235) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_315 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_316 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1234 5 (646234) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_317 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_318 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_319 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_320 | Single Phase Fault with Stuck Breaker on S1235 5 161.00 (646235) 161 kV Bus a. Apply Fault at the S1235 5 161.00 (646235) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1231 5 (646231) 161.0 kV to S1235 5 (646235) 161.0 kV Transmission Circuit #1 b.2. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_321 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_322 | Single Phase Fault with Stuck Breaker on S1236 5 161.00 (646236) 161 kV Bus a. Apply Fault at the S1236 5 161.00 (646236) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1236 5 (646236) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_323 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_324 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_325 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_326 | Single Phase Fault with Stuck Breaker on S1237 5 161.00 (646237) 161 kV Bus a. Apply Fault at the S1237 5 161.00 (646237) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1237 5 (646237) 161.0 kV Transmission Circuit #1 b.2. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.3. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_327 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_328 | Single Phase Fault with Stuck Breaker on S1345 5 161.00 (646345) 161 kV Bus a. Apply Fault at the S1345 5 161.00 (646345) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.2. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_329 | Single Phase Fault with Stuck Breaker on S1249 5 161.00 (646249) 161 kV Bus a. Apply Fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_330 | Single Phase Fault with Stuck Breaker on S1249 5 161.00 (646249) 161 kV Bus a. Apply Fault at the S1249 5 161.00 (646249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_331 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_332 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_333 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_334 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_335 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_336 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_337 | Single Phase Fault with Stuck Breaker on S1297 5 161.00 (646297) 161 kV Bus a. Apply Fault at the S1297 5 161.00 (646297) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_338 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_339 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.3. S1251 5 (646251) 161.0 kV to S1297 5 (646297) 161.0 kV Transmission Circuit #1 b.4. S1297 9 (649297) 13.8 kV to S1297 5 (646297) 161.0 kV Two Winding #1 b.5. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_340 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_341 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.3. S1250 5 (646250) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_342 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_343 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_344 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 b.5. S1211 5 (646211) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_345 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_346 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_347 | Single Phase Fault with Stuck Breaker on S1250 5 161.00 (646250) 161 kV Bus a. Apply Fault at the S1250 5 161.00 (646250) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 b.2. S1250 5 (646250) 161.0 kV to S950 8 (647950) 69.0 kV to S1250T19 (648250) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_348 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_349 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_350 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_351 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_352 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_353 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S1305 5 (646305) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_354 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S1366 5 (646366) 161.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_355 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S1366 5 (646366) 161.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_356 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.3. S6866 8 (647866) 69.0 kV to S1366 5 (646366) 161.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_357 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_358 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_359 | Single Phase Fault with Stuck Breaker on S1341 5 161.00 (646341) 161 kV Bus a. Apply Fault at the S1341 5 161.00 (646341) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1341 5 (646341) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T49 (648351) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_360 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_361 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_362 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S1251 5 (646251) 161.0 kV to S3451T39 (648251) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_363 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_364 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_365 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_366 | Single Phase Fault with Stuck Breaker on S1305 5 161.00 (646305) 161 kV Bus a. Apply Fault at the S1305 5 161.00 (646305) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1298 5 (646298) 161.0 kV to S1305 5 (646305) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.3. S1305 5 (646305) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_367 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_368 | Single Phase Fault with Stuck Breaker on S1226 5 161.00 (646226) 161 kV Bus a. Apply Fault at the S1226 5 161.00 (646226) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_369 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_370 | Single Phase Fault with Stuck Breaker on S1298 5 161.00 (646298) 161 kV Bus a. Apply Fault at the S1298 5 161.00 (646298) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1251 5 (646251) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #1 b.2. S1226 5 (646226) 161.0 kV to S1298 5 (646298) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_371 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_372 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_373 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_374 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_375 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_376 | Single Phase Fault with Stuck Breaker on S1253 5 161.00 (646253) 161 kV Bus a. Apply Fault at the S1253 5 161.00 (646253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1235 5 (646235) 161.0 kV to S1253 5 (646253) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.3. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.4. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_377 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_378 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_379 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_380 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_381 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_382 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_383 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_384 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_385 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_386 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_387 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_388 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_389 | Single Phase Fault with Stuck Breaker on S1256 5 161.00 (646256) 161 kV Bus a. Apply Fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_390 | Single Phase Fault with Stuck Breaker on S1256 5 161.00 (646256) 161 kV Bus a. Apply Fault at the S1256 5 161.00 (646256) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1249 5 (646249) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1256 5 (646256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_391 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_392 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_393 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_394 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_395 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_396 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.3. S1278 5 (646278) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_397 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_398 | Single Phase Fault with Stuck Breaker on S1278 5 161.00 (646278) 161 kV Bus a. Apply Fault at the S1278 5 161.00 (646278) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1232 5 (646232) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 b.2. S1259 5 (646259) 161.0 kV to S1278 5 (646278) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_399 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_400 | Single Phase Fault with Stuck Breaker on S1280 5 161.00 (646280) 161 kV Bus a. Apply Fault at the S1280 5 161.00 (646280) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. HUMBOLT5 (640234) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.3. S1263 5 (646263) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_401 | Single Phase Fault with Stuck Breaker on S1286 5 161.00 (646286) 161 kV Bus a. Apply Fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_402 | Single Phase Fault with Stuck Breaker on S1286 5 161.00 (646286) 161 kV Bus a. Apply Fault at the S1286 5 161.00 (646286) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1201 5 (646201) 161.0 kV to S1286 5 (646286) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_403 | Single Phase Fault with Stuck Breaker on S1287 5 161.00 (646287) 161 kV Bus a. Apply Fault at the S1287 5 161.00 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_404 | Single Phase Fault with Stuck Breaker on S1287 5 161.00 (646287) 161 kV Bus a. Apply Fault at the S1287 5 161.00 (646287) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1214 5 (646214) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_405 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_406 | Single Phase Fault with Stuck Breaker on S1299 5 161.00 (646299) 161 kV Bus a. Apply Fault at the S1299 5 161.00 (646299) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 b.2. S1286 5 (646286) 161.0 kV to S1299 5 (646299) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_407 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_408 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_409 | Single Phase Fault with Stuck Breaker on TEKAMAH5 161.00 (640377) 161 kV Bus a. Apply Fault at the TEKAMAH5 161.00 (640377) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TEKAMAH5 (640377) 161.0 kV to S1226 5 (646226) 161.0 kV Transmission Circuit #1 b.2. TEKAMAH5 (640377) 161.0 kV to G17-105TAP (762069) 161.0 kV Transmission Circuit #1 b.3. TEKAMAH5 (640377) 161.0 kV to TEKAMAH7 (640378) 115.0 kV to TEKAMAH T1 9 (643151) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_410 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_411 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_412 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_413 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_414 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_415 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_416 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_417 | Single Phase Fault with Stuck Breaker on S1244 5 161.00 (646244) 161 kV Bus a. Apply Fault at the S1244 5 161.00 (646244) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_418 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_419 | Single Phase Fault with Stuck Breaker on S1252 5 161.00 (646252) 161 kV Bus a. Apply Fault at the S1252 5 161.00 (646252) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1226 5 (646226) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.2. S1236 5 (646236) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 b.3. S1252 5 (646252) 161.0 kV to S1345 5 (646345) 161.0 kV Transmission Circuit #1 b.4. S1252 5 (646252) 161.0 kV to S1347 5 (646347) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_420 | Single Phase Fault with Stuck Breaker on S1367 5 161.00 (646367) 161 kV Bus a. Apply Fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_421 | Single Phase Fault with Stuck Breaker on S1367 5 161.00 (646367) 161 kV Bus a. Apply Fault at the S1367 5 161.00 (646367) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1237 5 (646237) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 b.2. S1253 5 (646253) 161.0 kV to S1367 5 (646367) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_422 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_423 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to S960 8 (647960) 69.0 kV to S1260T29 (648260) 7.6 kV Three Winding #1 b.8. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_424 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_425 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.2. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.5. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.6. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_426 | Single Phase Fault with Stuck Breaker on S1255 5 161.00 (646255) 161 kV Bus a. Apply Fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_427 | Single Phase Fault with Stuck Breaker on S1255 5 161.00 (646255) 161 kV Bus a. Apply Fault at the S1255 5 161.00 (646255) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_428 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_429 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_430 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_431 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_432 | Single Phase Fault with Stuck Breaker on S1259 5 161.00 (646259) 161 kV Bus a. Apply Fault at the S1259 5 161.00 (646259) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1259 5 (646259) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_433 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.2. S1281 5 (646281) 161.0 kV to S1287 5 (646287) 161.0 kV Transmission Circuit #1 b.3. S1281 5 (646281) 161.0 kV to S1361 5 (646361) 161.0 kV Transmission Circuit #1 b.4. S1281 5 (646281) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 b.5. S1260 5 (646260) 161.0 kV to Load # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_434 | Single Phase Fault with Stuck Breaker on S1201 5 161.00 (646201) 161 kV Bus a. Apply Fault at the S1201 5 161.00 (646201) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S901 8 (647901) 69.0 kV Transmission Circuit #1 b.2. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.3. S901 8 (647901) 69.0 kV to GEN-2017-198 (760872) 69.0 kV Transmission Circuit #1 b.4. S901 8 (647901) 69.0 kV to JONES 1G (645051) 13.8 kV Two Winding #1 b.5. S901 8 (647901) 69.0 kV to JONES 2G (645052) 13.8 kV Two Winding #1 b.6. S901 8 (647901) 69.0 kV to S1201 5 (646201) 161.0 kV to S1201T19 (648201) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_435 | Single Phase Fault with Stuck Breaker on S902 8 69.000 (647902) 69 kV Bus a. Apply Fault at the S902 8 69.000 (647902) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.2. S902 8 (647902) 69.0 kV to S983 8 (647983) 69.0 kV Transmission Circuit #1 b.3. S902 8 (647902) 69.0 kV to S984 8 (647984) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_436 | Single Phase Fault with Stuck Breaker on S985 8 69.000 (647985) 69 kV Bus a. Apply Fault at the S985 8 69.000 (647985) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.2. S904 8 (647904) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.3. PLTSMTH8 (640320) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 b.4. S900 8 (647900) 69.0 kV to S985 8 (647985) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_437 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_438 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.2. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.3. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.4. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.5. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_439 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.2. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_440 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.2. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.4. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.5. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.6. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.7. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_441 | Single Phase Fault with Stuck Breaker on S907 8 69.000 (647907) 69 kV Bus a. Apply Fault at the S907 8 69.000 (647907) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_442 | Single Phase Fault with Stuck Breaker on S909 8 69.000 (647909) 69 kV Bus a. Apply Fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S1209 5 (646209) 161.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 b.6. S902 8 (647902) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_443 | Single Phase Fault with Stuck Breaker on S1209 5 161.00 (646209) 161 kV Bus a. Apply Fault at the S1209 5 161.00 (646209) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.3. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 b.4. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.5. S909 8 (647909) 69.0 kV to S1209 5 (646209) 161.0 kV to S1209T19 (648209) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_444 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.2. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S1210 5 (646210) 161.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_445 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.3. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.4. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.5. S910 8 (647910) 69.0 kV to S1210 5 (646210) 161.0 kV to S1210T79 (648210) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_446 | Single Phase Fault with Stuck Breaker on N OMA 1G 13.800 (645021) 13.80000019 kV Bus a. Apply Fault at the N OMA 1G 13.800 (645021) 13.80000019 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S911 8 (647911) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 b.3. S911 8 (647911) 69.0 kV to N OMA 1G (645021) 13.8 kV Two Winding #1 b.4. S911 8 (647911) 69.0 kV to S911 HS9 (645126) 13.8 kV Two Winding #1 b.5. S911 8 (647911) 69.0 kV to S1211 5 (646211) 161.0 kV to S1211T19 (648211) 13.8 kV Three Winding #1 b.8. N OMA 1G (645021) 13.8 kV to NO1 AUX9 (645121) 2.4 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_447 | Single Phase Fault with Stuck Breaker on S912 8 69.000 (647912) 69 kV Bus a. Apply Fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S901 8 (647901) 69.0 kV to S912 8 (647912) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_448 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.3. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_449 | Single Phase Fault with Stuck Breaker on S916 8 69.000 (647916) 69 kV Bus a. Apply Fault at the S916 8 69.000 (647916) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S916 8 (647916) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_450 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S916 8 (647916) 69.0 kV to S917 8 (647917) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S917 8 (647917) 69.0 kV to S1217 5 (646217) 161.0 kV to S1217T19 (648217) 13.8 kV Three Winding #1 b.4. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.5. S1216 5 (646216) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.6. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_451 | Single Phase Fault with Stuck Breaker on S918 8 69.000 (647918) 69 kV Bus a. Apply Fault at the S918 8 69.000 (647918) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 b.3. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_452 | Single Phase Fault with Stuck Breaker on S919 8 69.000 (647919) 69 kV Bus a. Apply Fault at the S919 8 69.000 (647919) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S907 8 (647907) 69.0 kV to S919 8 (647919) 69.0 kV Transmission Circuit #1 b.2. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.3. S919 8 (647919) 69.0 kV to S950 8 (647950) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_453 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S921 8 (647921) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.3. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 b.4. S921 8 (647921) 69.0 kV to S1221 5 (646221) 161.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_454 | Single Phase Fault with Stuck Breaker on S923 8 69.000 (647923) 69 kV Bus a. Apply Fault at the S923 8 69.000 (647923) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.2. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 b.3. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_455 | Single Phase Fault with Stuck Breaker on S912 8 69.000 (647912) 69 kV Bus a. Apply Fault at the S912 8 69.000 (647912) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_456 | Single Phase Fault with Stuck Breaker on JCT205 8 69.000 (647105) 69 kV Bus a. Apply Fault at the JCT205 8 69.000 (647105) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAX MIT8 (647106) 69.0 kV to S923 8 (647923) 69.0 kV Two Winding #1 b.2. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.3. S912 8 (647912) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 b.4. JCT205 8 (647105) 69.0 kV to PAX MIT8 (647106) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_457 | Single Phase Fault with Stuck Breaker on S924 8 69.000 (647924) 69 kV Bus a. Apply Fault at the S924 8 69.000 (647924) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.2. S912 8 (647912) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_458 | Single Phase Fault with Stuck Breaker on S928 8 69.000 (647928) 69 kV Bus a. Apply Fault at the S928 8 69.000 (647928) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.2. S928 8 (647928) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_459 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_460 | Single Phase Fault with Stuck Breaker on S930 8 69.000 (647930) 69 kV Bus a. Apply Fault at the S930 8 69.000 (647930) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S919 8 (647919) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 b.2. S918 8 (647918) 69.0 kV to S930 8 (647930) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_461 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_462 | Single Phase Fault with Stuck Breaker on S939 8 69.000 (647939) 69 kV Bus a. Apply Fault at the S939 8 69.000 (647939) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S930 8 (647930) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. MUD LNG8 (647104) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_463 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. 6815TP38 (647016) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.8. SAC623 8 (647107) 69.0 kV to SAC SO 8 (647109) 69.0 kV Transmission Circuit #1 b.9. 6815TP38 (647016) 69.0 kV to S6815T3 8 (647815) 69.0 kV Transmission Circuit #1 b.10. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_464 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_465 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_466 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1258 5 (646258) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.3. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.4. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.5. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_467 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S906 N 8 (647006) 69.0 kV to S1206T29 (648306) 13.8 kV Three Winding #1 b.4. S906 N 8 (647006) 69.0 kV to SARPY 1G (645031) 13.8 kV Two Winding #1 b.5. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.6. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 b.7. S906 N 8 (647006) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.8. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.9. S906 N 8 (647006) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_468 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to SARPY 2G (645032) 13.8 kV Two Winding #1 b.2. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 b.3. 6815TP38 (647016) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.4. S904 8 (647904) 69.0 kV to S906 S 8 (647906) 69.0 kV Transmission Circuit #1 b.5. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.6. S1206 5 (646206) 161.0 kV to S906 S 8 (647906) 69.0 kV to S1206T19 (648206) 13.8 kV Three Winding #1 b.9. S906 S 8 (647906) 69.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_469 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_470 | Single Phase Fault with Stuck Breaker on S938 8 69.000 (647938) 69 kV Bus a. Apply Fault at the S938 8 69.000 (647938) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S938 8 (647938) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 b.3. S6874 8 (647874) 69.0 kV to S995 8 (647995) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_471 | Single Phase Fault with Stuck Breaker on S6815T1&T2 869.000 (647015) 69 kV Bus a. Apply Fault at the S6815T1&T2 869.000 (647015) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1244 5 (646244) 161.0 kV to S1366 5 (646366) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 b.5. SAC623 8 (647107) 69.0 kV to S6866 8 (647866) 69.0 kV Transmission Circuit #1 b.6. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.7. 6815TP98 (647017) 69.0 kV to SAC629 8 (647108) 69.0 kV Transmission Circuit #1 b.8. SAC629 8 (647108) 69.0 kV to SAC NO 8 (647110) 69.0 kV Transmission Circuit #1 b.9. SAC629 8 (647108) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 b.10. S906 N 8 (647006) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 b.11. S6815T1&T2 8 (647015) 69.0 kV to 6815TP98 (647017) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_472 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.10. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.11. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.12. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.13. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_473 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.7. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.10. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 b.13. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.14. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.15. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.16. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z2 b.17. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.18. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_474 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_475 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_476 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.5. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.6. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.7. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_477 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.3. LETCHER4 (652606) 230.0 kV to LETCHER7 (652609) 115.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_478 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_479 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_480 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-GR-BE3 (659422) 345.0 kV Transmission Circuit #z b.2. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.3. GROTON__-BE3 (659160) 345.0 kV to GR.LS-LO-BE3 (659423) 345.0 kV Transmission Circuit #z b.4. GR.LS-LO-BE3 (659423) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.5. LO.KVA2_-BE9 (659202) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_481 | Single Phase Fault with Stuck Breaker on SD.LS-KS-MB3345.00 (659425) 345 kV Bus a. Apply Fault at the SD.LS-KS-MB3345.00 (659425) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. SIDNEY__-MB3 (659133) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #z b.3. SIDNEY__-MB3 (659133) 345.0 kV to STEGALL_-MB3 (659135) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_482 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_483 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to LELAND_2-BEG (659111) 20.0 kV Two Winding #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.3. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.5. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_484 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_485 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #2 b.2. LO.KU1A_-BE9 (659201) 13.8 kV to LELAND_O-BE3 (659105) 345.0 kV to LELAND_O-BE4 (659106) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_486 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_487 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_488 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESSINGTON1W (662101) 0.6 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_489 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SD.PW1__-BE9 (659327) 34.5 kV to WESSINGTON1W (659296) 0.6 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_490 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to SD.PW1__-BE4 (659295) 230.0 kV Transmission Circuit #1 b.4. WESSINGTON 4 (652607) 230.0 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.5. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.6. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_491 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESSINGTON1W (662101) 0.6 kV to WESSINGTON 9 (662100) 34.5 kV Two Winding #1 b.2. HANLON 4 (652513) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.3. WESSINGTON 4 (652607) 230.0 kV to STORLA__-BE4 (659122) 230.0 kV Transmission Circuit #1 b.4. STORLA__-BE4 (659122) 230.0 kV to STORLA__-BE7 (659123) 115.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_492 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_493 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_494 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_495 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_496 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_497 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_498 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE2-3G (652556) 13.8 kV Two Winding #1 b.2. OAHE 9 (652589) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.3. OAHE 29 (652598) 13.8 kV to OAHE 4 (652519) 230.0 kV to OAHE 7 (652520) 115.0 kV Three Winding #1 b.4. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.6. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.7. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.8. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_499 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_500 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_501 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_502 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_503 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_504 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_505 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_506 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_507 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.3. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.4. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.7. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_508 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_509 | Single Phase Fault with Stuck Breaker on UTICAJC4 230.00 (652526) 230 kV Bus a. Apply Fault at the UTICAJC4 230.00 (652526) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.2. UTICAJC4 (652526) 230.0 kV to UTICAJC7 (652626) 115.0 kV to UTICAJC9 (652627) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_510 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY4 (652565) 230.0 kV to RASMUSN-ER4 (655484) 230.0 kV Transmission Circuit #1 b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 b.5. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC29 (652305) 13.8 kV Three Winding #1 b.8. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC39 (652308) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_511 | Single Phase Fault with Stuck Breaker on SIOUXCY4 230.00 (652565) 230 kV Bus a. Apply Fault at the SIOUXCY4 230.00 (652565) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWIN CH4 (640386) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. SIOUXCY4 (652565) 230.0 kV to DENISON4 (652567) 230.0 kV Transmission Circuit #1 b.4. SIOUXCY4 (652565) 230.0 kV to SIOUXCY5 (652566) 161.0 kV to SIOUXC49 (652310) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_512 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.3. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_513 | Single Phase Fault with Stuck Breaker on SIOUXFL4 230.00 (652523) 230 kV Bus a. Apply Fault at the SIOUXFL4 230.00 (652523) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK4 (602004) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.2. VFODNES4 (652398) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.3. HANLON 4 (652513) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 b.4. SIOUXFL4 (652523) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.5. SIOUXFL4 (652523) 230.0 kV to PAHOJA__-BE4 (659311) 230.0 kV Transmission Circuit #1 b.6. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF19 (652232) 13.2 kV Three Winding #1 b.7. SIOUXFL4 (652523) 230.0 kV to SIOUXFL7 (652524) 115.0 kV to SIOUXF29 (652233) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_514 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HURON 4 (652514) 230.0 kV to HURON 7 (652515) 115.0 kV to HURON419 (652281) 13.3 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_515 | Single Phase Fault with Stuck Breaker on HURON 4 230.00 (652514) 230 kV Bus a. Apply Fault at the HURON 4 230.00 (652514) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 b.2. HURON 4 (652514) 230.0 kV to WATERTN4 (652530) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_516 | Single Phase Fault with Stuck Breaker on PHILIP_T-BE4230.00 (659188) 230 kV Bus a. Apply Fault at the PHILIP_T-BE4230.00 (659188) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.2. PHILIP__-BE4 (659192) 230.0 kV to PHILIP 7 (652487) 115.0 kV to PHILIP__-BE9 (659193) 13.2 kV Three Winding #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_517 | Single Phase Fault with Stuck Breaker on NUNDRWD4 230.00 (652484) 230 kV Bus a. Apply Fault at the NUNDRWD4 230.00 (652484) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NUNDRWD4 (652484) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #z b.2. MAURINE4 (652497) 230.0 kV to NUNDRWD-LNX3 (652884) 230.0 kV Transmission Circuit #1 b.3. GEN-2017-014 (588590) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. NUNDRWD4 (652484) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.5. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.6. PHILIP_T-BE4 (659188) 230.0 kV to PHILIP__-BE4 (659192) 230.0 kV Transmission Circuit #1 b.7. NUNDRWD4 (652484) 230.0 kV to NUNDRWD7 (652485) 115.0 kV to NUNDRWD9 (652267) 13.8 kV Three Winding #1 b.10. NUNDRWD4 (652484) 230.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_518 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_519 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_520 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_521 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_522 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_523 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_524 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to FTTHOMP8 (652276) 69.0 kV to FTTHOMP9 (652277) 13.8 kV Three Winding #1 b.4. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_525 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_526 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_527 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_528 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_529 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_530 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_531 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.2. FTTHOMP4 (652507) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_532 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 b.2. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_533 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND14 (652540) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_534 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_535 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_536 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_537 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_538 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_539 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_540 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_541 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_542 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_543 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_544 | Single Phase Fault with Stuck Breaker on MCCOOL 3 345.00 (640271) 345 kV Bus a. Apply Fault at the MCCOOL 3 345.00 (640271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_545 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_546 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_547 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISL19 (653314) 13.8 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV Three Winding #1 b.2. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_548 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_549 | Single Phase Fault with Stuck Breaker on ANTELOPE-BE3345.00 (659101) 345 kV Bus a. Apply Fault at the ANTELOPE-BE3345.00 (659101) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE-BE3 (659101) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #1 b.2. ANTELOPE-BE3 (659101) 345.0 kV to DGC_____-BE3 (659212) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_550 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_551 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_552 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_553 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to BIGBND24 (652541) 230.0 kV Transmission Circuit #2 b.2. FTTHOMP4 (652507) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_554 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_555 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_556 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE4-5G (652557) 13.8 kV Two Winding #1 b.2. OAHE 4 (652519) 230.0 kV to SULLYBT-ER4 (655487) 230.0 kV Transmission Circuit #1 b.3. OAHE 4 (652519) 230.0 kV to PHILIP_T-BE4 (659188) 230.0 kV Transmission Circuit #1 b.4. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_557 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to OAHE6-7G (652558) 13.8 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #3 b.3. FTTHOMP4 (652507) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_558 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_559 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_560 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_561 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_562 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_563 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_564 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_565 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_566 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_567 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_568 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_569 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_570 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_571 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_572 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_573 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_574 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_575 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_576 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_577 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_578 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_579 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_580 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_581 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_582 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_583 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_584 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_585 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_586 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_587 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_588 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_589 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_590 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_591 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_592 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_593 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_594 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. BONESTL7 (652475) 115.0 kV to GREGORY7 (652478) 115.0 kV Transmission Circuit #1 b.3. BONESTL7 (652475) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_595 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to FTRDL12G (652546) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_596 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. ARMOUR 7 (652501) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. ARMOUR 7 (652501) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.4. ARMOUR 9 (652246) 34.5 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.5. ARMOUR 8 (652249) 69.0 kV to ARMOUR 7 (652501) 115.0 kV Two Winding #1 b.6. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_597 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. SPENCER7 (640349) 115.0 kV to FTRANDL7 (652510) 115.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_598 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL7 (652510) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.3. TYNDALL7 (652525) 115.0 kV to WHTSWAN-ER7 (655490) 115.0 kV Transmission Circuit #1 b.4. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_599 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_600 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_601 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_602 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_603 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_604 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_605 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_606 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_607 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_608 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_609 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_610 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_611 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL78G (652549) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_612 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_613 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. MEADOWGROVE4 (640540) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_614 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL56G (652548) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_615 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to LAKPLAT-ER4 (655475) 230.0 kV Transmission Circuit #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_616 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRDL34G (652547) 13.8 kV Two Winding #1 b.3. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_617 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #1 b.2. FTRANDL4 (652509) 230.0 kV to FTRANDL7 (652510) 115.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_618 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_619 | Single Phase Fault with Stuck Breaker on J748POI 345.00 (87487) 345 kV Bus a. Apply Fault at the J748POI 345.00 (87487) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J748POI (87487) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. J748POI (87487) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_620 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_621 | Single Phase Fault with Stuck Breaker on SMOKYHL6 230.00 (530592) 230 kV Bus a. Apply Fault at the SMOKYHL6 230.00 (530592) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMOKYHL6 (530592) 230.0 kV to SUMMIT 6 (532873) 230.0 kV Transmission Circuit #1 b.2. SMOKYHL6 (530592) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_622 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_623 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_624 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_625 | Single Phase Fault with Stuck Breaker on G16-050-TAP 345.00 (560082) 345 kV Bus a. Apply Fault at the G16-050-TAP 345.00 (560082) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-050-TAP (560082) 345.0 kV to POSTROCK7 (530583) 345.0 kV Transmission Circuit #1 b.2. G16-050-TAP (560082) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_626 | Single Phase Fault with Stuck Breaker on GEN-2016-075345.00 (579450) 345 kV Bus a. Apply Fault at the GEN-2016-075345.00 (579450) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-075 (579450) 345.0 kV to G16-075XFMR1 (579457) 34.5 kV Two Winding #1 b.2. GEN-2016-075 (579450) 345.0 kV to GRPR2 3 (648520) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_627 | Single Phase Fault with Stuck Breaker on GEN-2015-023345.00 (584650) 345 kV Bus a. Apply Fault at the GEN-2015-023345.00 (584650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-023 (584650) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-023 (584650) 345.0 kV to G15-023XFMR2 (584654) 34.5 kV to G15-023-TER2 (584659) 13.9 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_628 | Single Phase Fault with Stuck Breaker on GEN-2015-088345.00 (585241) 345 kV Bus a. Apply Fault at the GEN-2015-088345.00 (585241) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-088 (585241) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-088 (585241) 345.0 kV to G15-088-XF-2 (585249) 34.5 kV to G15-088-TR-1 (906007) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_629 | Single Phase Fault with Stuck Breaker on GEN-2016-021345.00 (587150) 345 kV Bus a. Apply Fault at the GEN-2016-021345.00 (587150) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-021 (587150) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-021 (587150) 345.0 kV to G16-021-XF-2 (587151) 34.5 kV to G16-021-TER2 (587158) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_630 | Single Phase Fault with Stuck Breaker on GEN-2016-074345.00 (587680) 345 kV Bus a. Apply Fault at the GEN-2016-074345.00 (587680) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-074 (587680) 345.0 kV to G16-074XFMR1 (587681) 34.5 kV Two Winding #1 b.2. GEN-2016-074 (587680) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_631 | Single Phase Fault with Stuck Breaker on G16-094-TAP 230.00 (587764) 230 kV Bus a. Apply Fault at the G16-094-TAP 230.00 (587764) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-094-TAP (587764) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 b.2. G16-094-TAP (587764) 230.0 kV to OAHE 4 (652519) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_632 | Single Phase Fault with Stuck Breaker on G17-094-TAP 230.00 (589324) 230 kV Bus a. Apply Fault at the G17-094-TAP 230.00 (589324) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-094-TAP (589324) 230.0 kV to HURON 4 (652514) 230.0 kV Transmission Circuit #1 b.2. G17-094-TAP (589324) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_633 | Single Phase Fault with Stuck Breaker on SUB701 5 161.00 (635003) 161 kV Bus a. Apply Fault at the SUB701 5 161.00 (635003) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #1 b.2. SUB701 8 (635004) 69.0 kV to SUB701 5 (635003) 161.0 kV Two Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_634 | Single Phase Fault with Stuck Breaker on SUB704 8 69.000 (635007) 69 kV Bus a. Apply Fault at the SUB704 8 69.000 (635007) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB704 8 (635007) 69.0 kV to SUB701 8 (635004) 69.0 kV Transmission Circuit #1 b.2. SUB704 8 (635007) 69.0 kV to SUB705 8 (635008) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_635 | Single Phase Fault with Stuck Breaker on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply Fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ATCHSN 3 (635017) 345.0 kV to WESTBORO 3 (635018) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_636 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 3 (635200) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. RAUN 3 (635200) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_637 | Single Phase Fault with Stuck Breaker on RAUN 3 345.00 (635200) 345 kV Bus a. Apply Fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV Two Winding #2 b.2. RAUN 5 (635201) 161.0 kV to RAUN 3 (635200) 345.0 kV to RAUN1XT9 (635205) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_638 | Single Phase Fault with Stuck Breaker on IDA CO 3 345.00 (635206) 345 kV Bus a. Apply Fault at the IDA CO 3 345.00 (635206) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IDA CO 3 (635206) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. IDA CO 3 (635206) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_639 | Single Phase Fault with Stuck Breaker on GARD AVE 3 345.00 (635219) 345 kV Bus a. Apply Fault at the GARD AVE 3 345.00 (635219) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GARD AVE 3 (635219) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. GARD AVE 3 (635219) 345.0 kV to LEHIGH 3 (636010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_640 | Single Phase Fault with Stuck Breaker on REMSEN 3 345.00 (635398) 345 kV Bus a. Apply Fault at the REMSEN 3 345.00 (635398) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REMSEN 3 (635398) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. REMSEN 3 (635398) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_641 | Single Phase Fault with Stuck Breaker on CHEROKEE 3 345.00 (635399) 345 kV Bus a. Apply Fault at the CHEROKEE 3 345.00 (635399) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHEROKEE 3 (635399) 345.0 kV to HIGHLND 3 (635400) 345.0 kV Transmission Circuit #1 b.2. CHEROKEE 3 (635399) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_642 | Single Phase Fault with Stuck Breaker on BATTLCR7 115.00 (640072) 115 kV Bus a. Apply Fault at the BATTLCR7 115.00 (640072) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BATTLCR7 (640072) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. BATTLCR7 (640072) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_643 | Single Phase Fault with Stuck Breaker on CO.LINE7 115.00 (640115) 115 kV Bus a. Apply Fault at the CO.LINE7 115.00 (640115) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CO.LINE7 (640115) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. CO.LINE7 (640115) 115.0 kV to BATTLCR7 (640072) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_644 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS3 (640226) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 b.2. HOSKINS3 (640226) 345.0 kV to HOSKINS7 (640228) 115.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_645 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_646 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations; GEN-2018-056 | Build a 50 MVAR STATCOM at GR PRAIRIE 345 kV | Tuned (if applicable) GEN-2018-056 developer model that provides VAR support
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_647 | Single Phase Fault with Stuck Breaker on ANTELOPE 3345.00 (640520) 345 kV Bus a. Apply Fault at the ANTELOPE 3345.00 (640520) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 3 (640520) 345.0 kV to ANTELOPE 7 (640521) 115.0 kV to ANTELOPE 9 (640524) 13.8 kV Three Winding #1 b.2. ANTELOPE 3 (640520) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_648 | Single Phase Fault with Stuck Breaker on ANTELOPE 7115.00 (640521) 115 kV Bus a. Apply Fault at the ANTELOPE 7115.00 (640521) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTELOPE 7 (640521) 115.0 kV to CO.LINE7 (640115) 115.0 kV Transmission Circuit #1 b.2. ANTELOPE 7 (640521) 115.0 kV to CREITON7 (640149) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_649 | Single Phase Fault with Stuck Breaker on TOBIAS 3345.00 (640525) 345 kV Bus a. Apply Fault at the TOBIAS 3345.00 (640525) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOBIAS 3 (640525) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. TOBIAS 3 (640525) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_650 | Single Phase Fault with Stuck Breaker on WAKEFIELD 4230.00 (640560) 230 kV Bus a. Apply Fault at the WAKEFIELD 4230.00 (640560) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAKEFIELD 4 (640560) 230.0 kV to TWIN CH4 (640386) 230.0 kV Transmission Circuit #1 b.2. WAKEFIELD 4 (640560) 230.0 kV to HOSKINS4 (640227) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_651 | Single Phase Fault with Stuck Breaker on TURTLE.CRK 3345.00 (640588) 345 kV Bus a. Apply Fault at the TURTLE.CRK 3345.00 (640588) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TURTLE.CRK 3 (640588) 345.0 kV to GEN-2016-021 (587150) 345.0 kV Transmission Circuit #1 b.2. TURTLE.CRK 3 (640588) 345.0 kV to PLUMBCR.W 3 (643271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_652 | Single Phase Fault with Stuck Breaker on S3451 3 345.00 (645451) 345 kV Bus a. Apply Fault at the S3451 3 345.00 (645451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3451 3 (645451) 345.0 kV to G18-043-TAP (762779) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_653 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_654 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_655 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 b.2. S1209 5 (646209) 161.0 kV to S3459 3 (645459) 345.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_656 | Single Phase Fault with Stuck Breaker on S1211 5 161.00 (646211) 161 kV Bus a. Apply Fault at the S1211 5 161.00 (646211) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #2 b.2. S1211 5 (646211) 161.0 kV to S1250 5 (646250) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_657 | Single Phase Fault with Stuck Breaker on S1260 5 161.00 (646260) 161 kV Bus a. Apply Fault at the S1260 5 161.00 (646260) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1260 5 (646260) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.2. S1260 5 (646260) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_658 | Single Phase Fault with Stuck Breaker on S1362 5 161.00 (646362) 161 kV Bus a. Apply Fault at the S1362 5 161.00 (646362) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1362 5 (646362) 161.0 kV to S1260 5 (646260) 161.0 kV Transmission Circuit #1 b.2. S1362 5 (646362) 161.0 kV to S1363 5 (646363) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_659 | Single Phase Fault with Stuck Breaker on S908 8 69.000 (647908) 69 kV Bus a. Apply Fault at the S908 8 69.000 (647908) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S908 8 (647908) 69.0 kV to S910 8 (647910) 69.0 kV Transmission Circuit #1 b.2. S908 8 (647908) 69.0 kV to S913 8 (647913) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_660 | Single Phase Fault with Stuck Breaker on FTTHOMP4 230.00 (652507) 230 kV Bus a. Apply Fault at the FTTHOMP4 230.00 (652507) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP4 (652507) 230.0 kV to LETCHER4 (652606) 230.0 kV Transmission Circuit #1 b.2. FTTHOMP4 (652507) 230.0 kV to FTRANDL4 (652509) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_661 | Single Phase Fault with Stuck Breaker on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply Fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_662 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX5345.00 (652808) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX5345.00 (652808) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM1-LNX5 (652808) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #1 b.2. FTTHOM1-LNX5 (652808) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_663 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations; GEN-2018-056 | Build a 50 MVAR STATCOM at GR PRAIRIE 345 kV | Tuned (if applicable) GEN-2018-056 developer model that provides VAR support
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_664 | Single Phase Fault with Stuck Breaker on CHAPELLE-BE3345.00 (659130) 345 kV Bus a. Apply Fault at the CHAPELLE-BE3345.00 (659130) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHAPELLE-BE3 (659130) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #z b.2. CHAPELLE-BE3 (659130) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_665 | Single Phase Fault with Stuck Breaker on GEN-2017-181345.00 (761292) 345 kV Bus a. Apply Fault at the GEN-2017-181345.00 (761292) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-181 (761292) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-181 (761292) 345.0 kV to GEN-2017-182 (761313) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_666 | Single Phase Fault with Stuck Breaker on G18-043-TAP 345.00 (762779) 345 kV Bus a. Apply Fault at the G18-043-TAP 345.00 (762779) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-043-TAP (762779) 345.0 kV to S3451 3 (645451) 345.0 kV Transmission Circuit #1 b.2. G18-043-TAP (762779) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_667 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. KNOLL N 6 (530558) 230.0 kV to KNOLL S 6 (530720) 230.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_668 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_669 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. HEIZER 6 (530680) 230.0 kV to HEIZER 3 (530601) 115.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_670 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND3 (539678) 115.0 kV to GRTBEND6 (539679) 230.0 kV to GRTBNDTT (539920) 13.8 kV Three Winding #1 b.2. GRTBEND3 (539678) 115.0 kV to HEIZER 3 (530601) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_671 | Single Phase Fault with Stuck Breaker on ST JOE 7 345.00 (541199) 345 kV Bus a. Apply Fault at the ST JOE 7 345.00 (541199) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ST JOE 7 (541199) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_672 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN7 (541400) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. EASTOWN7 (541400) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_673 | Single Phase Fault with Stuck Breaker on SPLT RK3 345.00 (601006) 345 kV Bus a. Apply Fault at the SPLT RK3 345.00 (601006) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK3 (601006) 345.0 kV to WHITE 3 (652537) 345.0 kV Transmission Circuit #1 b.2. SPLT RK3 (601006) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_674 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_675 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E7 (640127) 115.0 kV to E.COL. 4 (640126) 230.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 b.2. COLMB.E7 (640127) 115.0 kV to COLMB.E3 (640125) 345.0 kV to COLMB.T9 (640129) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_676 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KELLY 7 (640134) 115.0 kV to COLMBUS7 (640136) 115.0 kV Transmission Circuit #1 b.2. KELLY 7 (640134) 115.0 kV to COLMBUS4 (640133) 230.0 kV to COLMBS19 (640135) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_677 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_678 | Single Phase Fault with Stuck Breaker on GENTLMN4 230.00 (640184) 230 kV Bus a. Apply Fault at the GENTLMN4 230.00 (640184) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #1 b.2. GENTLMN4 (640184) 230.0 kV to N.PLATT4 (640286) 230.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_679 | Single Phase Fault with Stuck Breaker on GR ISLD4 230.00 (640200) 230 kV Bus a. Apply Fault at the GR ISLD4 230.00 (640200) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.2. GR ISLD4 (640200) 230.0 kV to GR ISLD7 (640201) 115.0 kV to G.I.T219 (640203) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_680 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS4 (640227) 230.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKINS T2 9 (643082) 13.8 kV Three Winding #1 b.2. HOSKINS4 (640227) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_681 | Single Phase Fault with Stuck Breaker on HOSKINS3 345.00 (640226) 345 kV Bus a. Apply Fault at the HOSKINS3 345.00 (640226) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOSKINS7 (640228) 115.0 kV to HOSKINS3 (640226) 345.0 kV to HOSKNS19 (640231) 13.8 kV Three Winding #1 b.2. HOSKINS7 (640228) 115.0 kV to NORFOLK7 (640298) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_682 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON7 (640253) 115.0 kV to KEYSTON3 (640252) 345.0 kV to KEYSTON9 (640254) 13.8 kV Three Winding #1 b.2. KEYSTON7 (640253) 115.0 kV to OGALALANPPD7 (640304) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_683 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELDON7 (640278) 115.0 kV to MOORE 3 (640277) 345.0 kV to MOORE 9 (640280) 13.8 kV Three Winding #1 b.2. SHELDON7 (640278) 115.0 kV to SW7&BENNET7 (650246) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_684 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE7 (640313) 115.0 kV to HASTING7 (640215) 115.0 kV Transmission Circuit #1 b.2. PAULINE7 (640313) 115.0 kV to PAULINE3 (640312) 345.0 kV to PAULINE9 (640315) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_685 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK4 (640343) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. SHELCRK4 (640343) 230.0 kV to SHELCRK3 (640342) 345.0 kV to SHELLCRK T19 (643136) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_686 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD7 (640381) 115.0 kV to THEDFRD3 (640500) 345.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD7 (640381) 115.0 kV to CALAMS 7 (640096) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_687 | Single Phase Fault with Stuck Breaker on COOPER 5 161.00 (640140) 161 kV Bus a. Apply Fault at the COOPER 5 161.00 (640140) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 8 (640446) 69.0 kV to COOPER_ESST8 (640141) 69.0 kV Transmission Circuit #1 b.2. COOPER 8 (640446) 69.0 kV to COOPER 5 (640140) 161.0 kV to COOPER T6 9 (643173) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_688 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_689 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S3456 3 (645456) 345.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.2. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_690 | Single Phase Fault with Stuck Breaker on S1210 5 161.00 (646210) 161 kV Bus a. Apply Fault at the S1210 5 161.00 (646210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1210 5 (646210) 161.0 kV to S1217 5 (646217) 161.0 kV Transmission Circuit #1 b.2. S1210 5 (646210) 161.0 kV to S1222 5 (646222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_691 | Single Phase Fault with Stuck Breaker on S1217 5 161.00 (646217) 161 kV Bus a. Apply Fault at the S1217 5 161.00 (646217) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1217 5 (646217) 161.0 kV to S1227 5 (646227) 161.0 kV Transmission Circuit #1 b.2. S1217 5 (646217) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_692 | Single Phase Fault with Stuck Breaker on S1221 5 161.00 (646221) 161 kV Bus a. Apply Fault at the S1221 5 161.00 (646221) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S1221 5 (646221) 161.0 kV to S921 8 (647921) 69.0 kV to S1221T99 (648221) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_693 | Single Phase Fault with Stuck Breaker on S1366 5 161.00 (646366) 161 kV Bus a. Apply Fault at the S1366 5 161.00 (646366) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1366 5 (646366) 161.0 kV to S1244 5 (646244) 161.0 kV Transmission Circuit #1 b.2. S1366 5 (646366) 161.0 kV to S6866 8 (647866) 69.0 kV to S1366T29 (648266) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_694 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.2. NW68HOLDRG7 (650214) 115.0 kV to SW27&F 7 (650216) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_695 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_696 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_697 | Single Phase Fault with Stuck Breaker on OAHE 4 230.00 (652519) 230 kV Bus a. Apply Fault at the OAHE 4 230.00 (652519) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 4 (652519) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #3 b.2. OAHE 4 (652519) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #4 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_698 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY3 (652564) 345.0 kV to SIOUXCY-LNX3 (652864) 345.0 kV Transmission Circuit #z b.2. SIOUXCY3 (652564) 345.0 kV to SIOUXCY2 (652552) 230.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_699 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LETCHER4 (652606) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #1 b.2. LETCHER4 (652606) 230.0 kV to SIOUXFL4 (652523) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_700 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_701 | Single Phase Fault with Stuck Breaker on LELAND_O-BE3345.00 (659105) 345 kV Bus a. Apply Fault at the LELAND_O-BE3345.00 (659105) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE3 (659105) 345.0 kV to FINSTAD345 (659060) 345.0 kV Transmission Circuit #1 b.2. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_702 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STORLA__-BE4 (659122) 230.0 kV to WESSINGTON 4 (652607) 230.0 kV Transmission Circuit #1 b.2. STORLA__-BE4 (659122) 230.0 kV to HANLON 4 (652513) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_703 | Single Phase Fault with Stuck Breaker on KNOLL N 6 230.00 (530558) 230 kV Bus a. Apply Fault at the KNOLL N 6 230.00 (530558) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOLL 3 (530561) 115.0 kV to KNOLL N 6 (530558) 230.0 kV to KNLL1 1 (530629) 11.5 kV Three Winding #1 b.2. KNOLL 3 (530561) 115.0 kV to SALINE 3 (530551) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_704 | Single Phase Fault with Stuck Breaker on CHETOLAH3 115.00 (530695) 115 kV Bus a. Apply Fault at the CHETOLAH3 115.00 (530695) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHETOLAH3 (530695) 115.0 kV to S HAYS 3 (530553) 115.0 kV Transmission Circuit #1 b.2. CHETOLAH3 (530695) 115.0 kV to VINETAP3 (530693) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_705 | Single Phase Fault with Stuck Breaker on NEAL N 5 161.00 (635203) 161 kV Bus a. Apply Fault at the NEAL N 5 161.00 (635203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEAL N 8 (635204) 69.0 kV to NEAL N 5 (635203) 161.0 kV Two Winding #1 b.2. NEAL N 8 (635204) 69.0 kV to SBRIDGE T8 (635227) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_706 | Single Phase Fault with Stuck Breaker on LEHIGH 3 345.00 (636010) 345 kV Bus a. Apply Fault at the LEHIGH 3 345.00 (636010) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEHIGH 3 (636010) 345.0 kV to BVR CRK 3 (636003) 345.0 kV Transmission Circuit #1 b.2. LEHIGH 3 (636010) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_707 | Single Phase Fault with Stuck Breaker on CREITON7 115.00 (640149) 115 kV Bus a. Apply Fault at the CREITON7 115.00 (640149) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CREITON7 (640149) 115.0 kV to BLMFLD 7 (640084) 115.0 kV Transmission Circuit #1 b.2. CREITON7 (640149) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_708 | Single Phase Fault with Stuck Breaker on NELIGH 7 115.00 (640293) 115 kV Bus a. Apply Fault at the NELIGH 7 115.00 (640293) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NELIGH 7 (640293) 115.0 kV to CLRWATR7 (640113) 115.0 kV Transmission Circuit #1 b.2. NELIGH 7 (640293) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_709 | Single Phase Fault with Stuck Breaker on NORFOLK7 115.00 (640298) 115 kV Bus a. Apply Fault at the NORFOLK7 115.00 (640298) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NORFOLK7 (640298) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 b.2. NORFOLK7 (640298) 115.0 kV to NORFK.N7 (640296) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_710 | Single Phase Fault with Stuck Breaker on S909 8 69.000 (647909) 69 kV Bus a. Apply Fault at the S909 8 69.000 (647909) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S909 8 (647909) 69.0 kV to S939 8 (647939) 69.0 kV Transmission Circuit #1 b.2. S909 8 (647909) 69.0 kV to S937 8 (647937) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_711 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_712 | Single Phase Fault with Stuck Breaker on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply Fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z b.2. GRPRAR2-LNX3 (652833) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_713 | Single Phase Fault with Stuck Breaker on SIOUXCY-LNX3345.00 (652864) 345 kV Bus a. Apply Fault at the SIOUXCY-LNX3345.00 (652864) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY-LNX3 (652864) 345.0 kV to SIOUXCY3 (652564) 345.0 kV Transmission Circuit #z b.2. SIOUXCY-LNX3 (652864) 345.0 kV to SPLT RK3 (601006) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_714 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z b.2. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_715 | Single Phase Fault with Stuck Breaker on LO.LS-GR-BE3345.00 (659422) 345 kV Bus a. Apply Fault at the LO.LS-GR-BE3345.00 (659422) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-GR-BE3 (659422) 345.0 kV to G18-008-TAP (762544) 345.0 kV Transmission Circuit #1 b.2. LO.LS-GR-BE3 (659422) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_716 | Single Phase Fault with Stuck Breaker on LO.LS-FT-BE3345.00 (659424) 345 kV Bus a. Apply Fault at the LO.LS-FT-BE3345.00 (659424) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.2. LO.LS-FT-BE3 (659424) 345.0 kV to LELAND_O-BE3 (659105) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_717 | Single Phase Fault with Stuck Breaker on CC.LS-LO-BE3345.00 (659428) 345 kV Bus a. Apply Fault at the CC.LS-LO-BE3345.00 (659428) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CC.LS-LO-BE3 (659428) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #1 b.2. CC.LS-LO-BE3 (659428) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_718 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_719 | Single Phase Fault with Stuck Breaker on GEN-2017-115345.00 (760746) 345 kV Bus a. Apply Fault at the GEN-2017-115345.00 (760746) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-115 (760746) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-115 (760746) 345.0 kV to G17-115XFMR1 (760747) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_720 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. AXTELL 3 (640065) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_721 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_722 | Single Phase Fault with Stuck Breaker on SUB703 8 69.000 (635006) 69 kV Bus a. Apply Fault at the SUB703 8 69.000 (635006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB703 8 (635006) 69.0 kV to SUB701 8 (635004) 69.0 kV Transmission Circuit #1 b.2. SUB703 8 (635006) 69.0 kV to SUB706 8 (635009) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_723 | Single Phase Fault with Stuck Breaker on HONEYCK8 69.000 (635080) 69 kV Bus a. Apply Fault at the HONEYCK8 69.000 (635080) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HONEYCK8 (635080) 69.0 kV to SUB701 8 (635004) 69.0 kV Transmission Circuit #1 b.2. HONEYCK8 (635080) 69.0 kV to MOVALLY8 (635081) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_724 | Single Phase Fault with Stuck Breaker on SUB705 8 69.000 (635008) 69 kV Bus a. Apply Fault at the SUB705 8 69.000 (635008) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB705 8 (635008) 69.0 kV to CBLUFFS8 (635002) 69.0 kV Transmission Circuit #1 b.2. SUB705 8 (635008) 69.0 kV to SUB704 8 (635007) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_725 | Single Phase Fault with Stuck Breaker on WESTBORO 3 345.00 (635018) 345 kV Bus a. Apply Fault at the WESTBORO 3 345.00 (635018) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WESTBORO 3 (635018) 345.0 kV to ORIENT 3 (635570) 345.0 kV Transmission Circuit #1 b.2. WESTBORO 3 (635018) 345.0 kV to ATCHSN 3 (635017) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_726 | Single Phase Fault with Stuck Breaker on J412 POI 3 345.00 (635252) 345 kV Bus a. Apply Fault at the J412 POI 3 345.00 (635252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. J412 POI 3 (635252) 345.0 kV to IDA CO 3 (635206) 345.0 kV Transmission Circuit #1 b.2. J412 POI 3 (635252) 345.0 kV to RAUN 3 (635200) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_727 | Single Phase Fault with Stuck Breaker on G17-105TAP 161.00 (762069) 161 kV Bus a. Apply Fault at the G17-105TAP 161.00 (762069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-105TAP (762069) 161.0 kV to RAUN 5 (635201) 161.0 kV Transmission Circuit #1 b.2. G17-105TAP (762069) 161.0 kV to TEKAMAH5 (640377) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_728 | Single Phase Fault with Stuck Breaker on RICHLAND W 345.00 (637024) 345 kV Bus a. Apply Fault at the RICHLAND W 345.00 (637024) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RICHLAND W (637024) 345.0 kV to GARD AVE 3 (635219) 345.0 kV Transmission Circuit #1 b.2. RICHLAND W (637024) 345.0 kV to J535 COL (637023) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_729 | Single Phase Fault with Stuck Breaker on HIGHLND 3 345.00 (635400) 345 kV Bus a. Apply Fault at the HIGHLND 3 345.00 (635400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HIGHLND 3 (635400) 345.0 kV to CHEROKEE 3 (635399) 345.0 kV Transmission Circuit #1 b.2. HIGHLND 3 (635400) 345.0 kV to OBRIEN 3 (635368) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_730 | Single Phase Fault with Stuck Breaker on GEN-2017-144345.00 (760767) 345 kV Bus a. Apply Fault at the GEN-2017-144345.00 (760767) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-144 (760767) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-144 (760767) 345.0 kV to G17-144XFMR2 (760771) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_731 | Single Phase Fault with Stuck Breaker on G18-056-TAP 345.00 (762916) 345 kV Bus a. Apply Fault at the G18-056-TAP 345.00 (762916) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. None to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. None to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_732 | Single Phase Fault with Stuck Breaker on UPSTREAM.W 7115.00 (643254) 115 kV Bus a. Apply Fault at the UPSTREAM.W 7115.00 (643254) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. UPSTREAM.W 7 (643254) 115.0 kV to ANTELOPE 7 (640521) 115.0 kV Transmission Circuit #1 b.2. UPSTREAM.W 7 (643254) 115.0 kV to UPSTRM.COL19 (643255) 34.5 kV to UPSTRM.T1 9 (643257) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_733 | Single Phase Fault with Stuck Breaker on RTLSNAKE.W 4230.00 (640561) 230 kV Bus a. Apply Fault at the RTLSNAKE.W 4230.00 (640561) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RTLSNAKE.W 4 (640561) 230.0 kV to WAKEFIELD 4 (640560) 230.0 kV Transmission Circuit #1 b.2. RTLSNAKE.W 4 (640561) 230.0 kV to RTLSNAK.C1 9 (643263) 34.5 kV to RTLSNAK.T1 9 (643264) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_734 | Single Phase Fault with Stuck Breaker on PLUMBCR.W 3345.00 (643271) 345 kV Bus a. Apply Fault at the PLUMBCR.W 3345.00 (643271) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PLUMBCR.W 3 (643271) 345.0 kV to TURTLE.CRK 3 (640588) 345.0 kV Transmission Circuit #1 b.2. PLUMBCR.W 3 (643271) 345.0 kV to PLUMBCR.COL9 (643272) 34.5 kV to PLUMBCR T1 9 (643273) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_735 | Single Phase Fault with Stuck Breaker on GEN-2017-201345.00 (760788) 345 kV Bus a. Apply Fault at the GEN-2017-201345.00 (760788) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-201 (760788) 345.0 kV to G17-201XFMR1 (760789) 34.5 kV Two Winding #1 b.2. GEN-2017-201 (760788) 345.0 kV to SHOLES.W 3 (640589) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_736 | Single Phase Fault with Stuck Breaker on S1347 5 161.00 (646347) 161 kV Bus a. Apply Fault at the S1347 5 161.00 (646347) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1347 5 (646347) 161.0 kV to S1209 5 (646209) 161.0 kV Transmission Circuit #1 b.2. S1347 5 (646347) 161.0 kV to S1252 5 (646252) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_737 | Single Phase Fault with Stuck Breaker on S1363 5 161.00 (646363) 161 kV Bus a. Apply Fault at the S1363 5 161.00 (646363) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1363 5 (646363) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #1 b.2. S1363 5 (646363) 161.0 kV to S1362 5 (646362) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_738 | Single Phase Fault with Stuck Breaker on S913 8 69.000 (647913) 69 kV Bus a. Apply Fault at the S913 8 69.000 (647913) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S913 8 (647913) 69.0 kV to S911 8 (647911) 69.0 kV Transmission Circuit #1 b.2. S913 8 (647913) 69.0 kV to S908 8 (647908) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_739 | Single Phase Fault with Stuck Breaker on FTRANDL4 230.00 (652509) 230 kV Bus a. Apply Fault at the FTRANDL4 230.00 (652509) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTRANDL4 (652509) 230.0 kV to FTTHOMP4 (652507) 230.0 kV Transmission Circuit #2 b.2. FTRANDL4 (652509) 230.0 kV to UTICAJC4 (652526) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_740 | Single Phase Fault with Stuck Breaker on GEN-2017-182345.00 (761313) 345 kV Bus a. Apply Fault at the GEN-2017-182345.00 (761313) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-182 (761313) 345.0 kV to G17-182XFMR1 (761314) 34.5 kV Two Winding #1 b.2. GEN-2017-182 (761313) 345.0 kV to GEN-2017-181 (761292) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_741 | Single Phase Fault with Stuck Breaker on S HAYS6 230.00 (530582) 230 kV Bus a. Apply Fault at the S HAYS6 230.00 (530582) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS 3 (530553) 115.0 kV to S HAYS6 (530582) 230.0 kV to SHYS1 1 (530632) 12.5 kV Three Winding #1 b.2. S HAYS 3 (530553) 115.0 kV to CHETOLAH3 (530695) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_742 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_743 | Single Phase Fault with Stuck Breaker on HEIZER 6 230.00 (530680) 230 kV Bus a. Apply Fault at the HEIZER 6 230.00 (530680) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 3 (530601) 115.0 kV to HEIZER 6 (530680) 230.0 kV to HZRT1 1 (530626) 12.5 kV Three Winding #1 b.2. HEIZER 3 (530601) 115.0 kV to GRTBEND3 (539678) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_744 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRTBEND6 (539679) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to CIRCLE 6 (532871) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_745 | Single Phase Fault with Stuck Breaker on ST JOE 5 161.00 (541253) 161 kV Bus a. Apply Fault at the ST JOE 5 161.00 (541253) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 5 (541253) 161.0 kV to COOK 5 (541257) 161.0 kV Transmission Circuit #1 b.2. ST JOE 5 (541253) 161.0 kV to WOODBIN5 (541258) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_746 | Single Phase Fault with Stuck Breaker on EASTOWN7 345.00 (541400) 345 kV Bus a. Apply Fault at the EASTOWN7 345.00 (541400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EASTOWN5 (541401) 161.0 kV to EASTOWN7 (541400) 345.0 kV to EASTOWN1 (541402) 13.8 kV Three Winding #11 b.2. EASTOWN5 (541401) 161.0 kV to IND PRK5 (541256) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_747 | Single Phase Fault with Stuck Breaker on SPLT RK7 115.00 (603016) 115 kV Bus a. Apply Fault at the SPLT RK7 115.00 (603016) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPLT RK7 (603016) 115.0 kV to FALLS 7 (603225) 115.0 kV Transmission Circuit #1 b.2. SPLT RK7 (603016) 115.0 kV to SPLITRK CAP7 (603228) 115.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_748 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_749 | Single Phase Fault with Stuck Breaker on BELDEN 7 115.00 (640080) 115 kV Bus a. Apply Fault at the BELDEN 7 115.00 (640080) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BELDEN 7 (640080) 115.0 kV to HARTGTN7 (640212) 115.0 kV Transmission Circuit #1 b.2. BELDEN 7 (640080) 115.0 kV to HOSKINS7 (640228) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_750 | Single Phase Fault with Stuck Breaker on E.COL. 4 230.00 (640126) 230 kV Bus a. Apply Fault at the E.COL. 4 230.00 (640126) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. E.COL. 4 (640126) 230.0 kV to COLMBUS4 (640133) 230.0 kV Transmission Circuit #1 b.2. E.COL. 4 (640126) 230.0 kV to COLMB.E7 (640127) 115.0 kV to COLMB.ESTT39 (643036) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_751 | Single Phase Fault with Stuck Breaker on COLMB.E3 345.00 (640125) 345 kV Bus a. Apply Fault at the COLMB.E3 345.00 (640125) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMB.E3 (640125) 345.0 kV to SHELCRK3 (640342) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_752 | Single Phase Fault with Stuck Breaker on COLMBUS4 230.00 (640133) 230 kV Bus a. Apply Fault at the COLMBUS4 230.00 (640133) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COLMBUS4 (640133) 230.0 kV to MEADOWGROVE4 (640540) 230.0 kV Transmission Circuit #1 b.2. COLMBUS4 (640133) 230.0 kV to E.COL. 4 (640126) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_753 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_754 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations | Update Grand Prairie dynamic controller
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_755 | Single Phase Fault with Stuck Breaker on KEYSTON3 345.00 (640252) 345 kV Bus a. Apply Fault at the KEYSTON3 345.00 (640252) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KEYSTON3 (640252) 345.0 kV to SD.LS-KS-MB3 (659425) 345.0 kV Transmission Circuit #1 b.2. KEYSTON3 (640252) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_756 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_757 | Single Phase Fault with Stuck Breaker on PAULINE3 345.00 (640312) 345 kV Bus a. Apply Fault at the PAULINE3 345.00 (640312) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PAULINE3 (640312) 345.0 kV to TOBIAS 3 (640525) 345.0 kV Transmission Circuit #1 b.2. PAULINE3 (640312) 345.0 kV to AXTELL 3 (640065) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_758 | Single Phase Fault with Stuck Breaker on SHELCRK3 345.00 (640342) 345 kV Bus a. Apply Fault at the SHELCRK3 345.00 (640342) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHELCRK3 (640342) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 b.2. SHELCRK3 (640342) 345.0 kV to HOSKINS3 (640226) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_759 | Single Phase Fault with Stuck Breaker on HOLDREG7 115.00 (640224) 115 kV Bus a. Apply Fault at the HOLDREG7 115.00 (640224) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLDREG7 (640224) 115.0 kV to JOHN.2 7 (640242) 115.0 kV Transmission Circuit #1 b.2. HOLDREG7 (640224) 115.0 kV to AXTELL 7 (640066) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_760 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MONOLITH 3 (640590) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 3 (640590) 345.0 kV to MONOLITH 7 (640591) 115.0 kV to MONOLITHT1 9 (640596) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_761 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1254 5 (646254) 161.0 kV to S3454 3 (645454) 345.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.2. S1254 5 (646254) 161.0 kV to S1249 5 (646249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_762 | Single Phase Fault with Stuck Breaker on S906 S 8 69.000 (647906) 69 kV Bus a. Apply Fault at the S906 S 8 69.000 (647906) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 S 8 (647906) 69.0 kV to S904 8 (647904) 69.0 kV Transmission Circuit #1 b.2. S906 S 8 (647906) 69.0 kV to S924 8 (647924) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_763 | Single Phase Fault with Stuck Breaker on S906 N 8 69.000 (647006) 69 kV Bus a. Apply Fault at the S906 N 8 69.000 (647006) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S906 N 8 (647006) 69.0 kV to S938 8 (647938) 69.0 kV Transmission Circuit #1 b.2. S906 N 8 (647006) 69.0 kV to S928 8 (647928) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_764 | Single Phase Fault with Stuck Breaker on S910 8 69.000 (647910) 69 kV Bus a. Apply Fault at the S910 8 69.000 (647910) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S910 8 (647910) 69.0 kV to S908 8 (647908) 69.0 kV Transmission Circuit #1 b.2. S910 8 (647910) 69.0 kV to S923 8 (647923) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_765 | Single Phase Fault with Stuck Breaker on S917 8 69.000 (647917) 69 kV Bus a. Apply Fault at the S917 8 69.000 (647917) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S917 8 (647917) 69.0 kV to S916 8 (647916) 69.0 kV Transmission Circuit #1 b.2. S917 8 (647917) 69.0 kV to S918 8 (647918) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_766 | Single Phase Fault with Stuck Breaker on S921 8 69.000 (647921) 69 kV Bus a. Apply Fault at the S921 8 69.000 (647921) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S921 8 (647921) 69.0 kV to S940 8 (647940) 69.0 kV Transmission Circuit #1 b.2. S921 8 (647921) 69.0 kV to S942 8 (647942) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_767 | Single Phase Fault with Stuck Breaker on S6866 8 69.000 (647866) 69 kV Bus a. Apply Fault at the S6866 8 69.000 (647866) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S6866 8 (647866) 69.0 kV to SAC623 8 (647107) 69.0 kV Transmission Circuit #1 b.2. S6866 8 (647866) 69.0 kV to S994 8 (647994) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_768 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to NW68HOLDRG7 (650214) 115.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.2. NW68HOLDRG3 (650114) 345.0 kV to COLMB.E3 (640125) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_769 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_770 | Single Phase Fault with Stuck Breaker on OAHE 7 115.00 (652520) 115 kV Bus a. Apply Fault at the OAHE 7 115.00 (652520) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAHE 7 (652520) 115.0 kV to ASH TAP (652600) 115.0 kV Transmission Circuit #1 b.2. OAHE 7 (652520) 115.0 kV to IRVSIMM7 (658174) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_771 | Single Phase Fault with Stuck Breaker on SIOUXCY3 345.00 (652564) 345 kV Bus a. Apply Fault at the SIOUXCY3 345.00 (652564) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIOUXCY2 (652552) 230.0 kV to SIOUXCY4 (652565) 230.0 kV Transmission Circuit #z1 b.2. SIOUXCY2 (652552) 230.0 kV to SIOUXCY3 (652564) 345.0 kV to SIOUXC19 (652304) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_772 | Single Phase Fault with Stuck Breaker on LETCHER4 230.00 (652606) 230 kV Bus a. Apply Fault at the LETCHER4 230.00 (652606) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LETCHER7 (652609) 115.0 kV to LETCHER4 (652606) 230.0 kV to LETCHER9 (652608) 13.2 kV Three Winding #1 b.2. LETCHER7 (652609) 115.0 kV to MITCHELL 7 (660004) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_773 | Single Phase Fault with Stuck Breaker on LELAND_O-BE4230.00 (659106) 230 kV Bus a. Apply Fault at the LELAND_O-BE4230.00 (659106) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LELAND_O-BE4 (659106) 230.0 kV to WASHBRN4 (652456) 230.0 kV Transmission Circuit #1 b.2. LELAND_O-BE4 (659106) 230.0 kV to GRE-STANTON4 (615901) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Transfer | GROUP2_FAULT_774 | Single Phase Fault with Stuck Breaker on STORLA__-BE4230.00 (659122) 230 kV Bus a. Apply Fault at the STORLA__-BE4230.00 (659122) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STORLA__-BE7 (659123) 115.0 kV to MTVERN 7 (652518) 115.0 kV Transmission Circuit #1 b.2. STORLA__-BE7 (659123) 115.0 kV to STORLA__-BE4 (659122) 230.0 kV to ST.KV1A_-BE9 (659119) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_1 | 3 Phase fault on CJ 366 5 161.00 (547477) 161 kV Bus a. Apply fault at the CJ 366 5 161.00 (547477) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASB349 5 (547476) 161.0 kV to CJ 366 5 (547477) 161.0 kV Transmission Circuit #1 b.2. CJ 366 5 (547477) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_2 | 3 Phase fault on OAK432 5 161.00 (547494) 161 kV Bus a. Apply fault at the OAK432 5 161.00 (547494) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATL109 5 (547466) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_3 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VINTAJC4 (510417) 138.0 kV to HOC404 4 (547486) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 b.4. HOC404A1 (547715) 12.5 kV to HOC404 5 (547487) 161.0 kV to HOC404 4 (547486) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_4 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_5 | 3 Phase fault on JAGGER 3 115.00 (531360) 115 kV Bus a. Apply fault at the JAGGER 3 115.00 (531360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELER 3 (531359) 115.0 kV to NESSCTY3 (531456) 115.0 kV Transmission Circuit #1 b.2. BEELER 3 (531359) 115.0 kV to LIBERTYT (531495) 115.0 kV Transmission Circuit #1 b.3. JAGGER 3 (531360) 115.0 kV to DIGHTON3 (531361) 115.0 kV Transmission Circuit #1 b.4. JAGGER 3 (531360) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 b.5. JAGGER 3 (531360) 115.0 kV to LIBERTYT (531495) 115.0 kV Transmission Circuit #1 b.6. MANNGT 3 (531362) 115.0 kV to MANNING3 (531363) 115.0 kV Transmission Circuit #1 b.7. MANNGT 3 (531362) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_6 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_7 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_8 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_9 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_10 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_11 | 3 Phase fault on CANEYRV7 345.00 (532780) 345 kV Bus a. Apply fault at the CANEYRV7 345.00 (532780) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANEYRV7 (532780) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_12 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_13 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_14 | 3 Phase fault on GEARY 7 345.00 (532767) 345 kV Bus a. Apply fault at the GEARY 7 345.00 (532767) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GEARY 7 (532767) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_15 | 3 Phase fault on JEC N 7 345.00 (532766) 345 kV Bus a. Apply fault at the JEC N 7 345.00 (532766) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. JEC N 7 (532766) 345.0 kV to MORRIS 7 (532770) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_16 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to LATHAMS7 (532800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_17 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_18 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_19 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_20 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_21 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_22 | 3 Phase fault on STRANGR7 345.00 (532772) 345 kV Bus a. Apply fault at the STRANGR7 345.00 (532772) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STRANGR7 (532772) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_23 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_24 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_25 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_26 | 3 Phase fault on WAVERLY7 345.00 (532799) 345 kV Bus a. Apply fault at the WAVERLY7 345.00 (532799) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAVERLY7 (532799) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_27 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WAVERLY7 (532799) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_28 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_29 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_30 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_31 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_32 | 3 Phase fault on TIOGA 4 138.00 (532996) 138 kV Bus a. Apply fault at the TIOGA 4 138.00 (532996) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TIOGA 4 (532996) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_33 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_34 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_35 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_36 | 3 Phase fault on ELPASO 4 138.00 (533039) 138 kV Bus a. Apply fault at the ELPASO 4 138.00 (533039) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELPASO 4 (533039) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_37 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_38 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_39 | 3 Phase fault on GILL 4 138.00 (533047) 138 kV Bus a. Apply fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_40 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to WACO S 4 (533071) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_41 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV to STEARMN4 (533068) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_42 | 3 Phase fault on SUMNER 4 138.00 (532984) 138 kV Bus a. Apply fault at the SUMNER 4 138.00 (532984) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUMNER 4 (532984) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_43 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_44 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_45 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_46 | 3 Phase fault on CITIES 3 115.00 (533414) 115 kV Bus a. Apply fault at the CITIES 3 115.00 (533414) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CITIES 3 (533414) 115.0 kV to DAVIS 3 (533415) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_47 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_48 | 3 Phase fault on EMCPHER3 115.00 (533417) 115 kV Bus a. Apply fault at the EMCPHER3 115.00 (533417) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMCPHER3 (533417) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_49 | 3 Phase fault on MANVILE3 115.00 (533426) 115 kV Bus a. Apply fault at the MANVILE3 115.00 (533426) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MANVILE3 (533426) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_50 | 3 Phase fault on REFINRY3 115.00 (533427) 115 kV Bus a. Apply fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_51 | 3 Phase fault on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_52 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_53 | 3 Phase fault on MEAD S 2 69.000 (533815) 69 kV Bus a. Apply fault at the MEAD S 2 69.000 (533815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_54 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_55 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_56 | 3 Phase fault on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_57 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_58 | 3 Phase fault on MOORE 3 345.00 (640277) 345 kV Bus a. Apply fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_59 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_60 | 3 Phase fault on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_61 | 3 Phase fault on DELWARE4 138.00 (510379) 138 kV Bus a. Apply fault at the DELWARE4 138.00 (510379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_62 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_63 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_64 | 3 Phase fault on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_65 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_66 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_67 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_68 | 3 Phase fault on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_69 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_70 | 3 Phase fault on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_71 | 3 Phase fault on DELWARE7 345.00 (510380) 345 kV Bus a. Apply fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_72 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_73 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_74 | 3 Phase fault on ONETA--7 345.00 (509807) 345 kV Bus a. Apply fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_75 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_76 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_77 | 3 Phase fault on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_78 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_79 | 3 Phase fault on 7OVERTON 345.00 (345408) 345 kV Bus a. Apply fault at the 7OVERTON 345.00 (345408) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7OVERTON (345408) 345.0 kV to 5OVERTON (345409) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_80 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_81 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_82 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to STHLND 3 (635016) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_83 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_84 | 3 Phase fault on ATCHSN 3 345.00 (635017) 345 kV Bus a. Apply fault at the ATCHSN 3 345.00 (635017) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_85 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_86 | 3 Phase fault on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CBLUFFS3 (635000) 345.0 kV to CBLUFFS5 (635001) 161.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_87 | 3 Phase fault on HARRIS 161.00 (541313) 161 kV Bus a. Apply fault at the HARRIS 161.00 (541313) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNWD 5 (541218) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_88 | 3 Phase fault on LEESUM 5 161.00 (541233) 161 kV Bus a. Apply fault at the LEESUM 5 161.00 (541233) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 b.2. GRNWD 5 (541218) 161.0 kV to LEESUM 5 (541233) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_89 | 3 Phase fault on STROTHR5 161.00 (541246) 161 kV Bus a. Apply fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PRALEE 5 (541206) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to STROTHR5 (541246) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_90 | 3 Phase fault on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_91 | 3 Phase fault on RICHMND5 161.00 (541236) 161 kV Bus a. Apply fault at the RICHMND5 161.00 (541236) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEX161 5 (541232) 161.0 kV to RICHMND5 (541236) 161.0 kV Transmission Circuit #1 b.2. RICHMND5 (541236) 161.0 kV to ORRICK 5 (541244) 161.0 kV Transmission Circuit #1 b.3. ORRICK 5 (541244) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_92 | 3 Phase fault on LKWOOD 5 161.00 (541238) 161 kV Bus a. Apply fault at the LKWOOD 5 161.00 (541238) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 b.2. BLSPW 5 (541237) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_93 | 3 Phase fault on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_94 | 3 Phase fault on WINJT N5 161.00 (543009) 161 kV Bus a. Apply fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEEDS 5 (542997) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.3. SWOPE N5 (543006) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_95 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_96 | 3 Phase fault on NAVY 5 161.00 (542989) 161 kV Bus a. Apply fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_97 | 3 Phase fault on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to BUCYRUS5 (543057) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to NLOUISB5 (543058) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_98 | 3 Phase fault on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to SHAWNEE5 (543041) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_99 | 3 Phase fault on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_100 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_101 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_102 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_103 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_104 | 3 Phase fault on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_105 | 3 Phase fault on RANDLPH5 161.00 (543027) 161 kV Bus a. Apply fault at the RANDLPH5 161.00 (543027) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_106 | 3 Phase fault on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_107 | 3 Phase fault on SIB REA1 345.00 (541414) 345 kV Bus a. Apply fault at the SIB REA1 345.00 (541414) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIB REA1 (541414) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_108 | 3 Phase fault on MC REAC3 345.00 (541413) 345 kV Bus a. Apply fault at the MC REAC3 345.00 (541413) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MC REAC3 (541413) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_109 | 3 Phase fault on MC REAC2 345.00 (541412) 345 kV Bus a. Apply fault at the MC REAC2 345.00 (541412) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. MC REAC1 (541411) 345.0 kV Switched Shunt Device # b.3. MC REAC2 (541412) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_110 | 3 Phase fault on CONWAY 138.00 (539009) 138 kV Bus a. Apply fault at the CONWAY 138.00 (539009) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to CONWAY (539009) 138.0 kV Transmission Circuit #1 b.2. CONWAY (539009) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 b.3. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_111 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_112 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_113 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_114 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_115 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_116 | 3 Phase fault on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_117 | 3 Phase fault on CORONAD3 115.00 (533394) 115 kV Bus a. Apply fault at the CORONAD3 115.00 (533394) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CORONAD3 (533394) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_118 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_119 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_120 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to DAKOTA_5 (543650) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_121 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to BELAIRE4 (532988) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_122 | 3 Phase fault on COMOTAR4 138.00 (533037) 138 kV Bus a. Apply fault at the COMOTAR4 138.00 (533037) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELAIRE4 (532988) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_123 | 3 Phase fault on INTERST4 138.00 (533051) 138 kV Bus a. Apply fault at the INTERST4 138.00 (533051) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_124 | 3 Phase fault on 43LORAN 115.00 (533440) 115 kV Bus a. Apply fault at the 43LORAN 115.00 (533440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 b.2. 3 VANBU3 (533435) 115.0 kV to MEADOW 3 (533441) 115.0 kV Transmission Circuit #1 b.3. 43LORAN (533440) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 b.4. MEADOW 3 (533441) 115.0 kV to TWR 33 3 (533455) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_125 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to SG9STMK2 (533874) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_126 | 3 Phase fault on DEARING4 138.00 (533002) 138 kV Bus a. Apply fault at the DEARING4 138.00 (533002) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 b.2. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.3. DEARING4 (533002) 138.0 kV to MONTGOM4 (533004) 138.0 kV Transmission Circuit #1 b.4. DEARING4 (533002) 138.0 kV to DEARING2 (533688) 69.0 kV to DEARING1 (533089) 13.2 kV Three Winding #1 b.5. DEARING1 (533089) 13.2 kV to DEARING2 (533688) 69.0 kV to DEARING4 (533002) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_127 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEARING4 (533002) 138.0 kV to LIBERTY4 (533003) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.3. LIBERTY4 (533003) 138.0 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 b.4. LIBERTY1 (533090) 13.2 kV to LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_128 | 3 Phase fault on NINMLTP4 138.00 (521128) 138 kV Bus a. Apply fault at the NINMLTP4 138.00 (521128) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 (520462) 138.0 kV to BEARCAT4 (520500) 138.0 kV Transmission Circuit #1 b.2. ASPEN 4 (520462) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. NINMILE4 (520492) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.4. BEARCAT4 (520500) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 b.5. MORWODS4 (521001) 138.0 kV to NINMLTP4 (521128) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_129 | 3 Phase fault on ROSEVLY4 138.00 (520436) 138 kV Bus a. Apply fault at the ROSEVLY4 138.00 (520436) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. NOELSW 4 (520430) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.3. ROSEVLY4 (520436) 138.0 kV to AVARD 4 (520601) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_130 | 3 Phase fault on CDRDLTP4 138.00 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 138.00 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 (520425) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.2. PIC4 (520425) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.3. CEDRDAL4 (520507) 138.0 kV to CDRDLTP4 (520848) 138.0 kV Transmission Circuit #1 b.4. CDRDLTP4 (520848) 138.0 kV to OKEENE 4 (521016) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_131 | 3 Phase fault on BYRONTP4 138.00 (520432) 138 kV Bus a. Apply fault at the BYRONTP4 138.00 (520432) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NOELSW 4 (520430) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.2. CHRKCTY4 (520431) 138.0 kV to SALTPLN4 (520437) 138.0 kV Transmission Circuit #1 b.3. CHRKCTY4 (520431) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.4. BYRONTP4 (520432) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.5. BYRONTP4 (520432) 138.0 kV to BYRON 4 (520477) 138.0 kV Transmission Circuit #1 b.6. BYRONTP4 (520432) 138.0 kV to DRIFTWD4 (521200) 138.0 kV Transmission Circuit #1 b.7. SANDYCR4 (520433) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 b.8. SANDYCR4 (520433) 138.0 kV to UNIONVL4 (520453) 138.0 kV Transmission Circuit #1 b.9. WAKTASW4 (520434) 138.0 kV to WAKTASB4 (520452) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_132 | 3 Phase fault on TONECE7 345.00 (512750) 345 kV Bus a. Apply fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_133 | 3 Phase fault on LACKMAN5 161.00 (543126) 161 kV Bus a. Apply fault at the LACKMAN5 161.00 (543126) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRGHL 5 (532914) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 b.2. STILWEL5 (542969) 161.0 kV to LACKMAN5 (543126) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_134 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_135 | 3 Phase fault on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_136 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_137 | 3 Phase fault on NWMAID5 161.00 (512757) 161 kV Bus a. Apply fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_138 | 3 Phase fault on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_139 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_140 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_141 | 3 Phase fault on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_142 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_143 | 3 Phase fault on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_144 | 3 Phase fault on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_145 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_146 | 3 Phase fault on KERR GR5 161.00 (512635) 161 kV Bus a. Apply fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_147 | 3 Phase fault on WMAIN ST5 161.00 (512742) 161 kV Bus a. Apply fault at the WMAIN ST5 161.00 (512742) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_148 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_149 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_150 | 3 Phase fault on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_151 | 3 Phase fault on LOCSTGVKM 5 161.00 (513050) 161 kV Bus a. Apply fault at the LOCSTGVKM 5 161.00 (513050) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_152 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_153 | 3 Phase fault on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_154 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_155 | 3 Phase fault on FARML 4 138.00 (512734) 138 kV Bus a. Apply fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY2 (512741) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_156 | 3 Phase fault on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_157 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_158 | 3 Phase fault on MAID 5 161.00 (512648) 161 kV Bus a. Apply fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_159 | 3 Phase fault on 5SPORTSMAN 161.00 (300741) 161 kV Bus a. Apply fault at the 5SPORTSMAN 161.00 (300741) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_160 | 3 Phase fault on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_161 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS_CAP5 (542948) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_162 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.3. SWOPE S5 (543007) 161.0 kV to WINJT S5 (543010) 161.0 kV Transmission Circuit #1 b.4. STHTOWN_CAP5 (542950) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_163 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.2. BARRY_CAP 5 (542944) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_164 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. MERRIAM_CAP5 (542947) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_165 | 3 Phase fault on BYPASJT2 69.000 (543084) 69 kV Bus a. Apply fault at the BYPASJT2 69.000 (543084) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYJT2 (543079) 69.0 kV to BYPASJT2 (543084) 69.0 kV Transmission Circuit #1 b.2. BYPASJT2 (543084) 69.0 kV to IND WTR2 (543086) 69.0 kV Transmission Circuit #1 b.3. BYPASJT2 (543084) 69.0 kV to LIBRTYS2 (543095) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_166 | 3 Phase fault on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.3. IND WTR2 (543086) 69.0 kV to CEMCITY2 (543090) 69.0 kV Transmission Circuit #1 b.4. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.5. TMP LAF2 (543103) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 b.6. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 b.7. MILCKJT2 (543110) 69.0 kV to LAFARGE2 (543111) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_167 | 3 Phase fault on LANG 7 345.00 (532769) 345 kV Bus a. Apply fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to LANG 7 (532769) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_168 | 3 Phase fault on TAYLOR 4 138.00 (533006) 138 kV Bus a. Apply fault at the TAYLOR 4 138.00 (533006) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 b.2. MONTGOM4 (533004) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_169 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_170 | 3 Phase fault on PARKCTY4 138.00 (533052) 138 kV Bus a. Apply fault at the PARKCTY4 138.00 (533052) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to PARKCTY4 (533052) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_171 | 3 Phase fault on TALLGRS4 138.00 (532993) 138 kV Bus a. Apply fault at the TALLGRS4 138.00 (532993) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_172 | 3 Phase fault on 45TH ST4 138.00 (533074) 138 kV Bus a. Apply fault at the 45TH ST4 138.00 (533074) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. EVANS S4 (533041) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_173 | 3 Phase fault on CENTENN4 138.00 (533034) 138 kV Bus a. Apply fault at the CENTENN4 138.00 (533034) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. CENTENN4 (533034) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_174 | 3 Phase fault on SCOFCTY4 138.00 (510378) 138 kV Bus a. Apply fault at the SCOFCTY4 138.00 (510378) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOFCTY4 (510378) 138.0 kV to SCOFFEYV4 (510420) 138.0 kV Transmission Circuit #1 b.2. SCOFCTY4 (510378) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.3. SCOFCTY4 (510378) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.4. NBVILLE4 (510386) 138.0 kV to BV-SE--4 (510391) 138.0 kV Transmission Circuit #1 b.5. NBVILLE4 (510386) 138.0 kV to COFFEYT4 (510422) 138.0 kV Transmission Circuit #1 b.6. COFFEYT4 (510422) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_175 | 3 Phase fault on 59TH ST4 138.00 (533029) 138 kV Bus a. Apply fault at the 59TH ST4 138.00 (533029) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 59TH ST4 (533029) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. 59TH ST4 (533029) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_176 | 3 Phase fault on LAKERDG4 138.00 (533053) 138 kV Bus a. Apply fault at the LAKERDG4 138.00 (533053) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS S4 (533041) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_177 | 3 Phase fault on BENTLEY4 138.00 (533015) 138 kV Bus a. Apply fault at the BENTLEY4 138.00 (533015) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. BENTLEY4 (533015) 138.0 kV to WWUPLNT4 (533016) 138.0 kV Transmission Circuit #1 b.3. BENTLEY4 (533015) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 b.4. EVANS N4 (533040) 138.0 kV to SG12COL4 (533065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_178 | 3 Phase fault on TV1MNDV4 138.00 (533008) 138 kV Bus a. Apply fault at the TV1MNDV4 138.00 (533008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. TV1MNDV4 (533008) 138.0 kV to NEOSHOS4 (533020) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_179 | 3 Phase fault on ANDOVER4 138.00 (533026) 138 kV Bus a. Apply fault at the ANDOVER4 138.00 (533026) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_180 | 3 Phase fault on ANTHONY4 138.00 (539001) 138 kV Bus a. Apply fault at the ANTHONY4 138.00 (539001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. ANTHONY4 (539001) 138.0 kV to BLF-CRK4 (539002) 138.0 kV Transmission Circuit #1 b.3. ANTHONY4 (539001) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_181 | 3 Phase fault on HUNTSVL3 115.00 (530618) 115 kV Bus a. Apply fault at the HUNTSVL3 115.00 (530618) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.2. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.3. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_182 | 3 Phase fault on MUND 3 115.00 (533282) 115 kV Bus a. Apply fault at the MUND 3 115.00 (533282) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. PENTAGN3 (533261) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_183 | 3 Phase fault on RENO 3 115.00 (533416) 115 kV Bus a. Apply fault at the RENO 3 115.00 (533416) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENO 3 (533416) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_184 | 3 Phase fault on WMBROSJ3 115.00 (533311) 115 kV Bus a. Apply fault at the WMBROSJ3 115.00 (533311) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEMPORI3 (533309) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.2. WMBROS 3 (533310) 115.0 kV to WMBROSJ3 (533311) 115.0 kV Transmission Circuit #1 b.3. WMBROSJ3 (533311) 115.0 kV to FLORENC3 (533366) 115.0 kV Transmission Circuit #1 b.4. FLORENC3 (533366) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.5. HILSBOR3 (533369) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 b.6. SPRGCRK3 (533380) 115.0 kV to MOUNDRG3 (533429) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_185 | 3 Phase fault on LYONS 3 115.00 (530620) 115 kV Bus a. Apply fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 b.2. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_186 | 3 Phase fault on 17TH TP2 69.000 (533835) 69 kV Bus a. Apply fault at the 17TH TP2 69.000 (533835) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MEAD S 2 (533815) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 b.2. RIVERSD2 (533834) 69.0 kV to 17TH TP2 (533835) 69.0 kV Transmission Circuit #1 b.3. RIVERSD2 (533834) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 b.4. 17TH TP2 (533835) 69.0 kV to 17TH 2 (533840) 69.0 kV Transmission Circuit #1 b.5. 17TH TP2 (533835) 69.0 kV to WEBSTER2 (533853) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_187 | 3 Phase fault on ZILAJCT2 69.000 (533654) 69 kV Bus a. Apply fault at the ZILAJCT2 69.000 (533654) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALLEN 2 (533621) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to UN1ELSM2 (533647) 69.0 kV Transmission Circuit #1 b.3. UN1ELSM2 (533647) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 b.4. UN8HUMB2 (533650) 69.0 kV to ZILAJCT2 (533654) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_188 | 3 Phase fault on CC4VERN2 69.000 (533631) 69 kV Bus a. Apply fault at the CC4VERN2 69.000 (533631) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ATHENS 2 (533623) 69.0 kV to CC4VERN2 (533631) 69.0 kV Transmission Circuit #1 b.2. BURLJCT2 (533626) 69.0 kV to CC3WEST2 (533630) 69.0 kV Transmission Circuit #1 b.3. BURLJCT2 (533626) 69.0 kV to WOLFCRK2 (533653) 69.0 kV Transmission Circuit #1 b.4. CC3WEST2 (533630) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 b.5. CC4VERN2 (533631) 69.0 kV to GREEN 2 (533636) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_189 | 3 Phase fault on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANALS 2 (533784) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_190 | 3 Phase fault on WESTLNK2 69.000 (533854) 69 kV Bus a. Apply fault at the WESTLNK2 69.000 (533854) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. HOOVERS2 (533806) 69.0 kV to TYLER 2 (533847) 69.0 kV Transmission Circuit #1 b.3. TYLER 2 (533847) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_191 | 3 Phase fault on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 b.2. SUNSET-2 (533844) 69.0 kV to GALE TP2 (533845) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_192 | 3 Phase fault on SE4DEVO2 69.000 (533644) 69 kV Bus a. Apply fault at the SE4DEVO2 69.000 (533644) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSCOTT2 (533635) 69.0 kV to SE4DEVO2 (533644) 69.0 kV Transmission Circuit #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 b.3. MCKEE 2 (533640) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 b.4. SE4DEVO2 (533644) 69.0 kV to SE9HIAT2 (533645) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_193 | 3 Phase fault on CRAWFOR2 69.000 (533758) 69 kV Bus a. Apply fault at the CRAWFOR2 69.000 (533758) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAWFOR2 (533758) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.2. CRAWFOR2 (533758) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 b.3. GIR JCT2 (533762) 69.0 kV to SE1GREE2 (533772) 69.0 kV Transmission Circuit #1 b.4. GIR JCT2 (533762) 69.0 kV to FRANKLIN2 (533876) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_194 | 3 Phase fault on WATER1 2 69.000 (533855) 69 kV Bus a. Apply fault at the WATER1 2 69.000 (533855) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. WATER1 2 (533855) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_195 | 3 Phase fault on WATER2 2 69.000 (533856) 69 kV Bus a. Apply fault at the WATER2 2 69.000 (533856) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 b.2. PLAZA E2 (533829) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_196 | 3 Phase fault on RIPLEYW2 69.000 (533832) 69 kV Bus a. Apply fault at the RIPLEYW2 69.000 (533832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.2. RIPLEYW2 (533832) 69.0 kV to 21ST 2 (533846) 69.0 kV Transmission Circuit #1 b.3. 21ST 2 (533846) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 b.4. RIPLEYW2 (533832) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_197 | 3 Phase fault on GILLJCT2 69.000 (533798) 69 kV Bus a. Apply fault at the GILLJCT2 69.000 (533798) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 b.2. GILLJCT2 (533798) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 b.3. GILLJCT2 (533798) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 b.4. MACARTH2 (533813) 69.0 kV to OATVILL2 (533825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_198 | 3 Phase fault on SENECA 2 69.000 (533839) 69 kV Bus a. Apply fault at the SENECA 2 69.000 (533839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MACARTH2 (533813) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 b.2. OSAGE 2 (533827) 69.0 kV to PLAZA E2 (533829) 69.0 kV Transmission Circuit #1 b.3. OSAGE 2 (533827) 69.0 kV to SENECA 2 (533839) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_199 | 3 Phase fault on ORDNJCT2 69.000 (533703) 69 kV Bus a. Apply fault at the ORDNJCT2 69.000 (533703) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNJCT2 (533703) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.2. ORDNJCT2 (533703) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_200 | 3 Phase fault on ALTAMNS2 69.000 (533672) 69 kV Bus a. Apply fault at the ALTAMNS2 69.000 (533672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTAMNS2 (533672) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 b.2. ALTAMNS2 (533672) 69.0 kV to PARSONS2 (533704) 69.0 kV Transmission Circuit #1 b.3. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_201 | 3 Phase fault on BUTLER 4 138.00 (532987) 138 kV Bus a. Apply fault at the BUTLER 4 138.00 (532987) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLER 4 (532987) 138.0 kV to BUTLERS4 (532989) 138.0 kV Transmission Circuit #z1 b.2. BUTLER 4 (532987) 138.0 kV to MIDIAN 4 (532990) 138.0 kV Transmission Circuit #1 b.3. BUTLER 4 (532987) 138.0 kV to TIOGA 4 (532996) 138.0 kV Transmission Circuit #1 b.4. BUTLER 4 (532987) 138.0 kV to OTTRCRK4 (532997) 138.0 kV Transmission Circuit #1 b.5. BUTLER 4 (532987) 138.0 kV to BUTLERN2 (533583) 69.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_202 | 3 Phase fault on HOLT_REACT7 345.00 (541517) 345 kV Bus a. Apply fault at the HOLT_REACT7 345.00 (541517) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. HOLT_REACT7 (541517) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_203 | 3 Phase fault on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 b.3. GRDVWTP2 (541284) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.4. RGAFB 2 (541288) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 b.5. BELTON 2 (541289) 69.0 kV to BELTONS2 (541290) 69.0 kV Transmission Circuit #1 b.6. BELTON 2 (541289) 69.0 kV to RGAFBTP2 (541322) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_204 | 3 Phase fault on GRDWST 2 69.000 (541286) 69 kV Bus a. Apply fault at the GRDWST 2 69.000 (541286) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDWCTY2 (541285) 69.0 kV to GRDWST 2 (541286) 69.0 kV Transmission Circuit #1 b.2. GRDWST 2 (541286) 69.0 kV to MARTCTY2 (541287) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_205 | 3 Phase fault on FROSTRD_CAP5161.00 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5161.00 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_206 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_207 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_208 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_209 | 3 Phase fault on TERRACE5 161.00 (542991) 161 kV Bus a. Apply fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_210 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_211 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_212 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_213 | 3 Phase fault on QUIND 5 161.00 (546652) 161 kV Bus a. Apply fault at the QUIND 5 161.00 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_214 | 3 Phase fault on QUIND 5 161.00 (546652) 161 kV Bus a. Apply fault at the QUIND 5 161.00 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_215 | 3 Phase fault on NEARMAN5 161.00 (546653) 161 kV Bus a. Apply fault at the NEARMAN5 161.00 (546653) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_216 | 3 Phase fault on NEARMAN5 161.00 (546653) 161 kV Bus a. Apply fault at the NEARMAN5 161.00 (546653) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_217 | 3 Phase fault on SUNSET 5 161.00 (546654) 161 kV Bus a. Apply fault at the SUNSET 5 161.00 (546654) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_218 | 3 Phase fault on KAW W 5 161.00 (546655) 161 kV Bus a. Apply fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_219 | 3 Phase fault on KAW W 5 161.00 (546655) 161 kV Bus a. Apply fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_220 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_221 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_222 | 3 Phase fault on GIBBS 5 161.00 (546658) 161 kV Bus a. Apply fault at the GIBBS 5 161.00 (546658) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_223 | 3 Phase fault on CTR CTY5 161.00 (546659) 161 kV Bus a. Apply fault at the CTR CTY5 161.00 (546659) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_224 | 3 Phase fault on CTR CTY5 161.00 (546659) 161 kV Bus a. Apply fault at the CTR CTY5 161.00 (546659) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_225 | 3 Phase fault on ARMDALE5 161.00 (546661) 161 kV Bus a. Apply fault at the ARMDALE5 161.00 (546661) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_226 | 3 Phase fault on GM PLT 5 161.00 (546663) 161 kV Bus a. Apply fault at the GM PLT 5 161.00 (546663) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GM PLT 5 (546663) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_227 | 3 Phase fault on FAIRFX-5 161.00 (546667) 161 kV Bus a. Apply fault at the FAIRFX-5 161.00 (546667) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRFX-5 (546667) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_228 | 3 Phase fault on PIPER 5 161.00 (546668) 161 kV Bus a. Apply fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_229 | 3 Phase fault on PIPER 5 161.00 (546668) 161 kV Bus a. Apply fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIPER 5 (546668) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_230 | 3 Phase fault on OAK KNOL 69.000 (546670) 69 kV Bus a. Apply fault at the OAK KNOL 69.000 (546670) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK KNOL (546670) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_231 | 3 Phase fault on OAK KNOL 69.000 (546670) 69 kV Bus a. Apply fault at the OAK KNOL 69.000 (546670) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. OAK KNOL (546670) 69.0 kV to MAYWOOD2 (546677) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_232 | 3 Phase fault on MORRIS 2 69.000 (546672) 69 kV Bus a. Apply fault at the MORRIS 2 69.000 (546672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 2 (546672) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_233 | 3 Phase fault on MORRIS 2 69.000 (546672) 69 kV Bus a. Apply fault at the MORRIS 2 69.000 (546672) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_234 | 3 Phase fault on GR WHL 2 69.000 (546673) 69 kV Bus a. Apply fault at the GR WHL 2 69.000 (546673) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GR WHL 2 (546673) 69.0 kV to GW TAP 1 (546675) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_235 | 3 Phase fault on SPEAKER2 69.000 (546674) 69 kV Bus a. Apply fault at the SPEAKER2 69.000 (546674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_236 | 3 Phase fault on GW TAP 1 69.000 (546675) 69 kV Bus a. Apply fault at the GW TAP 1 69.000 (546675) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GW TAP 1 (546675) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_237 | 3 Phase fault on MAYWOOD2 69.000 (546677) 69 kV Bus a. Apply fault at the MAYWOOD2 69.000 (546677) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD2 (546677) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_238 | 3 Phase fault on EVERETT2 69.000 (546682) 69 kV Bus a. Apply fault at the EVERETT2 69.000 (546682) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVERETT2 (546682) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_239 | 3 Phase fault on QUINDA 2 69.000 (546692) 69 kV Bus a. Apply fault at the QUINDA 2 69.000 (546692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_240 | 3 Phase fault on QUINDA 2 69.000 (546692) 69 kV Bus a. Apply fault at the QUINDA 2 69.000 (546692) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_241 | 3 Phase fault on MAYSOTH5 161.00 (546722) 161 kV Bus a. Apply fault at the MAYSOTH5 161.00 (546722) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_242 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_243 | 3 Phase fault on KAW 5 161.00 (546214) 161 kV Bus a. Apply fault at the KAW 5 161.00 (546214) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_244 | 3 Phase fault on QUIND 5 161.00 (546652) 161 kV Bus a. Apply fault at the QUIND 5 161.00 (546652) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_245 | 3 Phase fault on KAW W 5 161.00 (546655) 161 kV Bus a. Apply fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_246 | 3 Phase fault on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_247 | 3 Phase fault on BRMALL 2 69.000 (541283) 69 kV Bus a. Apply fault at the BRMALL 2 69.000 (541283) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMALL 2 (541283) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_248 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_249 | 3 Phase fault on SUB I 69.000 (548800) 69 kV Bus a. Apply fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_250 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_251 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_252 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_253 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_254 | 3 Phase fault on SUB E 69.000 (548804) 69 kV Bus a. Apply fault at the SUB E 69.000 (548804) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_255 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_256 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_257 | 3 Phase fault on BLUVLY 69.000 (548806) 69 kV Bus a. Apply fault at the BLUVLY 69.000 (548806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to SUB P (548827) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_258 | 3 Phase fault on SUB B 69.000 (548810) 69 kV Bus a. Apply fault at the SUB B 69.000 (548810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB B (548810) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_259 | 3 Phase fault on SUB J 69.000 (548811) 69 kV Bus a. Apply fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_260 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY-161 (548807) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_261 | 3 Phase fault on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.3. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_262 | 3 Phase fault on STRLNGRD 69.000 (548826) 69 kV Bus a. Apply fault at the STRLNGRD 69.000 (548826) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB E (548804) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.3. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_263 | 3 Phase fault on KCPL JCT 69.000 (548832) 69 kV Bus a. Apply fault at the KCPL JCT 69.000 (548832) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB F (548803) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 b.2. SUB E (548804) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_264 | 3 Phase fault on BLUMILS5 161.00 (543004) 161 kV Bus a. Apply fault at the BLUMILS5 161.00 (543004) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUMILS5 (543004) 161.0 kV to BLUVLY-161 (548807) 161.0 kV Transmission Circuit #1 b.2. BLUMILS5 (543004) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_265 | 3 Phase fault on 5MOCITYB1 161.00 (301563) 161 kV Bus a. Apply fault at the 5MOCITYB1 161.00 (301563) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5MOCITYB1 (301563) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_266 | 3 Phase fault on 5LEVASY 161.00 (300320) 161 kV Bus a. Apply fault at the 5LEVASY 161.00 (300320) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_267 | 3 Phase fault on SIBLEYPL 161.00 (541250) 161 kV Bus a. Apply fault at the SIBLEYPL 161.00 (541250) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEYPL (541250) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_268 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_269 | 3 Phase fault on LAKCTYJ2 69.000 (543087) 69 kV Bus a. Apply fault at the LAKCTYJ2 69.000 (543087) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAKCTYJ2 (543087) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_270 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to SUB M-161 (548814) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_271 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to SUB N-161 (548820) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_272 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_273 | 3 Phase fault on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_N2 (543089) 69.0 kV to SUGRCRK_S2 (543163) 69.0 kV Transmission Circuit #z1 b.2. SUGRCRK_N2 (543089) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.3. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 b.4. SUGRCK_TP_W2 (543164) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.5. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_274 | 3 Phase fault on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KCSOUTH5 (541245) 161.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_275 | 3 Phase fault on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CENTENN4 (533034) 138.0 kV to COWSKIN4 (533038) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.3. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_276 | 3 Phase fault on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 b.3. HOOVERS4 (533050) 138.0 kV to HOOVERS2 (533806) 69.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_277 | 3 Phase fault on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 b.2. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.3. HOOVERN4 (533049) 138.0 kV to HOOVERN2 (533805) 69.0 kV to HOOVR3 1 (533109) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_278 | 3 Phase fault on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMOTAR4 (533037) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.3. NOEASTW4 (533061) 138.0 kV to NOEASTW2 (533822) 69.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_279 | 3 Phase fault on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 29TH 4 (533024) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.2. ANDOVER4 (533026) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #1 b.3. NOEASTE4 (533060) 138.0 kV to NOEASTW4 (533061) 138.0 kV Transmission Circuit #z1 b.4. NOEASTE4 (533060) 138.0 kV to NOEASTE2 (533823) 69.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_280 | 3 Phase fault on WEAVER 4 138.00 (532991) 138 kV Bus a. Apply fault at the WEAVER 4 138.00 (532991) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WEAVER 4 (532991) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 b.2. WEAVER 4 (532991) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 b.3. WEAVER 4 (532991) 138.0 kV to BU11PON4 (533032) 138.0 kV Transmission Circuit #1 b.4. WEAVER 4 (532991) 138.0 kV to ROSEHIL4 (533062) 138.0 kV Transmission Circuit #1 b.5. WEAVER 4 (532991) 138.0 kV to SPRNGDL4 (533067) 138.0 kV Transmission Circuit #1 b.6. WEAVER 4 (532991) 138.0 kV to WEAVER 2 (533604) 69.0 kV to WEAVER 1 (533083) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_281 | 3 Phase fault on CIRCLE 3 115.00 (533413) 115 kV Bus a. Apply fault at the CIRCLE 3 115.00 (533413) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 3 (533413) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_282 | 3 Phase fault on WMCPHER3 115.00 (533438) 115 kV Bus a. Apply fault at the WMCPHER3 115.00 (533438) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WMCPHER3 (533438) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_283 | 3 Phase fault on BENTON 4 138.00 (532986) 138 kV Bus a. Apply fault at the BENTON 4 138.00 (532986) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENTON 4 (532986) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_284 | 3 Phase fault on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEARWT4 (533036) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_285 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_286 | 3 Phase fault on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEHIL4 (533062) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_287 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_288 | 3 Phase fault on PARSONS2 69.000 (533704) 69 kV Bus a. Apply fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PARSONS2 (533704) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_289 | 3 Phase fault on WOLFCRK2 69.000 (533653) 69 kV Bus a. Apply fault at the WOLFCRK2 69.000 (533653) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOLFCRK2 (533653) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_290 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_291 | 3 Phase fault on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_292 | 3 Phase fault on BAKER 2 69.000 (532926) 69 kV Bus a. Apply fault at the BAKER 2 69.000 (532926) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BAKER 2 (532926) 69.0 kV to SOPITT 2 (533773) 69.0 kV Transmission Circuit #1 b.2. BAKER 2 (532926) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_293 | 3 Phase fault on EDWARVL3 115.00 (533238) 115 kV Bus a. Apply fault at the EDWARVL3 115.00 (533238) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWARVL3 (533238) 115.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_294 | 3 Phase fault on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_295 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_296 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_297 | 3 Phase fault on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.3. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 b.4. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_298 | 3 Phase fault on S3454 3 345.00 (645454) 345 kV Bus a. Apply fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_299 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_300 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_301 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_302 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_303 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_304 | 3 Phase fault on S3458 3 345.00 (645458) 345 kV Bus a. Apply fault at the S3458 3 345.00 (645458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3458 3 (645458) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_305 | 3 Phase fault on COOPER 3 345.00 (640139) 345 kV Bus a. Apply fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_306 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_307 | 3 Phase fault on S3455 3 345.00 (645455) 345 kV Bus a. Apply fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_308 | 3 Phase fault on S3456 3 345.00 (645456) 345 kV Bus a. Apply fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_309 | 3 Phase fault on RAGO 4 138.00 (539000) 138 kV Bus a. Apply fault at the RAGO 4 138.00 (539000) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAGO 4 (539000) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_310 | 3 Phase fault on IODINE 4 138.00 (520957) 138 kV Bus a. Apply fault at the IODINE 4 138.00 (520957) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSUPLY4 (520920) 138.0 kV to IODINE 4 (520957) 138.0 kV Transmission Circuit #1 b.2. IODINE 4 (520957) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_311 | 3 Phase fault on GLASMTN4 138.00 (514788) 138 kV Bus a. Apply fault at the GLASMTN4 138.00 (514788) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLEOCOR4 (514778) 138.0 kV to GLASMTN4 (514788) 138.0 kV Transmission Circuit #1 b.2. GLASMTN4 (514788) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_312 | 3 Phase fault on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_313 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_314 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_315 | 3 Phase fault on WFEC_RNFRO4 138.00 (520409) 138 kV Bus a. Apply fault at the WFEC_RNFRO4 138.00 (520409) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. WFEC_RNFRO4 (520409) 138.0 kV to WAKTASW4 (520434) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_316 | 3 Phase fault on SEILING4 138.00 (520553) 138 kV Bus a. Apply fault at the SEILING4 138.00 (520553) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SEILING4 (520553) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. SEILING4 (520553) 138.0 kV to TALOGA 4 (521065) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_317 | 3 Phase fault on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_318 | 3 Phase fault on REDCLFT4 138.00 (515533) 138 kV Bus a. Apply fault at the REDCLFT4 138.00 (515533) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEWEY 4 (514787) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.2. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 b.3. IODINE-4 (514796) 138.0 kV to REDCLFT4 (515533) 138.0 kV Transmission Circuit #1 b.4. REDCLFT4 (515533) 138.0 kV to REDCLF 4 (515863) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_319 | 3 Phase fault on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_320 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_321 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_322 | 3 Phase fault on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_323 | 3 Phase fault on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_324 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_325 | 3 Phase fault on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_326 | 3 Phase fault on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_327 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_328 | 3 Phase fault on TATONGA7 345.00 (515407) 345 kV Bus a. Apply fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_329 | 3 Phase fault on MDFRDTP4 138.00 (515569) 138 kV Bus a. Apply fault at the MDFRDTP4 138.00 (515569) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.3. MDFRDTP4 (515569) 138.0 kV to MEDFORD4 (522397) 138.0 kV Transmission Circuit #1 b.4. MEDFORD4 (522397) 138.0 kV to PONDCRK4 (522398) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_330 | 3 Phase fault on RENFROW4 138.00 (515544) 138 kV Bus a. Apply fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_331 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_332 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_333 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_334 | 3 Phase fault on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_335 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_336 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_337 | 3 Phase fault on RENFROW7 345.00 (515543) 345 kV Bus a. Apply fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_338 | 3 Phase fault on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_339 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_340 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_341 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_342 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations; GEN-2018-030 | Build a second circuit from HOLCOMB 345 kV to Finney 345 kV
03 - Central | 25W | Transfer | GROUP3_FAULT_343 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB7 (531449) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_344 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to BUCKNER7 (531501) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_345 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_346 | 3 Phase fault on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_347 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to BARBER 4 (539674) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_348 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_349 | 3 Phase fault on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_350 | 3 Phase fault on MILAN_GOAB 138.00 (539008) 138 kV Bus a. Apply fault at the MILAN_GOAB 138.00 (539008) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.2. BLF-CRK4 (539002) 138.0 kV to CLDWELL4 (539003) 138.0 kV Transmission Circuit #1 b.3. CLDWELL4 (539003) 138.0 kV to MILAN_GOAB (539008) 138.0 kV Transmission Circuit #1 b.4. MILAN_GOAB (539008) 138.0 kV to MILAN 4 (539676) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_351 | 3 Phase fault on SETAB 3 115.00 (531464) 115 kV Bus a. Apply fault at the SETAB 3 115.00 (531464) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to CNTRLPL3 (531485) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_352 | 3 Phase fault on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_353 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_354 | 3 Phase fault on PLYMELL3 115.00 (531393) 115 kV Bus a. Apply fault at the PLYMELL3 115.00 (531393) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIONTAP3 (531392) 115.0 kV to PLYMELL3 (531393) 115.0 kV Transmission Circuit #1 b.2. PLYMELL3 (531393) 115.0 kV to PIERCVL3 (531408) 115.0 kV Transmission Circuit #1 b.3. PLYMELL3 (531393) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_355 | 3 Phase fault on FLETCHR3 115.00 (531420) 115 kV Bus a. Apply fault at the FLETCHR3 115.00 (531420) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_356 | 3 Phase fault on PK_GOAB3 115.00 (531400) 115 kV Bus a. Apply fault at the PK_GOAB3 115.00 (531400) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PUCKET 3 (531375) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.2. PIONEER3 (531391) 115.0 kV to PK_GOAB3 (531400) 115.0 kV Transmission Circuit #1 b.3. PK_GOAB3 (531400) 115.0 kV to FLETCHR3 (531420) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_357 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_358 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_359 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR3 (531405) 115.0 kV to CIM-PLT3 (539654) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_360 | 3 Phase fault on WILLIAM3 115.00 (531440) 115 kV Bus a. Apply fault at the WILLIAM3 115.00 (531440) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR3 (531420) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 b.2. SYRACUS3 (531437) 115.0 kV to WILLIAM3 (531440) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_361 | 3 Phase fault on GANO 3 115.00 (531493) 115 kV Bus a. Apply fault at the GANO 3 115.00 (531493) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 b.2. PILE 3 (531432) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.3. PILE 3 (531432) 115.0 kV to GANO 3 (531493) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_362 | 3 Phase fault on KSAVWTP3 115.00 (531480) 115 kV Bus a. Apply fault at the KSAVWTP3 115.00 (531480) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to KSAVWTP3 (531480) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_363 | 3 Phase fault on SWNDTAP3 115.00 (531476) 115 kV Bus a. Apply fault at the SWNDTAP3 115.00 (531476) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 b.2. SWNDTAP3 (531476) 115.0 kV to S. WIND3 (531477) 115.0 kV Transmission Circuit #1 b.3. SWNDTAP3 (531476) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_364 | 3 Phase fault on MORRIS-3 115.00 (531430) 115 kV Bus a. Apply fault at the MORRIS-3 115.00 (531430) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOBSON 3 (531419) 115.0 kV to MORRIS-3 (531430) 115.0 kV Transmission Circuit #1 b.2. MORRIS-3 (531430) 115.0 kV to IRSKDOL3 (531478) 115.0 kV Transmission Circuit #1 b.3. MORRIS-3 (531430) 115.0 kV to MORRIS1 (531206) 34.5 kV to MORRIS-T (531207) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_365 | 3 Phase fault on LOWETAP3 115.00 (531425) 115 kV Bus a. Apply fault at the LOWETAP3 115.00 (531425) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. JONES3 (531379) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.2. JONES3 (531379) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.3. DOBSON 3 (531419) 115.0 kV to LOWETAP3 (531425) 115.0 kV Transmission Circuit #1 b.4. LOWETAP3 (531425) 115.0 kV to JAMESON3 (531426) 115.0 kV Transmission Circuit #1 b.5. LOWETAP3 (531425) 115.0 kV to LOWESUB3 (531435) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_366 | 3 Phase fault on SAWYER 3 115.00 (539649) 115 kV Bus a. Apply fault at the SAWYER 3 115.00 (539649) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SAWYER 3 (539649) 115.0 kV to RVROAD (539651) 115.0 kV Transmission Circuit #1 b.2. SAWYER 3 (539649) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_367 | 3 Phase fault on MED-LDG3 115.00 (539673) 115 kV Bus a. Apply fault at the MED-LDG3 115.00 (539673) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MED-LDG3 (539673) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_368 | 3 Phase fault on SUNCITY3 115.00 (539697) 115 kV Bus a. Apply fault at the SUNCITY3 115.00 (539697) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRNBURG3 (539664) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. GRNBURG3 (539664) 115.0 kV to SSTARTP3 (539763) 115.0 kV Transmission Circuit #1 b.3. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.4. GRNBURG3 (539664) 115.0 kV to GRNBURG1 (539710) 34.5 kV to GRNBUG-T (539910) 13.8 kV Three Winding #1 b.5. SUNCITY3 (539697) 115.0 kV to SUNCITY1 (539733) 34.5 kV to SUNCT-T (539937) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_369 | 3 Phase fault on SPRVL 3 115.00 (539759) 115 kV Bus a. Apply fault at the SPRVL 3 115.00 (539759) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to NFTDODG3 (539771) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_370 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER1 (531452) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_371 | 3 Phase fault on MINGO 7 345.00 (531451) 345 kV Bus a. Apply fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_372 | 3 Phase fault on HOLCOMB7 345.00 (531449) 345 kV Bus a. Apply fault at the HOLCOMB7 345.00 (531449) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLCOMB3 (531448) 115.0 kV to HOLCOMB7 (531449) 345.0 kV to HOLCTER1 (531450) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_373 | 3 Phase fault on SETAB 7 345.00 (531465) 345 kV Bus a. Apply fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_374 | 3 Phase fault on BARBER 4 138.00 (539674) 138 kV Bus a. Apply fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 3 (539760) 115.0 kV to BARBER 4 (539674) 138.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_375 | 3 Phase fault on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEARVL3 (539694) 115.0 kV to SPEARVL6 (539695) 230.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_376 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPEARVL6 (539695) 230.0 kV to SPERVIL7 (531469) 345.0 kV to SPERTER1 (531468) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_377 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPRVL 3 (539759) 115.0 kV to SPERVIL7 (531469) 345.0 kV to SPRVL-T (539960) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_378 | 3 Phase fault on HARPER 4 138.00 (539668) 138 kV Bus a. Apply fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HARPER 4 (539668) 138.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_379 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_380 | 3 Phase fault on NES3-1 22.000 (511840) 22 kV Bus a. Apply fault at the NES3-1 22.000 (511840) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NES3-1 (511840) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_381 | 3 Phase fault on GRECCTG_1 20.000 (512614) 20 kV Bus a. Apply fault at the GRECCTG_1 20.000 (512614) 20 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRECCTG_1 (512614) 20.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_382 | 3 Phase fault on GRECSTG_1 17.500 (512615) 17.5 kV Bus a. Apply fault at the GRECSTG_1 17.500 (512615) 17.5 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRECSTG_1 (512615) 17.5 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_383 | 3 Phase fault on GRDA17-1 22.800 (512688) 22.79999924 kV Bus a. Apply fault at the GRDA17-1 22.800 (512688) 22.79999924 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDA17-1 (512688) 22.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_384 | 3 Phase fault on EMPEC121 13.800 (532740) 13.80000019 kV Bus a. Apply fault at the EMPEC121 13.800 (532740) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC121 (532740) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_385 | 3 Phase fault on EMPEC121 13.800 (532740) 13.80000019 kV Bus a. Apply fault at the EMPEC121 13.800 (532740) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC121 (532740) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_386 | 3 Phase fault on EMPEC341 13.800 (532741) 13.80000019 kV Bus a. Apply fault at the EMPEC341 13.800 (532741) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC341 (532741) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_387 | 3 Phase fault on EMPEC341 13.800 (532741) 13.80000019 kV Bus a. Apply fault at the EMPEC341 13.800 (532741) 13.80000019 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC341 (532741) 13.8 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_388 | 3 Phase fault on EMPEC5 1 18.000 (532742) 18 kV Bus a. Apply fault at the EMPEC5 1 18.000 (532742) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC5 1 (532742) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_389 | 3 Phase fault on EMPEC6 1 18.000 (532743) 18 kV Bus a. Apply fault at the EMPEC6 1 18.000 (532743) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPEC6 1 (532743) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_390 | 3 Phase fault on WCGS U1 25.000 (532751) 25 kV Bus a. Apply fault at the WCGS U1 25.000 (532751) 25 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WCGS U1 (532751) 25.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_391 | 3 Phase fault on LAC G1 1 22.000 (542955) 22 kV Bus a. Apply fault at the LAC G1 1 22.000 (542955) 22 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC G1 1 (542955) 22.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_392 | 3 Phase fault on LAC G2 1 24.000 (542956) 24 kV Bus a. Apply fault at the LAC G2 1 24.000 (542956) 24 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC G2 1 (542956) 24.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_393 | 3 Phase fault on NEBCTY1G 18.000 (645011) 18 kV Bus a. Apply fault at the NEBCTY1G 18.000 (645011) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEBCTY1G (645011) 18.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_394 | 3 Phase fault on NEBCTY2G 23.000 (645012) 23 kV Bus a. Apply fault at the NEBCTY2G 23.000 (645012) 23 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEBCTY2G (645012) 23.0 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_395 | 3 Phase fault on G18-022GEN1 0.6000 (762584) 0.600000024 kV Bus a. Apply fault at the G18-022GEN1 0.6000 (762584) 0.600000024 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-022GEN1 (762584) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_396 | 3 Phase fault on G18-022GEN2 0.6000 (762587) 0.600000024 kV Bus a. Apply fault at the G18-022GEN2 0.6000 (762587) 0.600000024 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-022GEN2 (762587) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_397 | 3 Phase fault on G18-022GEN3 0.6300 (762588) 0.629999995 kV Bus a. Apply fault at the G18-022GEN3 0.6300 (762588) 0.629999995 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-022GEN3 (762588) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_398 | 3 Phase fault on G18-030GEN1 0.6600 (762661) 0.660000026 kV Bus a. Apply fault at the G18-030GEN1 0.6600 (762661) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-030GEN1 (762661) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_399 | 3 Phase fault on G18-031GEN1 0.6600 (762672) 0.660000026 kV Bus a. Apply fault at the G18-031GEN1 0.6600 (762672) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-031GEN1 (762672) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_400 | 3 Phase fault on G18-032GEN1 0.6500 (762683) 0.649999976 kV Bus a. Apply fault at the G18-032GEN1 0.6500 (762683) 0.649999976 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-032GEN1 (762683) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_401 | 3 Phase fault on G18-032GEN2 0.6500 (762686) 0.649999976 kV Bus a. Apply fault at the G18-032GEN2 0.6500 (762686) 0.649999976 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-032GEN2 (762686) 0.6 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_402 | 3 Phase fault on G18-049-GEN10.6600 (762837) 0.660000026 kV Bus a. Apply fault at the G18-049-GEN10.6600 (762837) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-049-GEN1 (762837) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_403 | 3 Phase fault on G18-054-GEN10.6600 (762892) 0.660000026 kV Bus a. Apply fault at the G18-054-GEN10.6600 (762892) 0.660000026 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-GEN1 (762892) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_404 | 3 Phase fault on G18-057-GEN10.6900 (762925) 0.689999998 kV Bus a. Apply fault at the G18-057-GEN10.6900 (762925) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-057-GEN1 (762925) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_405 | 3 Phase fault on G18-062-GEN10.6900 (762979) 0.689999998 kV Bus a. Apply fault at the G18-062-GEN10.6900 (762979) 0.689999998 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-062-GEN1 (762979) 0.7 kV Generator # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_406 | 3 Phase fault on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_407 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_408 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_409 | 3 Phase fault on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_410 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_411 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_412 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_413 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_414 | 3 Phase fault on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_415 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_416 | 3 Phase fault on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_417 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_418 | 3 Phase fault on SPERVIL7 345.00 (531469) 345 kV Bus a. Apply fault at the SPERVIL7 345.00 (531469) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SPERVIL7 (531469) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_419 | 3 Phase fault on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_420 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_421 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_422 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to G17-004-TAP (588494) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_423 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_424 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_425 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_426 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to MARMTNW5 (532935) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_427 | 3 Phase fault on MARMTNE5 161.00 (532934) 161 kV Bus a. Apply fault at the MARMTNE5 161.00 (532934) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMTNE5 (532934) 161.0 kV to G17-005-TAP (588504) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_428 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_429 | 3 Phase fault on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_430 | 3 Phase fault on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_431 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_432 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_433 | 3 Phase fault on EVANS N4 138.00 (533040) 138 kV Bus a. Apply fault at the EVANS N4 138.00 (533040) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EVANS N4 (533040) 138.0 kV to EVANS S4 (533041) 138.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_434 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_435 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL S 4 (533046) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_436 | 3 Phase fault on GILL W 4 138.00 (533045) 138 kV Bus a. Apply fault at the GILL W 4 138.00 (533045) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL W 4 (533045) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_437 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_438 | 3 Phase fault on WACO S 4 138.00 (533071) 138 kV Bus a. Apply fault at the WACO S 4 138.00 (533071) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO S 4 (533071) 138.0 kV to WACO 4 (533072) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_439 | 3 Phase fault on WACO 4 138.00 (533072) 138 kV Bus a. Apply fault at the WACO 4 138.00 (533072) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WACO 4 (533072) 138.0 kV to WACO N 4 (533073) 138.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_440 | 3 Phase fault on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUNDRG3 (533429) 115.0 kV to MNDRGCT3 (533430) 115.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_441 | 3 Phase fault on LABETTE2 69.000 (533695) 69 kV Bus a. Apply fault at the LABETTE2 69.000 (533695) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LABETTE2 (533695) 69.0 kV to LABETTS2 (533696) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_442 | 3 Phase fault on ORDNCE 2 69.000 (533702) 69 kV Bus a. Apply fault at the ORDNCE 2 69.000 (533702) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORDNCE 2 (533702) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_443 | 3 Phase fault on NEOSHON2 69.000 (533768) 69 kV Bus a. Apply fault at the NEOSHON2 69.000 (533768) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_444 | 3 Phase fault on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERN2 (533805) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_445 | 3 Phase fault on HOOVERS2 69.000 (533806) 69 kV Bus a. Apply fault at the HOOVERS2 69.000 (533806) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOOVERS2 (533806) 69.0 kV to SHERIDN2 (533841) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_446 | 3 Phase fault on PLAZA E2 69.000 (533829) 69 kV Bus a. Apply fault at the PLAZA E2 69.000 (533829) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA E2 (533829) 69.0 kV to PLAZA M2 (533857) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_447 | 3 Phase fault on PLAZA M2 69.000 (533857) 69 kV Bus a. Apply fault at the PLAZA M2 69.000 (533857) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PLAZA M2 (533857) 69.0 kV to PLAZA W2 (533858) 69.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_448 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_449 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_450 | 3 Phase fault on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_451 | 3 Phase fault on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_452 | 3 Phase fault on FROSTRD_CAP5161.00 (541139) 161 kV Bus a. Apply fault at the FROSTRD_CAP5161.00 (541139) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD_CAP5 (541139) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_453 | 3 Phase fault on NASHUA_CAP5 161.00 (541144) 161 kV Bus a. Apply fault at the NASHUA_CAP5 161.00 (541144) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA_CAP5 (541144) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_454 | 3 Phase fault on RNRIDGE_CAP5161.00 (541145) 161 kV Bus a. Apply fault at the RNRIDGE_CAP5161.00 (541145) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE_CAP5 (541145) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_455 | 3 Phase fault on WSTELEC_CAP5161.00 (541149) 161 kV Bus a. Apply fault at the WSTELEC_CAP5161.00 (541149) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC_CAP5 (541149) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_456 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC1 (541411) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_457 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC2 (541412) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_458 | 3 Phase fault on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MULLNCR7 (541197) 345.0 kV to MC REAC3 (541413) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_459 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_460 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_461 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_462 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIB REA1 (541414) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_463 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_464 | 3 Phase fault on SIBLEY 5 161.00 (541202) 161 kV Bus a. Apply fault at the SIBLEY 5 161.00 (541202) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_465 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to SMTHVL 5 (541204) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_466 | 3 Phase fault on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_467 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to GRDVWE 5 (541223) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_468 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to HONEYWL5 (541382) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_469 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_470 | 3 Phase fault on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_471 | 3 Phase fault on FROSTRD5 161.00 (541220) 161 kV Bus a. Apply fault at the FROSTRD5 161.00 (541220) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_472 | 3 Phase fault on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_473 | 3 Phase fault on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_474 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_475 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_476 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_477 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_478 | 3 Phase fault on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_479 | 3 Phase fault on G18-054-TAP 161.00 (541231) 161 kV Bus a. Apply fault at the G18-054-TAP 161.00 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-TAP (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_480 | 3 Phase fault on G18-054-TAP 161.00 (541231) 161 kV Bus a. Apply fault at the G18-054-TAP 161.00 (541231) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. G18-054-TAP (541231) 161.0 kV to NRAYMORE (541317) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_481 | 3 Phase fault on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_482 | 3 Phase fault on LNGVW 2 69.000 (541282) 69 kV Bus a. Apply fault at the LNGVW 2 69.000 (541282) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to BRMALL 2 (541283) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_483 | 3 Phase fault on NRAYMORE 161.00 (541317) 161 kV Bus a. Apply fault at the NRAYMORE 161.00 (541317) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NRAYMORE (541317) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_484 | 3 Phase fault on HOLT 7 345.00 (541510) 345 kV Bus a. Apply fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT 7 (541510) 345.0 kV to HOLT_REACT7 (541517) 345.0 kV Transmission Circuit #z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_485 | 3 Phase fault on LAC_LAKE_2 69.000 (541541) 69 kV Bus a. Apply fault at the LAC_LAKE_2 69.000 (541541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LAC_LAKE_2 (541541) 69.0 kV to LACYGNE2 (543659) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_486 | 3 Phase fault on BARRY_CAP 5 161.00 (542944) 161 kV Bus a. Apply fault at the BARRY_CAP 5 161.00 (542944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARRY_CAP 5 (542944) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_487 | 3 Phase fault on GLADSTN_CAP5161.00 (542946) 161 kV Bus a. Apply fault at the GLADSTN_CAP5161.00 (542946) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN_CAP5 (542946) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_488 | 3 Phase fault on MERRIAM_CAP5161.00 (542947) 161 kV Bus a. Apply fault at the MERRIAM_CAP5161.00 (542947) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERRIAM_CAP5 (542947) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_489 | 3 Phase fault on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS_CAP5 (542948) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_490 | 3 Phase fault on STHTOWN_CAP5161.00 (542950) 161 kV Bus a. Apply fault at the STHTOWN_CAP5161.00 (542950) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN_CAP5 (542950) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #r c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_491 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_492 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_493 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_494 | 3 Phase fault on WGARDNR5 161.00 (542966) 161 kV Bus a. Apply fault at the WGARDNR5 161.00 (542966) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_495 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_496 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_497 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to ANTIOCH5 (543050) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_498 | 3 Phase fault on STILWEL5 161.00 (542969) 161 kV Bus a. Apply fault at the STILWEL5 161.00 (542969) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STILWEL5 (542969) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_499 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_500 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_501 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_502 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_503 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHS_XF5 (543130) 161.0 kV Transmission Circuit #z2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_504 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_505 | 3 Phase fault on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_506 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_507 | 3 Phase fault on LEVEE 5 161.00 (542976) 161 kV Bus a. Apply fault at the LEVEE 5 161.00 (542976) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_508 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_509 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to G17-183-TAP (761383) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_510 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE11_7 (543629) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_511 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE22_7 (543632) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_512 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_513 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_514 | 3 Phase fault on NEASTS5 161.00 (542985) 161 kV Bus a. Apply fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEASTS5 (542985) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_515 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_516 | 3 Phase fault on TROOST 5 161.00 (542986) 161 kV Bus a. Apply fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_517 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_518 | 3 Phase fault on GRAND 5 161.00 (542987) 161 kV Bus a. Apply fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_519 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_520 | 3 Phase fault on GRAND W5 161.00 (542988) 161 kV Bus a. Apply fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_521 | 3 Phase fault on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CROSTWN5 (542990) 161.0 kV to CHARLOT5 (543133) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_522 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_523 | 3 Phase fault on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_524 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to HICKMAN5 (542994) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_525 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_526 | 3 Phase fault on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. STHTOWN5 (542993) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_527 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_528 | 3 Phase fault on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDTOWN5 (542996) 161.0 kV to FOREST 5 (543001) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_529 | 3 Phase fault on LVISTA 5 161.00 (542998) 161 kV Bus a. Apply fault at the LVISTA 5 161.00 (542998) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LVISTA 5 (542998) 161.0 kV to BUNKRDG5 (543008) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_530 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_531 | 3 Phase fault on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_532 | 3 Phase fault on CHOUTEU5 161.00 (543011) 161 kV Bus a. Apply fault at the CHOUTEU5 161.00 (543011) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_533 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_534 | 3 Phase fault on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_535 | 3 Phase fault on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_536 | 3 Phase fault on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_537 | 3 Phase fault on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_538 | 3 Phase fault on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRMGHAM5 (543020) 161.0 kV to CLAYCM25 (543023) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_539 | 3 Phase fault on NASHUA-5 161.00 (543028) 161 kV Bus a. Apply fault at the NASHUA-5 161.00 (543028) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NASHUA-5 (543028) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_540 | 3 Phase fault on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_541 | 3 Phase fault on SUGRCRK_S2 69.000 (543163) 69 kV Bus a. Apply fault at the SUGRCRK_S2 69.000 (543163) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUGRCRK_S2 (543163) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_542 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_543 | 3 Phase fault on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_544 | 3 Phase fault on MILLST 5 161.00 (546224) 161 kV Bus a. Apply fault at the MILLST 5 161.00 (546224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_545 | 3 Phase fault on SPEAKER2 69.000 (546674) 69 kV Bus a. Apply fault at the SPEAKER2 69.000 (546674) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW 2 (546678) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_546 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to EVERETT2 (546682) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_547 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_548 | 3 Phase fault on KAW 2 69.000 (546678) 69 kV Bus a. Apply fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_549 | 3 Phase fault on MUNCIE 2 69.000 (546681) 69 kV Bus a. Apply fault at the MUNCIE 2 69.000 (546681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNCIE 2 (546681) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_550 | 3 Phase fault on MUNCIE 2 69.000 (546681) 69 kV Bus a. Apply fault at the MUNCIE 2 69.000 (546681) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MUNCIE 2 (546681) 69.0 kV to QUINDA 2 (546692) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_551 | 3 Phase fault on WWR477 161.00 (547459) 161 kV Bus a. Apply fault at the WWR477 161.00 (547459) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WWR477 (547459) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_552 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_553 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to FIR417 5 (547490) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_554 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to STL439 5 (547498) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_555 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_556 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_557 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to RIV406 2 (547602) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_558 | 3 Phase fault on RIV167 2 69.000 (547541) 69 kV Bus a. Apply fault at the RIV167 2 69.000 (547541) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV167 2 (547541) 69.0 kV to GLF339 2 (547690) 69.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_559 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV to G18-030-TAP (762662) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_560 | 3 Phase fault on GI94_POI 345.00 (709400) 345 kV Bus a. Apply fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_561 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_562 | 3 Phase fault on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTH 2 (543080) 69.0 kV to HAWT12_2 (543664) 69.0 kV Transmission Circuit # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_563 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_564 | 3 Phase fault on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_565 | 3 Phase fault on 7JASPER 345.00 (300949) 345 kV Bus a. Apply fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_566 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM6 (511557) 230.0 kV to CHISHOLM7 (511553) 345.0 kV to CHISHOLM1 (511558) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_567 | 3 Phase fault on MOORLND4 138.00 (520999) 138 kV Bus a. Apply fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOORLND4 (520999) 138.0 kV to MOORLND2 (520995) 69.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_568 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_569 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_570 | 3 Phase fault on NOBLE_WND 7345.00 (523101) 345 kV Bus a. Apply fault at the NOBLE_WND 7345.00 (523101) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_571 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to G06-44 (560577) 115.0 kV to NOVUS1_TR2 2 (560578) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_572 | 3 Phase fault on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_573 | 3 Phase fault on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. WALKMYR2 (531404) 69.0 kV to WALKMYR3 (531405) 115.0 kV to WALKMYR1 (531252) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_574 | 3 Phase fault on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GARDNCY2 (531423) 69.0 kV to GRDNCTY3 (531445) 115.0 kV to GRDNCYT1 (531258) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_575 | 3 Phase fault on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_576 | 3 Phase fault on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_577 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 1X1 (532807) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_578 | 3 Phase fault on RENO 7 345.00 (532771) 345 kV Bus a. Apply fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_579 | 3 Phase fault on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_580 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV1X1 (532815) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_581 | 3 Phase fault on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SWISVAL7 (532774) 345.0 kV to SWISVAL6 (532856) 230.0 kV to SWISV2X2 (532819) 14.4 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_582 | 3 Phase fault on 87TH 7 345.00 (532775) 345 kV Bus a. Apply fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 87TH 7 (532775) 345.0 kV to 87TH 3 (533283) 115.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_583 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_584 | 3 Phase fault on BENTON 7 345.00 (532791) 345 kV Bus a. Apply fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_585 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 4 (533021) 138.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_586 | 3 Phase fault on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_587 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH1 1 (532826) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_588 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH3 1 (532831) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_589 | 3 Phase fault on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_590 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_591 | 3 Phase fault on WICHITA7 345.00 (532796) 345 kV Bus a. Apply fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WICHITA7 (532796) 345.0 kV to EVANS N4 (533040) 138.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_592 | 3 Phase fault on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. WOLFCRK7 (532797) 345.0 kV to WOLFCRK2 (533653) 69.0 kV to WOLFCRK1 (532962) 17.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_593 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 7 (532798) 345.0 kV to VIOLA 4 (533075) 138.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_594 | 3 Phase fault on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_595 | 3 Phase fault on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EDWRDVL5 (532912) 161.0 kV to EDWARVL3 (533238) 115.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_596 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 4 (533021) 138.0 kV to NEOSH4 1 (532958) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_597 | 3 Phase fault on NEOSHO 5 161.00 (532937) 161 kV Bus a. Apply fault at the NEOSHO 5 161.00 (532937) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHOS4 (533020) 138.0 kV to NEOSH5 1 (532959) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_598 | 3 Phase fault on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_599 | 3 Phase fault on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MIDIAN 4 (532990) 138.0 kV to MIDIANW2 (533597) 69.0 kV to MIDIAN 1 (533082) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_600 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_601 | 3 Phase fault on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HALSTD 4 (533011) 138.0 kV to HALSTED2 (533736) 69.0 kV to HALST4 1 (533093) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_602 | 3 Phase fault on MOUND 4 138.00 (533013) 138 kV Bus a. Apply fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MOUND 4 (533013) 138.0 kV to MOUNDRG3 (533429) 115.0 kV to MOUN 2X1 (533097) 7.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_603 | 3 Phase fault on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHOS2 (533778) 69.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_604 | 3 Phase fault on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHON2 (533768) 69.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_605 | 3 Phase fault on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHLM4 (533035) 138.0 kV to CHISHLM2 (533786) 69.0 kV to CHISOLM1 (533103) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_606 | 3 Phase fault on GILL E 4 138.00 (533044) 138 kV Bus a. Apply fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_607 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_608 | 3 Phase fault on GILL S 4 138.00 (533046) 138 kV Bus a. Apply fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. GILL S 4 (533046) 138.0 kV to GILL E 2 (533795) 69.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_609 | 3 Phase fault on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_610 | 3 Phase fault on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAVIS 3 (533415) 115.0 kV to DAVIS 2 (533506) 69.0 kV to DAVIS 1 (533444) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_611 | 3 Phase fault on HEC 3 115.00 (533419) 115 kV Bus a. Apply fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HEC 3 (533419) 115.0 kV to HEC 2 (533513) 69.0 kV to HEC 1 (533445) 34.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_612 | 3 Phase fault on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_613 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO E2 (533673) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO3 1 (533087) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_614 | 3 Phase fault on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ALTOO W2 (533674) 69.0 kV to ALTOONA4 (533001) 138.0 kV to ALTOO1 1 (533086) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_615 | 3 Phase fault on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_616 | 3 Phase fault on THISTLE7 345.00 (539801) 345 kV Bus a. Apply fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THISTLE7 (539801) 345.0 kV to THISTLE4 (539804) 138.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_617 | 3 Phase fault on PECULR 7 345.00 (541198) 345 kV Bus a. Apply fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_618 | 3 Phase fault on PHILL 7 345.00 (541200) 345 kV Bus a. Apply fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_619 | 3 Phase fault on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_620 | 3 Phase fault on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MARTCTY2 (541287) 69.0 kV to MARTCTY5 (541210) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_621 | 3 Phase fault on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_622 | 3 Phase fault on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_623 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_624 | 3 Phase fault on STILWEL7 345.00 (542968) 345 kV Bus a. Apply fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. STILWEL7 (542968) 345.0 kV to STILWEL5 (542969) 161.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_625 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_626 | 3 Phase fault on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T22 (543645) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_627 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_628 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_629 | 3 Phase fault on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRAIG 7 (542977) 345.0 kV to CRAIG 5 (542978) 161.0 kV to CRAI T33 (543643) 13.8 kV Three Winding #33 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_630 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_631 | 3 Phase fault on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. NASHUA 7 (542980) 345.0 kV to NASHUA-5 (543028) 161.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_632 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC3_STAR7 (543667) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_633 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LAC8_STAR7 (543669) 345.0 kV Transmission Circuit #h c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_634 | 3 Phase fault on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LACYGNE7 (542981) 345.0 kV to LACYGNE2 (543659) 69.0 kV to LACYGN7_TER1 (543660) 6.9 kV Three Winding #7 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_635 | 3 Phase fault on IATAN 7 345.00 (542982) 345 kV Bus a. Apply fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. IATAN 7 (542982) 345.0 kV to IATAN5 (541350) 161.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_636 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_637 | 3 Phase fault on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWT12_2 (543664) 69.0 kV Two Winding #12 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_638 | 3 Phase fault on BARBER 5 161.00 (546651) 161 kV Bus a. Apply fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_639 | 3 Phase fault on ORO110 5 161.00 (547467) 161 kV Bus a. Apply fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ORO110 5 (547467) 161.0 kV to ORO110 2 (547534) 69.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_640 | 3 Phase fault on RIV4525 161.00 (547469) 161 kV Bus a. Apply fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. RIV4525 (547469) 161.0 kV to RIV167 2 (547541) 69.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_641 | 3 Phase fault on HOC404 5 161.00 (547487) 161 kV Bus a. Apply fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_642 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_643 | 3 Phase fault on BLUVLY-161 161.00 (548807) 161 kV Bus a. Apply fault at the BLUVLY-161 161.00 (548807) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUVLY (548806) 69.0 kV to BLUVLY-161 (548807) 161.0 kV Two Winding #2 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_644 | 3 Phase fault on SUB M-161 161.00 (548814) 161 kV Bus a. Apply fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_645 | 3 Phase fault on SUB N-161 161.00 (548820) 161 kV Bus a. Apply fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_646 | 3 Phase fault on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 (511553) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_647 | 3 Phase fault on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HITCHLAND 7 (523097) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_648 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_649 | 3 Phase fault on SUB K 69.000 (548801) 69 kV Bus a. Apply fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB K (548801) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_650 | 3 Phase fault on SUB H 69.000 (548802) 69 kV Bus a. Apply fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB H (548802) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_651 | 3 Phase fault on SUB M 69.000 (548815) 69 kV Bus a. Apply fault at the SUB M 69.000 (548815) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB M (548815) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_652 | 3 Phase fault on SUB N 69.000 (548821) 69 kV Bus a. Apply fault at the SUB N 69.000 (548821) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB N (548821) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_653 | 3 Phase fault on SUB C 69.000 (548825) 69 kV Bus a. Apply fault at the SUB C 69.000 (548825) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SUB C (548825) 69.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_654 | 3 Phase fault on LAMAR7 345.00 (599950) 345 kV Bus a. Apply fault at the LAMAR7 345.00 (599950) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. LAMAR7 (599950) 345.0 kV Switched Shunt Device # c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_2 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. 5LEVASY (300320) 161.0 kV to ECKLES-161 (548808) 161.0 kV Transmission Circuit #1 b.3. 5PITTSV (300110) 161.0 kV to 5LEVASY (300320) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_1 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.3. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 b.4. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #1 b.5. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.6. WOODWRD4 (514785) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #2 b.7. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.8. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_3 | Single Phase Fault with Stuck Breaker on BARBER 5 161.00 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_4 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_5 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_6 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_7 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_8 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_9 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T39 (648259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_10 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_11 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_12 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG7 (650214) 115.0 kV to NW68HOLDRG3 (650114) 345.0 kV to NW68HOL1 9 (650314) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_13 | Single Phase Fault with Stuck Breaker on NW68HOLDRG3 345.00 (650114) 345 kV Bus a. Apply Fault at the NW68HOLDRG3 345.00 (650114) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. COLMB.E3 (640125) 345.0 kV to NW68HOLDRG3 (650114) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_14 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_15 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_16 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_17 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_18 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NW68HOLDRG3 (650114) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_19 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_20 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_21 | Single Phase Fault with Stuck Breaker on 103&ROKEBY3 345.00 (650189) 345 kV Bus a. Apply Fault at the 103&ROKEBY3 345.00 (650189) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. S3458 3 (645458) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_22 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 84LEIGHTON7 (650267) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_23 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER2 9 (650485) 13.8 kV Three Winding #2 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_24 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 81&OCHENEY7 (650271) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_25 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_26 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT1-1 (506921) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_27 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_28 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to FLINTCR7 (506935) 345.0 kV to FLINT2-1 (506920) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_29 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_30 | Single Phase Fault with Stuck Breaker on SHIPERD7 345.00 (506979) 345 kV Bus a. Apply Fault at the SHIPERD7 345.00 (506979) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 b.2. SHIPERD7 (506979) 345.0 kV to SHIPERD5 (506980) 161.0 kV to SHIPERD1 (506981) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_31 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. RSS T1 4 (509773) 138.0 kV to R.S.S.-7 (509782) 345.0 kV to RSST1 T1 (509882) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_32 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to COGENT 7 (509834) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_33 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-4 (509757) 138.0 kV to WEKIWA-7 (509755) 345.0 kV to WEKIW1-1 (509879) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_34 | Single Phase Fault with Stuck Breaker on WEKIWA-7 345.00 (509755) 345 kV Bus a. Apply Fault at the WEKIWA-7 345.00 (509755) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to SAPLPRD7 (509870) 345.0 kV Transmission Circuit #1 b.2. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_35 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_36 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_37 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WEKIWA-7 (509755) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_38 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_39 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_40 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_41 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_42 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_43 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_44 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_45 | Single Phase Fault with Stuck Breaker on CLARKSV7 345.00 (509745) 345 kV Bus a. Apply Fault at the CLARKSV7 345.00 (509745) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_46 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKSV7 (509745) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 b.2. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_47 | Single Phase Fault with Stuck Breaker on R.S.S.-7 345.00 (509782) 345 kV Bus a. Apply Fault at the R.S.S.-7 345.00 (509782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. R.S.S.-7 (509782) 345.0 kV to ONETA--7 (509807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_48 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_49 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 b.4. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA2-1 (509868) 34.5 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_50 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA1-1 (509881) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_51 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_52 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #1 b.2. ONETA--7 (509807) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_53 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_54 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 b.2. ONETA--4 (509806) 138.0 kV to ONETA--7 (509807) 345.0 kV to ONETA5-1 (509874) 34.5 kV Three Winding #3 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_55 | Single Phase Fault with Stuck Breaker on ONETA--7 345.00 (509807) 345 kV Bus a. Apply Fault at the ONETA--7 345.00 (509807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ONETA--7 (509807) 345.0 kV to OEC 7 (509836) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_56 | Single Phase Fault with Stuck Breaker on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply Fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_57 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_58 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_59 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_60 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_61 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_62 | Single Phase Fault with Stuck Breaker on OUSPRT 4 138.00 (515398) 138 kV Bus a. Apply Fault at the OUSPRT 4 138.00 (515398) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OUSPRT 1 (515397) 34.5 kV to OUSPRTC1 (515928) 34.5 kV Transmission Circuit #1 b.2. OUSPRT 1 (515397) 34.5 kV to OUSPRT 4 (515398) 138.0 kV to OUSPRT T (515396) 10.0 kV Three Winding #1 b.3. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_63 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_64 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_65 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_66 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_67 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_68 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_69 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_70 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 b.4. 120&ALVO 7 (650279) 115.0 kV to WAGENER 7 (650285) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_71 | Single Phase Fault with Stuck Breaker on BARBER 5 161.00 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.3. KAW 5 (546214) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.4. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 b.5. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.6. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_72 | Single Phase Fault with Stuck Breaker on QUIND 5 161.00 (546652) 161 kV Bus a. Apply Fault at the QUIND 5 161.00 (546652) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 b.2. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 b.3. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 b.4. QUIND 5 (546652) 161.0 kV to QGEN2 1 (546698) 15.0 kV Two Winding #1 b.5. QUIND 5 (546652) 161.0 kV to QCT3 1 (546701) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_73 | Single Phase Fault with Stuck Breaker on NEARMAN5 161.00 (546653) 161 kV Bus a. Apply Fault at the NEARMAN5 161.00 (546653) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to NEARMAN5 (546653) 161.0 kV Transmission Circuit #1 b.2. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 b.3. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 b.4. NEARMAN5 (546653) 161.0 kV to NM4BUS (546751) 161.0 kV Transmission Circuit #1 b.5. NEARMAN5 (546653) 161.0 kV to GEN-2018-062 (762976) 161.0 kV Transmission Circuit #1 b.6. NEARMAN5 (546653) 161.0 kV to NMISOBUS (546703) 20.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_74 | Single Phase Fault with Stuck Breaker on SUNSET 5 161.00 (546654) 161 kV Bus a. Apply Fault at the SUNSET 5 161.00 (546654) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEARMAN5 (546653) 161.0 kV to SUNSET 5 (546654) 161.0 kV Transmission Circuit #1 b.2. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_75 | Single Phase Fault with Stuck Breaker on KAW W 5 161.00 (546655) 161 kV Bus a. Apply Fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEAKER5 (546216) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.2. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 b.4. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.5. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_76 | Single Phase Fault with Stuck Breaker on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply Fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEARMAN5 (546653) 161.0 kV to MAYWOOD5 (546656) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.4. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_77 | Single Phase Fault with Stuck Breaker on GIBBS 5 161.00 (546658) 161 kV Bus a. Apply Fault at the GIBBS 5 161.00 (546658) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 5 (546651) 161.0 kV to GIBBS 5 (546658) 161.0 kV Transmission Circuit #1 b.2. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_78 | Single Phase Fault with Stuck Breaker on CTR CTY5 161.00 (546659) 161 kV Bus a. Apply Fault at the CTR CTY5 161.00 (546659) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 b.2. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_79 | Single Phase Fault with Stuck Breaker on ARMDALE5 161.00 (546661) 161 kV Bus a. Apply Fault at the ARMDALE5 161.00 (546661) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 b.2. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_80 | Single Phase Fault with Stuck Breaker on GM PLT 5 161.00 (546663) 161 kV Bus a. Apply Fault at the GM PLT 5 161.00 (546663) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. QUIND 5 (546652) 161.0 kV to GM PLT 5 (546663) 161.0 kV Transmission Circuit #1 b.2. GM PLT 5 (546663) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_81 | Single Phase Fault with Stuck Breaker on TURNER 5 161.00 (546665) 161 kV Bus a. Apply Fault at the TURNER 5 161.00 (546665) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 b.2. GIBBS 5 (546658) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_82 | Single Phase Fault with Stuck Breaker on FAIRFX-5 161.00 (546667) 161 kV Bus a. Apply Fault at the FAIRFX-5 161.00 (546667) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CTR CTY5 (546659) 161.0 kV to FAIRFX-5 (546667) 161.0 kV Transmission Circuit #1 b.2. FAIRFX-5 (546667) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_83 | Single Phase Fault with Stuck Breaker on PIPER 5 161.00 (546668) 161 kV Bus a. Apply Fault at the PIPER 5 161.00 (546668) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.2. PIPER 5 (546668) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_84 | Single Phase Fault with Stuck Breaker on WOLCOTT5 161.00 (546669) 161 kV Bus a. Apply Fault at the WOLCOTT5 161.00 (546669) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.2. MAYWOOD5 (546656) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 b.3. PIPER 5 (546668) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_85 | Single Phase Fault with Stuck Breaker on FIBGLAS5 161.00 (546684) 161 kV Bus a. Apply Fault at the FIBGLAS5 161.00 (546684) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GM PLT 5 (546663) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 b.2. FAIRFX-5 (546667) 161.0 kV to FIBGLAS5 (546684) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_86 | Single Phase Fault with Stuck Breaker on MAYSOTH5 161.00 (546722) 161 kV Bus a. Apply Fault at the MAYSOTH5 161.00 (546722) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYWOOD5 (546656) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.2. PIPER 5 (546668) 161.0 kV to MAYSOTH5 (546722) 161.0 kV Transmission Circuit #1 b.3. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_87 | Single Phase Fault with Stuck Breaker on METRO 5 161.00 (546742) 161 kV Bus a. Apply Fault at the METRO 5 161.00 (546742) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWRDVL5 (532912) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.4. MAYSOTH5 (546722) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_88 | Single Phase Fault with Stuck Breaker on MUNCIE 5 161.00 (546750) 161 kV Bus a. Apply Fault at the MUNCIE 5 161.00 (546750) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAW 5 (546214) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 b.2. CTR CTY5 (546659) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 b.3. ARMDALE5 (546661) 161.0 kV to MUNCIE 5 (546750) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_89 | Single Phase Fault with Stuck Breaker on ROSEDALE 5 161.00 (546222) 161 kV Bus a. Apply Fault at the ROSEDALE 5 161.00 (546222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 b.2. ROSEDALE 5 (546222) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_90 | Single Phase Fault with Stuck Breaker on MILLST 5 161.00 (546224) 161 kV Bus a. Apply Fault at the MILLST 5 161.00 (546224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEDALE 5 (546222) 161.0 kV to MILLST 5 (546224) 161.0 kV Transmission Circuit #1 b.2. MILLST 5 (546224) 161.0 kV to ARMDALE5 (546661) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_91 | Single Phase Fault with Stuck Breaker on KAW W 5 161.00 (546655) 161 kV Bus a. Apply Fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEAKER5 (546216) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.2. SUNSET 5 (546654) 161.0 kV to KAW W 5 (546655) 161.0 kV Transmission Circuit #1 b.3. KAW W 5 (546655) 161.0 kV to TURNER 5 (546665) 161.0 kV Transmission Circuit #1 b.4. KAW W 5 (546655) 161.0 kV to METRO 5 (546742) 161.0 kV Transmission Circuit #1 b.5. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_92 | Single Phase Fault with Stuck Breaker on MORRIS 2 69.000 (546672) 69 kV Bus a. Apply Fault at the MORRIS 2 69.000 (546672) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 2 (546672) 69.0 kV to GW TAP 2 (546676) 69.0 kV Transmission Circuit #1 b.2. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_93 | Single Phase Fault with Stuck Breaker on GR WHL 2 69.000 (546673) 69 kV Bus a. Apply Fault at the GR WHL 2 69.000 (546673) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR WHL 2 (546673) 69.0 kV to GW TAP 1 (546675) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_94 | Single Phase Fault with Stuck Breaker on SPEAKER2 69.000 (546674) 69 kV Bus a. Apply Fault at the SPEAKER2 69.000 (546674) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEAKER2 (546674) 69.0 kV to KAW 2 (546678) 69.0 kV Transmission Circuit #1 b.2. SPEAKER2 (546674) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_95 | Single Phase Fault with Stuck Breaker on MAYWOOD5 161.00 (546656) 161 kV Bus a. Apply Fault at the MAYWOOD5 161.00 (546656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OAK KNOL (546670) 69.0 kV to MAYWOOD2 (546677) 69.0 kV Transmission Circuit #1 b.2. MAYWOOD2 (546677) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 b.3. MAYWOOD2 (546677) 69.0 kV to MAYWOOD5 (546656) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_96 | Single Phase Fault with Stuck Breaker on EVERETT2 69.000 (546682) 69 kV Bus a. Apply Fault at the EVERETT2 69.000 (546682) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAW 2 (546678) 69.0 kV to EVERETT2 (546682) 69.0 kV Transmission Circuit #1 b.2. EVERETT2 (546682) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_97 | Single Phase Fault with Stuck Breaker on KAW W 5 161.00 (546655) 161 kV Bus a. Apply Fault at the KAW W 5 161.00 (546655) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 2 (546672) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 b.2. SPEAKER2 (546674) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 b.3. GW TAP 1 (546675) 69.0 kV to KAW WST2 (546690) 69.0 kV Transmission Circuit #1 b.4. KAW WST2 (546690) 69.0 kV to KAW W 5 (546655) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_98 | Single Phase Fault with Stuck Breaker on QUINDC 2 69.000 (546695) 69 kV Bus a. Apply Fault at the QUINDC 2 69.000 (546695) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUNCIE 2 (546681) 69.0 kV to QUINDA 2 (546692) 69.0 kV Transmission Circuit #1 b.2. QUINDA 2 (546692) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 b.3. QUINDA 2 (546692) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 b.4. QUINDA 2 (546692) 69.0 kV to QUIND 5 (546652) 161.0 kV Two Winding #1 b.5. EVERETT2 (546682) 69.0 kV to QUINDB 2 (546694) 69.0 kV Transmission Circuit #1 b.6. QUINDB 2 (546694) 69.0 kV to QUINDC 2 (546695) 69.0 kV Transmission Circuit #1 b.7. QUINDB 2 (546694) 69.0 kV to QGEN1 1 (546697) 13.8 kV Two Winding #1 b.8. QUINDC 2 (546695) 69.0 kV to QCT2 1 (546700) 13.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_99 | Single Phase Fault with Stuck Breaker on V WEST2 69.000 (546693) 69 kV Bus a. Apply Fault at the V WEST2 69.000 (546693) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAYWOOD2 (546677) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 b.2. QUINDA 2 (546692) 69.0 kV to V WEST2 (546693) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_100 | Single Phase Fault with Stuck Breaker on CARPENTER 7345.00 (523823) 345 kV Bus a. Apply Fault at the CARPENTER 7345.00 (523823) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.3. CARPENTER 7 (523823) 345.0 kV to HARBNGR7 (531512) 345.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_101 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CARPENTER 7 (523823) 345.0 kV to FINNEY 7 (523853) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_102 | Single Phase Fault with Stuck Breaker on NOVUS1 7345.00 (523112) 345 kV Bus a. Apply Fault at the NOVUS1 7345.00 (523112) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #2 b.2. NOVUS_WND 1 (523107) 4.2 kV to NOVUS1 1 (523109) 34.5 kV Two Winding #1 b.3. NOVUS1 1 (523109) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.4. G06-44-2 (560581) 34.5 kV to NOVUS1 3 (523111) 115.0 kV Two Winding #1 b.5. NOVUS1 3 (523111) 115.0 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1_TR1 1 (523110) 13.8 kV Three Winding #1 b.6. NOVUS1_TR1 1 (523110) 13.8 kV to NOVUS1 7 (523112) 345.0 kV to NOVUS1 3 (523111) 115.0 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_103 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLD_TR21 (523094) 13.2 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLAND 6 (523095) 230.0 kV Three Winding #2 b.3. HITCHLAND 7 (523097) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_104 | Single Phase Fault with Stuck Breaker on GRPLNS-CB2-134.500 (523126) 34.5 kV Bus a. Apply Fault at the GRPLNS-CB2-134.500 (523126) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. NOBLE_TR 1 (523102) 13.8 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_WND 3 (523103) 115.0 kV Three Winding #1 b.3. NOBLE_WND 3 (523103) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.4. NOBLE_WND 3 (523103) 115.0 kV to NOBLE_WND 7 (523101) 345.0 kV to NOBLE_TR 1 (523102) 13.8 kV Three Winding #1 b.5. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-HV2-3 (523131) 115.0 kV Transmission Circuit #1 b.6. GRPLNS-HV4-3 (523130) 115.0 kV to GRPLNS-LV4-1 (523127) 34.5 kV Two Winding #1 b.7. NBLWND-LV2 1 (523128) 34.5 kV to GRPLNS-HV2-3 (523131) 115.0 kV Two Winding #1 b.8. GRPLNS-HV2-3 (523131) 115.0 kV to GRPLNS-LV2-1 (523129) 34.5 kV Two Winding #1 b.9. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-LV4-1 (523127) 34.5 kV Transmission Circuit #1 b.10. GRPLNS-LV4-1 (523127) 34.5 kV to GRPLNS-GT4-1 (523133) 0.5 kV Two Winding #1 b.11. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-LV2-1 (523129) 34.5 kV Transmission Circuit #1 b.12. GRPLNS-LV2-1 (523129) 34.5 kV to GRPLNS-GT2-1 (523132) 0.5 kV Two Winding #1 b.13. GRPLNS-CB4-1 (523124) 34.5 kV to GRPLNS-WT4-1 (523121) 0.6 kV Two Winding #1 b.14. GRPLNS-CB2-1 (523126) 34.5 kV to GRPLNS-WT2-1 (523123) 0.6 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_105 | Single Phase Fault with Stuck Breaker on SPNSPUR_WND134.500 (524294) 34.5 kV Bus a. Apply Fault at the SPNSPUR_WND134.500 (524294) 34.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 b.2. POTTER_TR 1 (523957) 13.2 kV to POTTER_CO 7 (523961) 345.0 kV to POTTER_CO 6 (523959) 230.0 kV Three Winding #1 b.3. POTTER_CO 7 (523961) 345.0 kV to SPNSPUR_WND7 (524296) 345.0 kV Transmission Circuit #1 b.4. POTTER_CO 7 (523961) 345.0 kV to TOLK 7 (525549) 345.0 kV Transmission Circuit #1 b.5. POTTER_CO 7 (523961) 345.0 kV to None Transmission Circuit #1 b.7. SPNSPUR_WND7 (524296) 345.0 kV to SPNSPUR_COL7 (524299) 345.0 kV Transmission Circuit #1 b.8. SPNSPUR_GEN1 (524295) 0.7 kV to SPNSPUR_WND1 (524294) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_106 | Single Phase Fault with Stuck Breaker on BROOKLINE 7345.00 (549984) 345 kV Bus a. Apply Fault at the BROOKLINE 7345.00 (549984) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7MORGAN (300045) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to BROOKLINE 7 (549984) 345.0 kV Transmission Circuit #1 b.3. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF1 1 (549988) 13.2 kV Three Winding #1 b.4. BROOKLINE 7 (549984) 345.0 kV to BROOKLINE 5 (549969) 161.0 kV to BRKLNE XF2 1 (549989) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_107 | Single Phase Fault with Stuck Breaker on GRECCTG_1 20.000 (512614) 20 kV Bus a. Apply Fault at the GRECCTG_1 20.000 (512614) 20 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECCTG_1 (512614) 20.0 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GRECCTG_1 (512614) 20.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_108 | Single Phase Fault with Stuck Breaker on GRECSTG_1 17.500 (512615) 17.5 kV Bus a. Apply Fault at the GRECSTG_1 17.500 (512615) 17.5 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECSTG_1 (512615) 17.5 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GRECSTG_1 (512615) 17.5 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_109 | Single Phase Fault with Stuck Breaker on GRDA17-1 22.800 (512688) 22.79999924 kV Bus a. Apply Fault at the GRDA17-1 22.800 (512688) 22.79999924 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA17-1 (512688) 22.8 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_110 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_111 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_112 | Single Phase Fault with Stuck Breaker on KERR GR5 161.00 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to KERR BRK1 5 (512770) 161.0 kV Transmission Circuit #z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_113 | Single Phase Fault with Stuck Breaker on KERR GR5 161.00 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 b.2. KERR GR5 (512635) 161.0 kV to KERR BRK4 5 (512771) 161.0 kV Transmission Circuit #z0 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_114 | Single Phase Fault with Stuck Breaker on NWMAID5 161.00 (512757) 161 kV Bus a. Apply Fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_115 | Single Phase Fault with Stuck Breaker on NWMAID5 161.00 (512757) 161 kV Bus a. Apply Fault at the NWMAID5 161.00 (512757) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WMAIN ST5 (512742) 161.0 kV to NWMAID5 (512757) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_116 | Single Phase Fault with Stuck Breaker on CLEVLND7 345.00 (512694) 345 kV Bus a. Apply Fault at the CLEVLND7 345.00 (512694) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to CLEVLND7 (512694) 345.0 kV Transmission Circuit #1 b.2. CLEVLND7 (512694) 345.0 kV to CLEVLND 4 (512729) 138.0 kV to CLEVLND1 (512817) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_117 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_118 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_119 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_120 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_121 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_122 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_123 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV1 5 (513593) 161.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV1 5 (513593) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_124 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to IGLOOV2 5 (513595) 161.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 b.5. HERRON 5 (513591) 161.0 kV to IGLOOV2 5 (513595) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_125 | Single Phase Fault with Stuck Breaker on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER1 1 (512833) 13.8 kV Three Winding #1 b.4. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_126 | Single Phase Fault with Stuck Breaker on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATSAGR5 (512638) 161.0 kV to CATOOSA4 (509790) 138.0 kV to CATTER2 1 (512834) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_127 | Single Phase Fault with Stuck Breaker on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_128 | Single Phase Fault with Stuck Breaker on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_129 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_130 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_131 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_132 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_133 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_134 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_135 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 (512821) 13.8 kV Three Winding #1 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_136 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 5 (512656) 161.0 kV to GRDA15-1 (512689) 22.8 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_137 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_138 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_139 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_140 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_141 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_142 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_143 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_144 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.3. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_145 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEVLND7 (512694) 345.0 kV to G15-066T (560056) 345.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_146 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to MAID 2 (512626) 69.0 kV to MAITER2 1 (512837) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_147 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE5 (512751) 161.0 kV to TONNEC2 (512753) 69.0 kV to TONNEC1 (512754) 13.2 kV Three Winding #1 b.4. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_148 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to TONECE5 (512751) 161.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.4. SILMCTY5 (512643) 161.0 kV to TONECE5 (512751) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_149 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to COFCTY2 (512735) 69.0 kV to COFFEY1 (512740) 13.8 kV Three Winding #1 b.4. FARML 4 (512734) 138.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_150 | Single Phase Fault with Stuck Breaker on MIAMI 5 161.00 (512631) 161 kV Bus a. Apply Fault at the MIAMI 5 161.00 (512631) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI1 1 (512843) 13.8 kV Three Winding #1 b.4. MIAMI 5 (512631) 161.0 kV to MIAMI 2 (512630) 69.0 kV to MIAMI2 1 (512844) 13.8 kV Three Winding #2 b.7. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_151 | Single Phase Fault with Stuck Breaker on CLARMR 5 161.00 (512651) 161 kV Bus a. Apply Fault at the CLARMR 5 161.00 (512651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5KETONVL (300997) 161.0 kV to CLARMR 5 (512651) 161.0 kV Transmission Circuit #1 b.2. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.3. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR1 (512814) 13.8 kV Three Winding #1 b.4. CLARMR 5 (512651) 161.0 kV to CLARMR 2 (512679) 69.0 kV to CLARMR2 (512815) 13.8 kV Three Winding #2 b.5. CLARMR 5 (512651) 161.0 kV to CLARMR 4 (512707) 138.0 kV to CLARMR4 (512813) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_152 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA17-1 (512688) 22.8 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_153 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_154 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA2 1 (512826) 13.8 kV Three Winding #2 b.4. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_155 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECSTG_1 (512615) 17.5 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GRDA1 7 (512650) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_156 | Single Phase Fault with Stuck Breaker on GREC TAP5 345.00 (512865) 345 kV Bus a. Apply Fault at the GREC TAP5 345.00 (512865) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRECCTG_1 (512614) 20.0 kV to GREC TAP5 (512865) 345.0 kV Two Winding #1 b.2. GREC TAP5 (512865) 345.0 kV to IGLOOV 7 (513596) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_157 | Single Phase Fault with Stuck Breaker on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_158 | Single Phase Fault with Stuck Breaker on DRYGULCH5 161.00 (512629) 161 kV Bus a. Apply Fault at the DRYGULCH5 161.00 (512629) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. DRYGULCH5 (512629) 161.0 kV to PENSA 5 (512654) 161.0 kV Transmission Circuit #1 b.3. DRYGULCH5 (512629) 161.0 kV to GEN-2017-073 (589110) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_159 | Single Phase Fault with Stuck Breaker on GERALDGAY5 161.00 (512760) 161 kV Bus a. Apply Fault at the GERALDGAY5 161.00 (512760) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. NWMAID5 (512757) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_160 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_161 | Single Phase Fault with Stuck Breaker on WAGNOR 5 161.00 (512700) 161 kV Bus a. Apply Fault at the WAGNOR 5 161.00 (512700) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARMR 5 (512651) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. OKAYGR 5 (512640) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.3. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 b.4. WAGNOR 5 (512700) 161.0 kV to WAGNOR 2 (512697) 69.0 kV to WAGNOR1 (512818) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_162 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 b.2. GRDA1 5 (512656) 161.0 kV to GRDA1 2 (512727) 69.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_163 | Single Phase Fault with Stuck Breaker on KERR GR5 161.00 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_164 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 b.2. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_165 | Single Phase Fault with Stuck Breaker on CATSAGR5 161.00 (512638) 161 kV Bus a. Apply Fault at the CATSAGR5 161.00 (512638) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. CATSAGR5 (512638) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_166 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GRDA1 5 (512656) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_167 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DRYGULCH5 (512629) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. 5CDRCRST (301344) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 b.3. MAID 5 (512648) 161.0 kV to LOCSTGVKM 5 (513050) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_168 | Single Phase Fault with Stuck Breaker on KERR GR5 161.00 (512635) 161 kV Bus a. Apply Fault at the KERR GR5 161.00 (512635) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. KERR GR5 (512635) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_169 | Single Phase Fault with Stuck Breaker on AFTON 5 161.00 (512632) 161 kV Bus a. Apply Fault at the AFTON 5 161.00 (512632) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIAMI 5 (512631) 161.0 kV to HOC404 5 (547487) 161.0 kV Transmission Circuit #1 b.2. MIAMI 5 (512631) 161.0 kV to AFTON 5 (512632) 161.0 kV Transmission Circuit #1 b.3. AFTON 5 (512632) 161.0 kV to KETCHUM5 (512669) 161.0 kV Transmission Circuit #1 b.4. AFTON 5 (512632) 161.0 kV to AFTON 2 (512633) 69.0 kV to AFTON1 (512845) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_170 | Single Phase Fault with Stuck Breaker on RIVRSID5 161.00 (543021) 161 kV Bus a. Apply Fault at the RIVRSID5 161.00 (543021) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIVRSID5 (543021) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. RIVRSID5 (543021) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 b.3. NE CT11 (542958) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT12 (542959) 13.8 kV Three Winding #1 b.4. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_171 | Single Phase Fault with Stuck Breaker on NEASTN5 161.00 (543666) 161 kV Bus a. Apply Fault at the NEASTN5 161.00 (543666) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. LEVEE 5 (542976) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.3. NE CT13 (542970) 13.8 kV to NEASTN5 (543666) 161.0 kV to NE CT14 (542971) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_172 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_173 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PECULR 7 (541198) 345.0 kV to PHILL 7 (541200) 345.0 kV Transmission Circuit #1 b.3. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_174 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.3. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.4. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.5. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_175 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHOUTEU5 (543011) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_176 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_177 | Single Phase Fault with Stuck Breaker on HAW G5 1 22.000 (542951) 22 kV Bus a. Apply Fault at the HAW G5 1 22.000 (542951) 22 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. RANDLPH5 (543027) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.3. HAW G5 1 (542951) 22.0 kV to Generator # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_178 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_179 | Single Phase Fault with Stuck Breaker on NEASTS_CAP5 161.00 (542948) 161 kV Bus a. Apply Fault at the NEASTS_CAP5 161.00 (542948) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.3. NE CT15 (542974) 13.8 kV to NEASTS5 (542985) 161.0 kV to NE CT16 (542975) 13.8 kV Three Winding #1 b.4. NEASTS_CAP5 (542948) 161.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_180 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to RICE 3 (530623) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_181 | Single Phase Fault with Stuck Breaker on LYONS 3 115.00 (530620) 115 kV Bus a. Apply Fault at the LYONS 3 115.00 (530620) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LYONS 3 (530620) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.2. WMCPHER3 (533438) 115.0 kV to WHEATLD3 (533439) 115.0 kV Transmission Circuit #1 b.3. LYONS 3 (530620) 115.0 kV to SAXMAN 3 (530711) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_182 | Single Phase Fault with Stuck Breaker on PAWN-ED3 115.00 (530622) 115 kV Bus a. Apply Fault at the PAWN-ED3 115.00 (530622) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARDS3 (530617) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.2. EDWARDS3 (530617) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.3. KINSLEY3 (530619) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.4. PAWNEE 3 (530621) 115.0 kV to PAWN-ED3 (530622) 115.0 kV Transmission Circuit #1 b.5. KINSLEY3 (530619) 115.0 kV to GEN-2016-016 (587120) 115.0 kV Transmission Circuit #1 b.6. PAWNEE 3 (530621) 115.0 kV to LARNED3 (530685) 115.0 kV Transmission Circuit #1 b.7. HUNTSVL3 (530618) 115.0 kV to ST JOHN3 (530624) 115.0 kV Transmission Circuit #1 b.8. ST JOHN3 (530624) 115.0 kV to ST-JOHN3 (539696) 115.0 kV Transmission Circuit #z1 b.9. HUNTSVL3 (530618) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.10. ARKVAL 3 (533411) 115.0 kV to ARKVALJ3 (533412) 115.0 kV Transmission Circuit #1 b.11. ARKVALJ3 (533412) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_183 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S HAYS6 (530582) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_184 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.4. KNOLL N 6 (530558) 230.0 kV to POSTROCK6 (530584) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_185 | Single Phase Fault with Stuck Breaker on GRTBEND6 230.00 (539679) 230 kV Bus a. Apply Fault at the GRTBEND6 230.00 (539679) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEIZER 6 (530680) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. GRTBEND6 (539679) 230.0 kV to SPEARVL6 (539695) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_186 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_187 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.5. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_188 | Single Phase Fault with Stuck Breaker on REDWILO3 345.00 (640325) 345 kV Bus a. Apply Fault at the REDWILO3 345.00 (640325) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.3. REDWILO7 (640326) 115.0 kV to REDWILO3 (640325) 345.0 kV to REDWILO9 (640327) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_189 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MCCOOL 3 (640271) 345.0 kV to MOORE 3 (640277) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_190 | Single Phase Fault with Stuck Breaker on MOORE 3 345.00 (640277) 345 kV Bus a. Apply Fault at the MOORE 3 345.00 (640277) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORE 3 (640277) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. MOORE 3 (640277) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_191 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ST JOE 7 (541199) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. ATCHSN 3 (635017) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_192 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to COOPER1G (640009) 22.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_193 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_194 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_195 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_196 | Single Phase Fault with Stuck Breaker on MONOLITH 3 345.00 (640590) 345 kV Bus a. Apply Fault at the MONOLITH 3 345.00 (640590) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to MONOLITH 3 (640590) 345.0 kV Transmission Circuit #1 b.2. MONOLITH 7 (640591) 115.0 kV to MONOLITH 3 (640590) 345.0 kV to MONOLITHT2 9 (640597) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_197 | Single Phase Fault with Stuck Breaker on 7FAIRPT 345.00 (300039) 345 kV Bus a. Apply Fault at the 7FAIRPT 345.00 (300039) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T5 9 (643172) 13.8 kV Three Winding #1 b.4. 7FAIRPT (300039) 345.0 kV to COOPER 3 (640139) 345.0 kV Transmission Circuit #1 b.5. 7FAIRPT (300039) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.6. 5FAIRPTXF3 (301559) 161.0 kV to 7FAIRPT (300039) 345.0 kV Two Winding #3 b.7. 5FAIRPTB2 (300076) 161.0 kV to 5FAIRPTXF3 (301559) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_198 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_199 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3451 3 (645451) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_200 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_201 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_202 | Single Phase Fault with Stuck Breaker on S1254 5 161.00 (646254) 161 kV Bus a. Apply Fault at the S1254 5 161.00 (646254) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to S1254 5 (646254) 161.0 kV to S1254T19 (648254) 13.8 kV Three Winding #1 b.4. S1249 5 (646249) 161.0 kV to S1254 5 (646254) 161.0 kV Transmission Circuit #1 b.5. S1254 5 (646254) 161.0 kV to S1281 5 (646281) 161.0 kV Transmission Circuit #1 b.6. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_203 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_204 | Single Phase Fault with Stuck Breaker on S3454 3 345.00 (645454) 345 kV Bus a. Apply Fault at the S3454 3 345.00 (645454) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3454 3 (645454) 345.0 kV to WAGENER 3 (650185) 345.0 kV Transmission Circuit #1 b.2. S3454 3 (645454) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_205 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_206 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_207 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 b.4. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_208 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_209 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_210 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_211 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_212 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_213 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_214 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_215 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_216 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_217 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_218 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_219 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 b.4. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_220 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_221 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to S3456 3 (645456) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_222 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_223 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_224 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_225 | Single Phase Fault with Stuck Breaker on S3459 3 345.00 (645459) 345 kV Bus a. Apply Fault at the S3459 3 345.00 (645459) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3456 3 (645456) 345.0 kV to S3459 3 (645459) 345.0 kV Transmission Circuit #1 b.2. S3459 3 (645459) 345.0 kV to S1209 5 (646209) 161.0 kV to S3459T69 (648359) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_226 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_227 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_228 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_229 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3740 3 (645740) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to CASS 2G (645042) 15.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_230 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_231 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_232 | Single Phase Fault with Stuck Breaker on S3761 3 345.00 (645761) 345 kV Bus a. Apply Fault at the S3761 3 345.00 (645761) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3455 3 (645455) 345.0 kV to S3761 3 (645761) 345.0 kV Transmission Circuit #1 b.2. S3761 3 (645761) 345.0 kV to S1361 5 (646361) 161.0 kV to S3761T19 (648261) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_233 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_234 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_235 | Single Phase Fault with Stuck Breaker on S3456 3 345.00 (645456) 345 kV Bus a. Apply Fault at the S3456 3 345.00 (645456) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_236 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_237 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_238 | Single Phase Fault with Stuck Breaker on S1216 5 161.00 (646216) 161 kV Bus a. Apply Fault at the S1216 5 161.00 (646216) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1206 5 (646206) 161.0 kV to S1216 5 (646216) 161.0 kV Transmission Circuit #1 b.2. S3456 3 (645456) 345.0 kV to S1206 5 (646206) 161.0 kV to S3456T49 (648256) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_239 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_240 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_241 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1221 5 (646221) 161.0 kV to S1255 5 (646255) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T19 (648255) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_242 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_243 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_244 | Single Phase Fault with Stuck Breaker on S3455 3 345.00 (645455) 345 kV Bus a. Apply Fault at the S3455 3 345.00 (645455) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S1255 5 (646255) 161.0 kV to S1259 5 (646259) 161.0 kV Transmission Circuit #1 b.2. S3455 3 (645455) 345.0 kV to S1255 5 (646255) 161.0 kV to S3455T39 (648355) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_245 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_246 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_247 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_248 | Single Phase Fault with Stuck Breaker on BVRCNTY7 345.00 (515554) 345 kV Bus a. Apply Fault at the BVRCNTY7 345.00 (515554) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BVRCNTY7 (515554) 345.0 kV to PALDR2W7 (515590) 345.0 kV Transmission Circuit #1 b.2. BVRCNTY7 (515554) 345.0 kV to HITCHLAND 7 (523097) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_249 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_250 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_251 | Single Phase Fault with Stuck Breaker on DGRASSE4 138.00 (515853) 138 kV Bus a. Apply Fault at the DGRASSE4 138.00 (515853) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 b.2. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_252 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_253 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_254 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.4. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_255 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_256 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_257 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_258 | Single Phase Fault with Stuck Breaker on GRANTCO4 138.00 (515546) 138 kV Bus a. Apply Fault at the GRANTCO4 138.00 (515546) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLYDE 2 (514719) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.2. MEDFORD2 (514739) 69.0 kV to GRANTCO2 (515547) 69.0 kV Transmission Circuit #1 b.3. GRANTCO2 (515547) 69.0 kV to GRANTCO4 (515546) 138.0 kV to GRANTC11 (515548) 13.2 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_259 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_260 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_261 | Single Phase Fault with Stuck Breaker on HUNTERS7 345.00 (515476) 345 kV Bus a. Apply Fault at the HUNTERS7 345.00 (515476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to CHSHLMV7 (515477) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_262 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALVAOGE2 (514792) 69.0 kV to KNOBHIL2 (514794) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 b.3. KNOBHIL2 (514794) 69.0 kV to KNOBHIL4 (514795) 138.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 b.4. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.5. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #1 b.6. KNOBHIL4 (514795) 138.0 kV to NOELSW 4 (520430) 138.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_263 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_264 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_265 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW4 (515544) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_266 | Single Phase Fault with Stuck Breaker on RENFROW4 138.00 (515544) 138 kV Bus a. Apply Fault at the RENFROW4 138.00 (515544) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to WFEC_RNFRO4 (520409) 138.0 kV Transmission Circuit #1 b.2. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_267 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 b.2. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_268 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. HUNTERS7 (515476) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_269 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to GRNTWD 7 (515646) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_270 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.4. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_271 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to COYOTE 4 (515581) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_272 | Single Phase Fault with Stuck Breaker on RDRUNNR4 138.00 (515426) 138 kV Bus a. Apply Fault at the RDRUNNR4 138.00 (515426) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RDRUNNR4 (515426) 138.0 kV to MDFRDTP4 (515569) 138.0 kV Transmission Circuit #1 b.2. RDRUNNR4 (515426) 138.0 kV to RCKFALL4 (515427) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_273 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MAMTHPW7 (515585) 345.0 kV Transmission Circuit #1 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_274 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to SLNGWND7 (515582) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_275 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_276 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to FPLWIND4 (515786) 138.0 kV Transmission Circuit #1 b.2. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_277 | Single Phase Fault with Stuck Breaker on WINDFRM4 138.00 (515785) 138 kV Bus a. Apply Fault at the WINDFRM4 138.00 (515785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINDFRM4 (515785) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_278 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG4 (514714) 138.0 kV to WOODRNG7 (514715) 345.0 kV to WOODRNG1 (515770) 13.8 kV Three Winding #1 b.4. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_279 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.2. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_280 | Single Phase Fault with Stuck Breaker on WOODWRD4 138.00 (514785) 138 kV Bus a. Apply Fault at the WOODWRD4 138.00 (514785) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEWGRTP2 (514776) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.2. CEDARAV2 (514781) 69.0 kV to WODWRD 2 (514782) 69.0 kV Transmission Circuit #1 b.3. WODWRD 2 (514782) 69.0 kV to WOODWRD2 (521096) 69.0 kV Transmission Circuit #1 b.4. WODWRD 2 (514782) 69.0 kV to WOODWRD4 (514785) 138.0 kV to WOODWR21 (515771) 13.2 kV Three Winding #1 b.5. WOODWRD4 (514785) 138.0 kV to CENT 4 (515363) 138.0 kV Transmission Circuit #1 b.6. WOODWRD4 (514785) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #2 b.7. WOODWRD4 (514785) 138.0 kV to WINDFRM4 (515785) 138.0 kV Transmission Circuit #1 b.8. WWDPST 4 (515425) 138.0 kV to WOODWRD4 (514785) 138.0 kV Transmission Circuit #8 b.10. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_281 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_282 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV31 (515795) 13.8 kV Three Winding #1 b.4. WWRDEHV7 (515375) 345.0 kV to TATONGA7 (515407) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_283 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to GUTHRIE7 (515961) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_284 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 b.4. IODINE-4 (514796) 138.0 kV to WWRDEHV4 (515376) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_285 | Single Phase Fault with Stuck Breaker on WWRDEHV4 138.00 (515376) 138 kV Bus a. Apply Fault at the WWRDEHV4 138.00 (515376) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to OUSPRT 4 (515398) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV4 (515376) 138.0 kV to WWDPST 4 (515425) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_286 | Single Phase Fault with Stuck Breaker on WOODRNG7 345.00 (514715) 345 kV Bus a. Apply Fault at the WOODRNG7 345.00 (514715) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOODRNG7 (514715) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 b.2. WOODRNG7 (514715) 345.0 kV to PINTAIL7 (516010) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_287 | Single Phase Fault with Stuck Breaker on 5CHOTEAU1 161.00 (300069) 161 kV Bus a. Apply Fault at the 5CHOTEAU1 161.00 (300069) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU1 (300069) 161.0 kV to MAID 5 (512648) 161.0 kV Transmission Circuit #1 b.2. 5CHOTEAU1 (300069) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_288 | Single Phase Fault with Stuck Breaker on 7BLACKBERRY 345.00 (300739) 345 kV Bus a. Apply Fault at the 7BLACKBERRY 345.00 (300739) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7BLACKBERRY (300739) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 b.2. 7BLACKBERRY (300739) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_289 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5SPORTSMAN (300741) 161.0 kV to 5CHOTEAU2 (301348) 161.0 kV Transmission Circuit #1 b.2. 5SPORTSMAN (300741) 161.0 kV to 7SPORTSMAN (300740) 345.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_290 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7JASPER (300949) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. 7JASPER (300949) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_291 | Single Phase Fault with Stuck Breaker on CHISHOLM7 345.00 (511553) 345 kV Bus a. Apply Fault at the CHISHOLM7 345.00 (511553) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM7 (511553) 345.0 kV to G16-037-TAP (560078) 345.0 kV Transmission Circuit #1 b.2. CHISHOLM7 (511553) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_292 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV7 (515375) 345.0 kV to WWDBORDT (755000) 345.0 kV Transmission Circuit #1 b.2. WWRDEHV7 (515375) 345.0 kV to DGRASSE7 (515852) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_293 | Single Phase Fault with Stuck Breaker on TATONGA7 345.00 (515407) 345 kV Bus a. Apply Fault at the TATONGA7 345.00 (515407) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #2 b.2. TATONGA7 (515407) 345.0 kV to MATHWSN7 (515497) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_294 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW7 (515543) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #1 b.2. RENFROW7 (515543) 345.0 kV to HUNTERS7 (515476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_295 | Single Phase Fault with Stuck Breaker on G07621119-20345.00 (515599) 345 kV Bus a. Apply Fault at the G07621119-20345.00 (515599) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G07621119-20 (515599) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. G07621119-20 (515599) 345.0 kV to GREAT_WESTRN (585410) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_296 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE4 (515853) 138.0 kV to DGRASSE7 (515852) 345.0 kV to DGRASSE1 (515854) 13.8 kV Three Winding #1 b.2. DGRASSE4 (515853) 138.0 kV to ROSEVLY4 (520436) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_297 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND4 (520999) 138.0 kV to PIC4 (520425) 138.0 kV Transmission Circuit #1 b.2. MOORLND4 (520999) 138.0 kV to ASPEN 4 (520462) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_298 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 7 (523097) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 b.2. HITCHLAND 7 (523097) 345.0 kV to POTTER_CO 7 (523961) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_299 | Single Phase Fault with Stuck Breaker on FINNEY 7345.00 (523853) 345 kV Bus a. Apply Fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 b.2. FINNEY 7 (523853) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_300 | Single Phase Fault with Stuck Breaker on WALKMYR3 115.00 (531405) 115 kV Bus a. Apply Fault at the WALKMYR3 115.00 (531405) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WALKMYR3 (531405) 115.0 kV to HUGOTON3 (531481) 115.0 kV Transmission Circuit #1 b.2. WALKMYR3 (531405) 115.0 kV to HARBNGR3 (531510) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_301 | Single Phase Fault with Stuck Breaker on SCOTCTY3 115.00 (531433) 115 kV Bus a. Apply Fault at the SCOTCTY3 115.00 (531433) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SCOTCTY3 (531433) 115.0 kV to SETAB 3 (531464) 115.0 kV Transmission Circuit #1 b.2. SCOTCTY3 (531433) 115.0 kV to MANNGT 3 (531362) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_302 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 7 (531451) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. MINGO 7 (531451) 345.0 kV to SETAB 7 (531465) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_303 | Single Phase Fault with Stuck Breaker on EMPEC 7 345.00 (532768) 345 kV Bus a. Apply Fault at the EMPEC 7 345.00 (532768) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EMPEC 7 (532768) 345.0 kV to EXPEDITION7 (532803) 345.0 kV Transmission Circuit #1 b.2. EMPEC 7 (532768) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_304 | Single Phase Fault with Stuck Breaker on RENO 7 345.00 (532771) 345 kV Bus a. Apply Fault at the RENO 7 345.00 (532771) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENO 7 (532771) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. RENO 7 (532771) 345.0 kV to RENO 3 (533416) 115.0 kV to RENO 2X1 (532810) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_305 | Single Phase Fault with Stuck Breaker on SUMMIT 7 345.00 (532773) 345 kV Bus a. Apply Fault at the SUMMIT 7 345.00 (532773) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUMMIT 7 (532773) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 b.2. SUMMIT 7 (532773) 345.0 kV to SUMMIT 6 (532873) 230.0 kV to SUMMIT 1 (532813) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_306 | Single Phase Fault with Stuck Breaker on SWISVAL7 345.00 (532774) 345 kV Bus a. Apply Fault at the SWISVAL7 345.00 (532774) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL7 (532774) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. SWISVAL7 (532774) 345.0 kV to GEN-2017-125 (761901) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_307 | Single Phase Fault with Stuck Breaker on G17-009-TAP 345.00 (532777) 345 kV Bus a. Apply Fault at the G17-009-TAP 345.00 (532777) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-009-TAP (532777) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. G17-009-TAP (532777) 345.0 kV to CANEYRV7 (532780) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_308 | Single Phase Fault with Stuck Breaker on BUFFALO7 345.00 (532782) 345 kV Bus a. Apply Fault at the BUFFALO7 345.00 (532782) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 b.2. BUFFALO7 (532782) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_309 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 7 (532791) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. BENTON 7 (532791) 345.0 kV to BENTON 4 (532986) 138.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_310 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 7 (532793) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. NEOSHO 7 (532793) 345.0 kV to NEOSHO 5 (532937) 161.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_311 | Single Phase Fault with Stuck Breaker on ROSEHIL7 345.00 (532794) 345 kV Bus a. Apply Fault at the ROSEHIL7 345.00 (532794) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL7 (532794) 345.0 kV to WOLFCRK7 (532797) 345.0 kV Transmission Circuit #1 b.2. ROSEHIL7 (532794) 345.0 kV to ROSEHIL4 (533062) 138.0 kV to ROSEH5 1 (532827) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_312 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. WICHITA7 (532796) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_313 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 7 (532798) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. VIOLA 7 (532798) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_314 | Single Phase Fault with Stuck Breaker on CLEARWT4 138.00 (533036) 138 kV Bus a. Apply Fault at the CLEARWT4 138.00 (533036) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLEARWT4 (533036) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. CLEARWT4 (533036) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_315 | Single Phase Fault with Stuck Breaker on WICHITA7 345.00 (532796) 345 kV Bus a. Apply Fault at the WICHITA7 345.00 (532796) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH12 1 (532830) 13.8 kV Three Winding #1 b.2. EVANS N4 (533040) 138.0 kV to WICHITA7 (532796) 345.0 kV to WICH11 1 (532829) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_316 | Single Phase Fault with Stuck Breaker on REFINRY3 115.00 (533427) 115 kV Bus a. Apply Fault at the REFINRY3 115.00 (533427) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REFINRY3 (533427) 115.0 kV to EMCPHER3 (533417) 115.0 kV Transmission Circuit #1 b.2. REFINRY3 (533427) 115.0 kV to MCPHER 3 (533428) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_317 | Single Phase Fault with Stuck Breaker on MOUNDRG3 115.00 (533429) 115 kV Bus a. Apply Fault at the MOUNDRG3 115.00 (533429) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUNDRG3 (533429) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. MOUNDRG3 (533429) 115.0 kV to SPRGCRK3 (533380) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_318 | Single Phase Fault with Stuck Breaker on FLATRDG4 138.00 (539638) 138 kV Bus a. Apply Fault at the FLATRDG4 138.00 (539638) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLATRDG4 (539638) 138.0 kV to HARPER 4 (539668) 138.0 kV Transmission Circuit #1 b.2. FLATRDG4 (539638) 138.0 kV to THISTLE4 (539804) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_319 | Single Phase Fault with Stuck Breaker on MED-LDG3 115.00 (539673) 115 kV Bus a. Apply Fault at the MED-LDG3 115.00 (539673) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MED-LDG3 (539673) 115.0 kV to SUNCITY3 (539697) 115.0 kV Transmission Circuit #1 b.2. MED-LDG3 (539673) 115.0 kV to BARBER 3 (539760) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_320 | Single Phase Fault with Stuck Breaker on CLARKCOUNTY7345.00 (539800) 345 kV Bus a. Apply Fault at the CLARKCOUNTY7345.00 (539800) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. CLARKCOUNTY7 (539800) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_321 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. THISTLE7 (539801) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_322 | Single Phase Fault with Stuck Breaker on IRONWOOD7 345.00 (539803) 345 kV Bus a. Apply Fault at the IRONWOOD7 345.00 (539803) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IRONWOOD7 (539803) 345.0 kV to G16-046-TAP (560080) 345.0 kV Transmission Circuit #1 b.2. IRONWOOD7 (539803) 345.0 kV to SPERVIL7 (531469) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_323 | Single Phase Fault with Stuck Breaker on MULLNCR7 345.00 (541197) 345 kV Bus a. Apply Fault at the MULLNCR7 345.00 (541197) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MULLNCR7 (541197) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. MULLNCR7 (541197) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_324 | Single Phase Fault with Stuck Breaker on NASHUA 5 161.00 (541203) 161 kV Bus a. Apply Fault at the NASHUA 5 161.00 (541203) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 5 (541203) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #z1 b.2. NASHUA 5 (541203) 161.0 kV to LBRTYWT5 (541247) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_325 | Single Phase Fault with Stuck Breaker on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply Fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCTY5 (541210) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. MARTCTY5 (541210) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_326 | Single Phase Fault with Stuck Breaker on TWA 5 161.00 (541214) 161 kV Bus a. Apply Fault at the TWA 5 161.00 (541214) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TWA 5 (541214) 161.0 kV to FRLVW 5 (541213) 161.0 kV Transmission Circuit #1 b.2. TWA 5 (541214) 161.0 kV to NCONGRS5 (541318) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_327 | Single Phase Fault with Stuck Breaker on RAYTOWN5 161.00 (541219) 161 kV Bus a. Apply Fault at the RAYTOWN5 161.00 (541219) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RAYTOWN5 (541219) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 b.2. RAYTOWN5 (541219) 161.0 kV to LKWOOD 5 (541238) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_328 | Single Phase Fault with Stuck Breaker on FROSTRD5 161.00 (541220) 161 kV Bus a. Apply Fault at the FROSTRD5 161.00 (541220) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FROSTRD5 (541220) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 b.2. FROSTRD5 (541220) 161.0 kV to FROSTRD_CAP5 (541139) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_329 | Single Phase Fault with Stuck Breaker on WSTELEC5 161.00 (541222) 161 kV Bus a. Apply Fault at the WSTELEC5 161.00 (541222) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WSTELEC5 (541222) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 b.2. WSTELEC5 (541222) 161.0 kV to WSTELEC_CAP5 (541149) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_330 | Single Phase Fault with Stuck Breaker on GRDVWE 5 161.00 (541223) 161 kV Bus a. Apply Fault at the GRDVWE 5 161.00 (541223) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDVWE 5 (541223) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 b.2. GRDVWE 5 (541223) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_331 | Single Phase Fault with Stuck Breaker on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply Fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 5 (541224) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 b.2. LNGVW 5 (541224) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_332 | Single Phase Fault with Stuck Breaker on PHILL 5 161.00 (541225) 161 kV Bus a. Apply Fault at the PHILL 5 161.00 (541225) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 5 (541225) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. PHILL 5 (541225) 161.0 kV to HARRIS (541313) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_333 | Single Phase Fault with Stuck Breaker on RNRIDGE5 161.00 (541230) 161 kV Bus a. Apply Fault at the RNRIDGE5 161.00 (541230) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RNRIDGE5 (541230) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. RNRIDGE5 (541230) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_334 | Single Phase Fault with Stuck Breaker on G18-054-TAP 161.00 (541231) 161 kV Bus a. Apply Fault at the G18-054-TAP 161.00 (541231) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G18-054-TAP (541231) 161.0 kV to NRAYMORE (541317) 161.0 kV Transmission Circuit #1 b.2. G18-054-TAP (541231) 161.0 kV to KCSOUTH5 (541245) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_335 | Single Phase Fault with Stuck Breaker on LKWINBG5 161.00 (541243) 161 kV Bus a. Apply Fault at the LKWINBG5 161.00 (541243) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LKWINBG5 (541243) 161.0 kV to PHILL 5 (541225) 161.0 kV Transmission Circuit #1 b.2. LKWINBG5 (541243) 161.0 kV to HOOKRD 5 (541249) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_336 | Single Phase Fault with Stuck Breaker on LBRTYST5 161.00 (541248) 161 kV Bus a. Apply Fault at the LBRTYST5 161.00 (541248) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LBRTYST5 (541248) 161.0 kV to BRMGHAM5 (543020) 161.0 kV Transmission Circuit #1 b.2. LBRTYST5 (541248) 161.0 kV to LIBRTYS2 (543095) 69.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_337 | Single Phase Fault with Stuck Breaker on LNGVW 5 161.00 (541224) 161 kV Bus a. Apply Fault at the LNGVW 5 161.00 (541224) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LNGVW 2 (541282) 69.0 kV to LNGVW 5 (541224) 161.0 kV Two Winding #1 b.2. LNGVW 2 (541282) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_338 | Single Phase Fault with Stuck Breaker on GRDVWTP2 69.000 (541284) 69 kV Bus a. Apply Fault at the GRDVWTP2 69.000 (541284) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDVWTP2 (541284) 69.0 kV to LNGVW 2 (541282) 69.0 kV Transmission Circuit #1 b.2. GRDVWTP2 (541284) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_339 | Single Phase Fault with Stuck Breaker on GRDWCTY2 69.000 (541285) 69 kV Bus a. Apply Fault at the GRDWCTY2 69.000 (541285) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDWCTY2 (541285) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. GRDWCTY2 (541285) 69.0 kV to GRDWST 2 (541286) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_340 | Single Phase Fault with Stuck Breaker on GRDWST 2 69.000 (541286) 69 kV Bus a. Apply Fault at the GRDWST 2 69.000 (541286) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDWST 2 (541286) 69.0 kV to MARTCTY2 (541287) 69.0 kV Transmission Circuit #1 b.2. GRDWST 2 (541286) 69.0 kV to GRDWCTY2 (541285) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_341 | Single Phase Fault with Stuck Breaker on NRAYMORE 161.00 (541317) 161 kV Bus a. Apply Fault at the NRAYMORE 161.00 (541317) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NRAYMORE (541317) 161.0 kV to G18-054-TAP (541231) 161.0 kV Transmission Circuit #1 b.2. NRAYMORE (541317) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_342 | Single Phase Fault with Stuck Breaker on KETCHEM7 345.00 (541500) 345 kV Bus a. Apply Fault at the KETCHEM7 345.00 (541500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KETCHEM7 (541500) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. KETCHEM7 (541500) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_343 | Single Phase Fault with Stuck Breaker on HOLT 7 345.00 (541510) 345 kV Bus a. Apply Fault at the HOLT 7 345.00 (541510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT 7 (541510) 345.0 kV to MULLNCR7 (541197) 345.0 kV Transmission Circuit #1 b.2. HOLT 7 (541510) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_344 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. W.GRDNR7 (542965) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. W.GRDNR7 (542965) 345.0 kV to WGARDNR5 (542966) 161.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_345 | Single Phase Fault with Stuck Breaker on W.GRDNR7 345.00 (542965) 345 kV Bus a. Apply Fault at the W.GRDNR7 345.00 (542965) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WGARDNR5 (542966) 161.0 kV to W.GRDNR7 (542965) 345.0 kV to WGAR T11 (543649) 13.8 kV Three Winding #11 b.2. WGARDNR5 (542966) 161.0 kV to BNSF 5 (543132) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_346 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T22 (543648) 13.8 kV Three Winding #22 b.2. STILWEL5 (542969) 161.0 kV to STILWEL7 (542968) 345.0 kV to STIL T11 (543647) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_347 | Single Phase Fault with Stuck Breaker on HAWTHS5 161.00 (542973) 161 kV Bus a. Apply Fault at the HAWTHS5 161.00 (542973) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS5 (542973) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_348 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA 7 (542980) 345.0 kV to IATAN 7 (542982) 345.0 kV Transmission Circuit #1 b.2. NASHUA 7 (542980) 345.0 kV to HAWTH 7 (542972) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_349 | Single Phase Fault with Stuck Breaker on LACYGNE7 345.00 (542981) 345 kV Bus a. Apply Fault at the LACYGNE7 345.00 (542981) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LACYGNE7 (542981) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 b.2. LACYGNE7 (542981) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_350 | Single Phase Fault with Stuck Breaker on TROOST 5 161.00 (542986) 161 kV Bus a. Apply Fault at the TROOST 5 161.00 (542986) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TROOST 5 (542986) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. TROOST 5 (542986) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_351 | Single Phase Fault with Stuck Breaker on GRAND 5 161.00 (542987) 161 kV Bus a. Apply Fault at the GRAND 5 161.00 (542987) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND 5 (542987) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 b.2. GRAND 5 (542987) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_352 | Single Phase Fault with Stuck Breaker on GRAND W5 161.00 (542988) 161 kV Bus a. Apply Fault at the GRAND W5 161.00 (542988) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRAND W5 (542988) 161.0 kV to CROSTWN5 (542990) 161.0 kV Transmission Circuit #1 b.2. GRAND W5 (542988) 161.0 kV to NEASTS5 (542985) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_353 | Single Phase Fault with Stuck Breaker on NAVY 5 161.00 (542989) 161 kV Bus a. Apply Fault at the NAVY 5 161.00 (542989) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NAVY 5 (542989) 161.0 kV to GRAND 5 (542987) 161.0 kV Transmission Circuit #1 b.2. NAVY 5 (542989) 161.0 kV to TERRACE5 (542991) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_354 | Single Phase Fault with Stuck Breaker on CROSTWN5 161.00 (542990) 161 kV Bus a. Apply Fault at the CROSTWN5 161.00 (542990) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CROSTWN5 (542990) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. CROSTWN5 (542990) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_355 | Single Phase Fault with Stuck Breaker on BENDIX 5 161.00 (542992) 161 kV Bus a. Apply Fault at the BENDIX 5 161.00 (542992) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENDIX 5 (542992) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. BENDIX 5 (542992) 161.0 kV to TOMHAWK5 (543035) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_356 | Single Phase Fault with Stuck Breaker on STHTOWN5 161.00 (542993) 161 kV Bus a. Apply Fault at the STHTOWN5 161.00 (542993) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STHTOWN5 (542993) 161.0 kV to BENDIX 5 (542992) 161.0 kV Transmission Circuit #1 b.2. STHTOWN5 (542993) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_357 | Single Phase Fault with Stuck Breaker on MIDTOWN5 161.00 (542996) 161 kV Bus a. Apply Fault at the MIDTOWN5 161.00 (542996) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDTOWN5 (542996) 161.0 kV to TROOST 5 (542986) 161.0 kV Transmission Circuit #1 b.2. MIDTOWN5 (542996) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_358 | Single Phase Fault with Stuck Breaker on LEEDS 5 161.00 (542997) 161 kV Bus a. Apply Fault at the LEEDS 5 161.00 (542997) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. LEEDS 5 (542997) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_359 | Single Phase Fault with Stuck Breaker on LVISTA 5 161.00 (542998) 161 kV Bus a. Apply Fault at the LVISTA 5 161.00 (542998) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LVISTA 5 (542998) 161.0 kV to WINJT N5 (543009) 161.0 kV Transmission Circuit #1 b.2. LVISTA 5 (542998) 161.0 kV to FROSTRD5 (541220) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_360 | Single Phase Fault with Stuck Breaker on BLUEVLY5 161.00 (543000) 161 kV Bus a. Apply Fault at the BLUEVLY5 161.00 (543000) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #1 b.2. BLUEVLY5 (543000) 161.0 kV to HAWTHN5 (543665) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_361 | Single Phase Fault with Stuck Breaker on MARTCIT5 161.00 (543002) 161 kV Bus a. Apply Fault at the MARTCIT5 161.00 (543002) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCIT5 (543002) 161.0 kV to REDEL 5 (543053) 161.0 kV Transmission Circuit #1 b.2. MARTCIT5 (543002) 161.0 kV to MARTCTY5 (541210) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_362 | Single Phase Fault with Stuck Breaker on AVONDAL5 161.00 (543015) 161 kV Bus a. Apply Fault at the AVONDAL5 161.00 (543015) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AVONDAL5 (543015) 161.0 kV to RANDLPH5 (543027) 161.0 kV Transmission Circuit #1 b.2. AVONDAL5 (543015) 161.0 kV to NKANCTY5 (543018) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_363 | Single Phase Fault with Stuck Breaker on GLADSTN5 161.00 (543016) 161 kV Bus a. Apply Fault at the GLADSTN5 161.00 (543016) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLADSTN5 (543016) 161.0 kV to SHOLCRK5 (543029) 161.0 kV Transmission Circuit #1 b.2. GLADSTN5 (543016) 161.0 kV to GLADSTN_CAP5 (542946) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_364 | Single Phase Fault with Stuck Breaker on WETHRBY5 161.00 (543017) 161 kV Bus a. Apply Fault at the WETHRBY5 161.00 (543017) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WETHRBY5 (543017) 161.0 kV to TIFFANY5 (543026) 161.0 kV Transmission Circuit #1 b.2. WETHRBY5 (543017) 161.0 kV to WOLCOTT5 (546669) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_365 | Single Phase Fault with Stuck Breaker on BARRY 5 161.00 (543019) 161 kV Bus a. Apply Fault at the BARRY 5 161.00 (543019) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARRY 5 (543019) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. BARRY 5 (543019) 161.0 kV to LINECRK5 (543025) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_366 | Single Phase Fault with Stuck Breaker on BRMGHAM5 161.00 (543020) 161 kV Bus a. Apply Fault at the BRMGHAM5 161.00 (543020) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BRMGHAM5 (543020) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #1 b.2. BRMGHAM5 (543020) 161.0 kV to LBRTYST5 (541248) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_367 | Single Phase Fault with Stuck Breaker on NASHUA 7 345.00 (542980) 345 kV Bus a. Apply Fault at the NASHUA 7 345.00 (542980) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T11 (543640) 13.8 kV Three Winding #11 b.2. NASHUA-5 (543028) 161.0 kV to NASHUA 7 (542980) 345.0 kV to NASH T12 (543639) 13.8 kV Three Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_368 | Single Phase Fault with Stuck Breaker on SHWNMSN5 161.00 (543031) 161 kV Bus a. Apply Fault at the SHWNMSN5 161.00 (543031) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHWNMSN5 (543031) 161.0 kV to MERRIAM5 (543032) 161.0 kV Transmission Circuit #1 b.2. SHWNMSN5 (543031) 161.0 kV to LENEXA 5 (543038) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_369 | Single Phase Fault with Stuck Breaker on HAWTH 2 69.000 (543080) 69 kV Bus a. Apply Fault at the HAWTH 2 69.000 (543080) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 2 (543080) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.2. HAWTH 2 (543080) 69.0 kV to HAWT11_2 (543663) 69.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_370 | Single Phase Fault with Stuck Breaker on COURTNY2 69.000 (543085) 69 kV Bus a. Apply Fault at the COURTNY2 69.000 (543085) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COURTNY2 (543085) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 b.2. COURTNY2 (543085) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_371 | Single Phase Fault with Stuck Breaker on IND WTR2 69.000 (543086) 69 kV Bus a. Apply Fault at the IND WTR2 69.000 (543086) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IND WTR2 (543086) 69.0 kV to BYPASJT2 (543084) 69.0 kV Transmission Circuit #1 b.2. IND WTR2 (543086) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_372 | Single Phase Fault with Stuck Breaker on LAFJCT 2 69.000 (543104) 69 kV Bus a. Apply Fault at the LAFJCT 2 69.000 (543104) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAFJCT 2 (543104) 69.0 kV to IND WTR2 (543086) 69.0 kV Transmission Circuit #1 b.2. LAFJCT 2 (543104) 69.0 kV to MILCKJT2 (543110) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_373 | Single Phase Fault with Stuck Breaker on MILCKJT2 69.000 (543110) 69 kV Bus a. Apply Fault at the MILCKJT2 69.000 (543110) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MILCKJT2 (543110) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. MILCKJT2 (543110) 69.0 kV to LAFJCT 2 (543104) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_374 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_W269.000 (543164) 69 kV Bus a. Apply Fault at the SUGRCK_TP_W269.000 (543164) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_W2 (543164) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_W2 (543164) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_375 | Single Phase Fault with Stuck Breaker on SUGRCK_TP_E269.000 (543165) 69 kV Bus a. Apply Fault at the SUGRCK_TP_E269.000 (543165) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUGRCK_TP_E2 (543165) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 b.2. SUGRCK_TP_E2 (543165) 69.0 kV to SUB H (548802) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_376 | Single Phase Fault with Stuck Breaker on KAW 2 69.000 (546678) 69 kV Bus a. Apply Fault at the KAW 2 69.000 (546678) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KAW 2 (546678) 69.0 kV to BARBER 2 (546691) 69.0 kV Transmission Circuit #1 b.2. KAW 2 (546678) 69.0 kV to EVERETT2 (546682) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_377 | Single Phase Fault with Stuck Breaker on MUNCIE 2 69.000 (546681) 69 kV Bus a. Apply Fault at the MUNCIE 2 69.000 (546681) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MUNCIE 2 (546681) 69.0 kV to COL PAL2 (546687) 69.0 kV Transmission Circuit #1 b.2. MUNCIE 2 (546681) 69.0 kV to QUINDA 2 (546692) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_378 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV167 2 (547541) 69.0 kV to RIV4525 (547469) 161.0 kV to RIV452 1 (547725) 12.5 kV Three Winding #1 b.2. RIV167 2 (547541) 69.0 kV to JOP 59 2 (547525) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_379 | Single Phase Fault with Stuck Breaker on SUB I 69.000 (548800) 69 kV Bus a. Apply Fault at the SUB I 69.000 (548800) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB I (548800) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 b.2. SUB I (548800) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_380 | Single Phase Fault with Stuck Breaker on SUB K 69.000 (548801) 69 kV Bus a. Apply Fault at the SUB K 69.000 (548801) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB K (548801) 69.0 kV to BLUVLY (548806) 69.0 kV Transmission Circuit #1 b.2. SUB K (548801) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_381 | Single Phase Fault with Stuck Breaker on SUB H 69.000 (548802) 69 kV Bus a. Apply Fault at the SUB H 69.000 (548802) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB H (548802) 69.0 kV to COURTNY2 (543085) 69.0 kV Transmission Circuit #1 b.2. SUB H (548802) 69.0 kV to SUGRCK_TP_E2 (543165) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_382 | Single Phase Fault with Stuck Breaker on SUB F 69.000 (548803) 69 kV Bus a. Apply Fault at the SUB F 69.000 (548803) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB F (548803) 69.0 kV to HAWTH 2 (543080) 69.0 kV Transmission Circuit #1 b.2. SUB F (548803) 69.0 kV to SUGRCK_TP_W2 (543164) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_383 | Single Phase Fault with Stuck Breaker on SUB E 69.000 (548804) 69 kV Bus a. Apply Fault at the SUB E 69.000 (548804) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB E (548804) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 b.2. SUB E (548804) 69.0 kV to KCPL JCT (548832) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_384 | Single Phase Fault with Stuck Breaker on SHRNKRD 69.000 (548809) 69 kV Bus a. Apply Fault at the SHRNKRD 69.000 (548809) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHRNKRD (548809) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SHRNKRD (548809) 69.0 kV to SUB R (548830) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_385 | Single Phase Fault with Stuck Breaker on SUB J 69.000 (548811) 69 kV Bus a. Apply Fault at the SUB J 69.000 (548811) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB J (548811) 69.0 kV to SUB M (548815) 69.0 kV Transmission Circuit #1 b.2. SUB J (548811) 69.0 kV to SUB B (548810) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_386 | Single Phase Fault with Stuck Breaker on SUB N-161 161.00 (548820) 161 kV Bus a. Apply Fault at the SUB N-161 161.00 (548820) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB N (548821) 69.0 kV to SUB N-161 (548820) 161.0 kV Two Winding #1 b.2. SUB N (548821) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_387 | Single Phase Fault with Stuck Breaker on SUB C 69.000 (548825) 69 kV Bus a. Apply Fault at the SUB C 69.000 (548825) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB C (548825) 69.0 kV to STRLNGRD (548826) 69.0 kV Transmission Circuit #1 b.2. SUB C (548825) 69.0 kV to SUB I (548800) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_388 | Single Phase Fault with Stuck Breaker on G15-052T 345.00 (560053) 345 kV Bus a. Apply Fault at the G15-052T 345.00 (560053) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G15-052T (560053) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 b.2. G15-052T (560053) 345.0 kV to OPENSKY7 (515621) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_389 | Single Phase Fault with Stuck Breaker on G16-003-TAP 345.00 (560071) 345 kV Bus a. Apply Fault at the G16-003-TAP 345.00 (560071) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #2 b.2. G16-003-TAP (560071) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_390 | Single Phase Fault with Stuck Breaker on G16-046-TAP 345.00 (560080) 345 kV Bus a. Apply Fault at the G16-046-TAP 345.00 (560080) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-046-TAP (560080) 345.0 kV to CLARKCOUNTY7 (539800) 345.0 kV Transmission Circuit #1 b.2. G16-046-TAP (560080) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_391 | Single Phase Fault with Stuck Breaker on G14-001-TAP 345.00 (562476) 345 kV Bus a. Apply Fault at the G14-001-TAP 345.00 (562476) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G14-001-TAP (562476) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. G14-001-TAP (562476) 345.0 kV to WICHITA7 (532796) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_392 | Single Phase Fault with Stuck Breaker on GEN-2016-111345.00 (587880) 345 kV Bus a. Apply Fault at the GEN-2016-111345.00 (587880) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-111 (587880) 345.0 kV to G16-111XFMR1 (587881) 34.5 kV Two Winding #1 b.2. GEN-2016-111 (587880) 345.0 kV to G16-111-TAP (587884) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_393 | Single Phase Fault with Stuck Breaker on GEN-2016-153345.00 (588360) 345 kV Bus a. Apply Fault at the GEN-2016-153345.00 (588360) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-153 (588360) 345.0 kV to G16-153-TAP (588364) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-153 (588360) 345.0 kV to G16-153XFMR1 (588361) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_394 | Single Phase Fault with Stuck Breaker on GEN-2017-022138.00 (588660) 138 kV Bus a. Apply Fault at the GEN-2017-022138.00 (588660) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-022 (588660) 138.0 kV to G17-022XFMR1 (588661) 34.5 kV Two Winding #1 b.2. GEN-2017-022 (588660) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_395 | Single Phase Fault with Stuck Breaker on S3740 3 345.00 (645740) 345 kV Bus a. Apply Fault at the S3740 3 345.00 (645740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. S3740 3 (645740) 345.0 kV to S3455 3 (645455) 345.0 kV Transmission Circuit #1 b.2. S3740 3 (645740) 345.0 kV to S3454 3 (645454) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_396 | Single Phase Fault with Stuck Breaker on GI94_POI 345.00 (709400) 345 kV Bus a. Apply Fault at the GI94_POI 345.00 (709400) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI94_POI (709400) 345.0 kV to GI-95_POI (709500) 345.0 kV Transmission Circuit #1 b.2. GI94_POI (709400) 345.0 kV to 7JASPER (300949) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_397 | Single Phase Fault with Stuck Breaker on GI-95_POI 345.00 (709500) 345 kV Bus a. Apply Fault at the GI-95_POI 345.00 (709500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GI-95_POI (709500) 345.0 kV to 7MORGAN (300045) 345.0 kV Transmission Circuit #1 b.2. GI-95_POI (709500) 345.0 kV to GI94_POI (709400) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_398 | Single Phase Fault with Stuck Breaker on GEN-2017-209345.00 (760914) 345 kV Bus a. Apply Fault at the GEN-2017-209345.00 (760914) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-209 (760914) 345.0 kV to G17-209-TAP (760921) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-209 (760914) 345.0 kV to G17-209XFMR1 (760915) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_399 | Single Phase Fault with Stuck Breaker on 7JASPER 345.00 (300949) 345 kV Bus a. Apply Fault at the 7JASPER 345.00 (300949) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5JASPER (300950) 161.0 kV to 5LAMAR (300794) 161.0 kV Transmission Circuit #1 b.2. 5JASPER (300950) 161.0 kV to 7JASPER (300949) 345.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_400 | Single Phase Fault with Stuck Breaker on FLINTCR5 161.00 (506934) 161 kV Bus a. Apply Fault at the FLINTCR5 161.00 (506934) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR5 (506934) 161.0 kV to TONTITN5 (506957) 161.0 kV Transmission Circuit #1 b.2. FLINTCR5 (506934) 161.0 kV to GENTRY 5 (504201) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_401 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.2-4 (509895) 138.0 kV to T.NO.--4 (509817) 138.0 kV Transmission Circuit #1 b.2. T.NO.2-4 (509895) 138.0 kV to T.NO.--7 (509852) 345.0 kV to TNO2-1 (509894) 34.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_402 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE4 (510379) 138.0 kV to FARML 4 (512734) 138.0 kV Transmission Circuit #1 b.2. DELWARE4 (510379) 138.0 kV to DELWARE7 (510380) 345.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_403 | Single Phase Fault with Stuck Breaker on CHISHOLM6 230.00 (511557) 230 kV Bus a. Apply Fault at the CHISHOLM6 230.00 (511557) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHOLM6 (511557) 230.0 kV to ELKCITY6 (511490) 230.0 kV Transmission Circuit #1 b.2. CHISHOLM6 (511557) 230.0 kV to SWEETWT6 (511541) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_404 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 5 (512648) 161.0 kV to 5CHOTEAU1 (300069) 161.0 kV Transmission Circuit #1 b.2. MAID 5 (512648) 161.0 kV to GERALDGAY5 (512760) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_405 | Single Phase Fault with Stuck Breaker on GRDA1 7 345.00 (512650) 345 kV Bus a. Apply Fault at the GRDA1 7 345.00 (512650) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 7 (512650) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. GRDA1 7 (512650) 345.0 kV to 7SPORTSMAN (300740) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_406 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 5 (512656) 161.0 kV to WMAIN ST5 (512742) 161.0 kV Transmission Circuit #1 b.2. GRDA1 5 (512656) 161.0 kV to WAGNOR 5 (512700) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_407 | Single Phase Fault with Stuck Breaker on FARML 4 138.00 (512734) 138 kV Bus a. Apply Fault at the FARML 4 138.00 (512734) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FARML 4 (512734) 138.0 kV to DELWARE4 (510379) 138.0 kV Transmission Circuit #1 b.2. FARML 4 (512734) 138.0 kV to SCOFCTY4 (510378) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_408 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE7 (512750) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. TONECE7 (512750) 345.0 kV to FLINTCR7 (506935) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_409 | Single Phase Fault with Stuck Breaker on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IGLOOV 7 (513596) 345.0 kV to GREC TAP5 (512865) 345.0 kV Transmission Circuit #1 b.2. IGLOOV 7 (513596) 345.0 kV to T.NO.--7 (509852) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_410 | Single Phase Fault with Stuck Breaker on KNOBHIL4 138.00 (514795) 138 kV Bus a. Apply Fault at the KNOBHIL4 138.00 (514795) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL4 (514795) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. KNOBHIL4 (514795) 138.0 kV to KNOBHIL2 (514794) 69.0 kV to KNOBHIL1 (515732) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_411 | Single Phase Fault with Stuck Breaker on WWRDEHV7 345.00 (515375) 345 kV Bus a. Apply Fault at the WWRDEHV7 345.00 (515375) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWRDEHV4 (515376) 138.0 kV to IODINE-4 (514796) 138.0 kV Transmission Circuit #1 b.2. WWRDEHV4 (515376) 138.0 kV to WWRDEHV7 (515375) 345.0 kV to WWDEHV21 (515799) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_412 | Single Phase Fault with Stuck Breaker on RENFROW7 345.00 (515543) 345 kV Bus a. Apply Fault at the RENFROW7 345.00 (515543) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RENFROW4 (515544) 138.0 kV to RENFROW7 (515543) 345.0 kV to RENFRO11 (515545) 13.8 kV Three Winding #1 b.2. RENFROW4 (515544) 138.0 kV to GRANTCO4 (515546) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_413 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to POSTROCK6 (530584) 230.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_414 | Single Phase Fault with Stuck Breaker on MINGO 7 345.00 (531451) 345 kV Bus a. Apply Fault at the MINGO 7 345.00 (531451) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MINGO 3 (531429) 115.0 kV to COLBY 3 (530555) 115.0 kV Transmission Circuit #1 b.2. MINGO 3 (531429) 115.0 kV to MINGO 7 (531451) 345.0 kV to MINGTER (531453) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_415 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 3 (531464) 115.0 kV to SCOTCTY3 (531433) 115.0 kV Transmission Circuit #1 b.2. SETAB 3 (531464) 115.0 kV to SETAB 7 (531465) 345.0 kV to SETAB 1 (531259) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_416 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR3 (531510) 115.0 kV to WALKMYR3 (531405) 115.0 kV Transmission Circuit #1 b.2. HARBNGR3 (531510) 115.0 kV to HARBNGR7 (531512) 345.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_417 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 7 (532769) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. LANG 7 (532769) 345.0 kV to LANG 3 (533304) 115.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_418 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 7 (532770) 345.0 kV to EMPEC 7 (532768) 345.0 kV Transmission Circuit #1 b.2. MORRIS 7 (532770) 345.0 kV to MORRIS 6 (532863) 230.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_419 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 7 (532775) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 b.2. 87TH 7 (532775) 345.0 kV to CRAIG 7 (542977) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_420 | Single Phase Fault with Stuck Breaker on WOLFCRK7 345.00 (532797) 345 kV Bus a. Apply Fault at the WOLFCRK7 345.00 (532797) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WOLFCRK7 (532797) 345.0 kV to 7BLACKBERRY (300739) 345.0 kV Transmission Circuit #1 b.2. WOLFCRK7 (532797) 345.0 kV to ROSEHIL7 (532794) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_421 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 6 (532871) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. CIRCLE 6 (532871) 230.0 kV to CIRCLE 3 (533413) 115.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_422 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 5 (532937) 161.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 2 1 (532825) 13.8 kV Three Winding #1 b.2. NEOSHO 5 (532937) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_423 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLERS4 (532989) 138.0 kV to BUTLERS2 (533609) 69.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 b.2. BUTLERS4 (532989) 138.0 kV to TALLGRS4 (532993) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_424 | Single Phase Fault with Stuck Breaker on MIDIAN 4 138.00 (532990) 138 kV Bus a. Apply Fault at the MIDIAN 4 138.00 (532990) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDIAN 4 (532990) 138.0 kV to BENTON 4 (532986) 138.0 kV Transmission Circuit #1 b.2. MIDIAN 4 (532990) 138.0 kV to BUTLER 4 (532987) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_425 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTD 4 (533011) 138.0 kV to BENTLEY4 (533015) 138.0 kV Transmission Circuit #1 b.2. HALSTD 4 (533011) 138.0 kV to MOUND 4 (533013) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_426 | Single Phase Fault with Stuck Breaker on MOUND 4 138.00 (533013) 138 kV Bus a. Apply Fault at the MOUND 4 138.00 (533013) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOUND 4 (533013) 138.0 kV to MOUND 2 (533742) 69.0 kV to MOUND1X1 (533095) 13.2 kV Three Winding #1 b.2. MOUND 4 (533013) 138.0 kV to HALSTD 4 (533011) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_427 | Single Phase Fault with Stuck Breaker on NEOSHO 7 345.00 (532793) 345 kV Bus a. Apply Fault at the NEOSHO 7 345.00 (532793) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHO 4 (533021) 138.0 kV to NEOSHO 7 (532793) 345.0 kV to N345 1 1 (532824) 13.8 kV Three Winding #1 b.2. NEOSHO 4 (533021) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_428 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON4 (533022) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 b.2. NEOSHON4 (533022) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_429 | Single Phase Fault with Stuck Breaker on CHISHLM4 138.00 (533035) 138 kV Bus a. Apply Fault at the CHISHLM4 138.00 (533035) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM4 (533035) 138.0 kV to MAIZE 4 (533054) 138.0 kV Transmission Circuit #1 b.2. CHISHLM4 (533035) 138.0 kV to 17TH 4 (533064) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_430 | Single Phase Fault with Stuck Breaker on COWSKIN4 138.00 (533038) 138 kV Bus a. Apply Fault at the COWSKIN4 138.00 (533038) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN4 (533038) 138.0 kV to 45TH ST4 (533074) 138.0 kV Transmission Circuit #1 b.2. COWSKIN4 (533038) 138.0 kV to COWSKIN2 (533788) 69.0 kV to COWSKIN1 (533104) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_431 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 4 (533044) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 b.2. GILL E 4 (533044) 138.0 kV to GILL W 2 (533796) 69.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_432 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL S 4 (533046) 138.0 kV to GILL 4 (533047) 138.0 kV Transmission Circuit #z1 b.2. GILL S 4 (533046) 138.0 kV to GILL W 2 (533796) 69.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_433 | Single Phase Fault with Stuck Breaker on HOOVERN4 138.00 (533049) 138 kV Bus a. Apply Fault at the HOOVERN4 138.00 (533049) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN4 (533049) 138.0 kV to LAKERDG4 (533053) 138.0 kV Transmission Circuit #1 b.2. HOOVERN4 (533049) 138.0 kV to HOOVERS4 (533050) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_434 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS4 (533050) 138.0 kV to HOOVERN4 (533049) 138.0 kV Transmission Circuit #z1 b.2. HOOVERS4 (533050) 138.0 kV to INTERST4 (533051) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_435 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOEASTE4 (533060) 138.0 kV to 29TH 4 (533024) 138.0 kV Transmission Circuit #1 b.2. NOEASTE4 (533060) 138.0 kV to ANDOVER4 (533026) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_436 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOEASTW4 (533061) 138.0 kV to COMOTAR4 (533037) 138.0 kV Transmission Circuit #1 b.2. NOEASTW4 (533061) 138.0 kV to NOEASTE4 (533060) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_437 | Single Phase Fault with Stuck Breaker on VIOLA 7 345.00 (532798) 345 kV Bus a. Apply Fault at the VIOLA 7 345.00 (532798) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to VIOLA1X1 (532832) 13.8 kV Three Winding #1 b.2. VIOLA 4 (533075) 138.0 kV to VIOLA 7 (532798) 345.0 kV to SCJ1X1 (999532) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_438 | Single Phase Fault with Stuck Breaker on DAVIS 3 115.00 (533415) 115 kV Bus a. Apply Fault at the DAVIS 3 115.00 (533415) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DAVIS 3 (533415) 115.0 kV to RENO 3 (533416) 115.0 kV Transmission Circuit #1 b.2. DAVIS 3 (533415) 115.0 kV to CITIES 3 (533414) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_439 | Single Phase Fault with Stuck Breaker on HEC 3 115.00 (533419) 115 kV Bus a. Apply Fault at the HEC 3 115.00 (533419) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HEC 3 (533419) 115.0 kV to CIRCLE 3 (533413) 115.0 kV Transmission Circuit #1 b.2. HEC 3 (533419) 115.0 kV to 43LORAN (533440) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_440 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMATN2 (533639) 69.0 kV to MARMTNW5 (532935) 161.0 kV to MARMATN1 (532955) 13.2 kV Three Winding #1 b.2. MARMATN2 (533639) 69.0 kV to MCKEE 2 (533640) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_441 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERT-2 (533697) 69.0 kV to LIBERTY4 (533003) 138.0 kV to LIBERTY1 (533090) 13.2 kV Three Winding #1 b.2. LIBERT-2 (533697) 69.0 kV to SUNFLRS2 (533670) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_442 | Single Phase Fault with Stuck Breaker on BARBER 3 115.00 (539760) 115 kV Bus a. Apply Fault at the BARBER 3 115.00 (539760) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 3 (539760) 115.0 kV to MED-LDG3 (539673) 115.0 kV Transmission Circuit #1 b.2. BARBER 3 (539760) 115.0 kV to SAWYER 3 (539649) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_443 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 7 (541198) 345.0 kV to PECULR 5 (541342) 161.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 7 (541198) 345.0 kV to STILWEL7 (542968) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_444 | Single Phase Fault with Stuck Breaker on PHILL 7 345.00 (541200) 345 kV Bus a. Apply Fault at the PHILL 7 345.00 (541200) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PHILL 7 (541200) 345.0 kV to SIBLEY 7 (541201) 345.0 kV Transmission Circuit #1 b.2. PHILL 7 (541200) 345.0 kV to PHILL 5 (541225) 161.0 kV to PHILL T (541361) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_445 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 7 (541201) 345.0 kV to KETCHEM7 (541500) 345.0 kV Transmission Circuit #1 b.2. SIBLEY 7 (541201) 345.0 kV to SIBLEY 5 (541202) 161.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_446 | Single Phase Fault with Stuck Breaker on MARTCTY5 161.00 (541210) 161 kV Bus a. Apply Fault at the MARTCTY5 161.00 (541210) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARTCTY2 (541287) 69.0 kV to GRDWST 2 (541286) 69.0 kV Transmission Circuit #1 b.2. MARTCTY2 (541287) 69.0 kV to MARTCTY5 (541210) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_447 | Single Phase Fault with Stuck Breaker on STILWEL7 345.00 (542968) 345 kV Bus a. Apply Fault at the STILWEL7 345.00 (542968) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STILWEL7 (542968) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. STILWEL7 (542968) 345.0 kV to PECULR 7 (541198) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_448 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTH 7 (542972) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. HAWTH 7 (542972) 345.0 kV to HAWTHN5 (543665) 161.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_449 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 7 (542977) 345.0 kV to 87TH 7 (532775) 345.0 kV Transmission Circuit #1 b.2. CRAIG 7 (542977) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_450 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN 7 (542982) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. IATAN 7 (542982) 345.0 kV to STRANGR7 (532772) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_451 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 5 (547467) 161.0 kV to OAK432 5 (547494) 161.0 kV Transmission Circuit #1 b.2. ORO110 5 (547467) 161.0 kV to RIV4525 (547469) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_452 | Single Phase Fault with Stuck Breaker on RIV4525 161.00 (547469) 161 kV Bus a. Apply Fault at the RIV4525 161.00 (547469) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV4525 (547469) 161.0 kV to ORO110 5 (547467) 161.0 kV Transmission Circuit #1 b.2. RIV4525 (547469) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_453 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 5 (547487) 161.0 kV to BAX488 5 (547729) 161.0 kV Transmission Circuit #1 b.2. HOC404 5 (547487) 161.0 kV to HOC404 2 (547601) 69.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_454 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS3 (635000) 345.0 kV to OVRLND 3 (635014) 345.0 kV Transmission Circuit #1 b.2. CBLUFFS3 (635000) 345.0 kV to PNYCRK 3 (635013) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_455 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 5 (640140) 161.0 kV to S1280 5 (646280) 161.0 kV Transmission Circuit #1 b.2. COOPER 5 (640140) 161.0 kV to COOPER 3 (640139) 345.0 kV to COOPER T2 9 (640142) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_456 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 7 (650285) 115.0 kV to 84LEIGHTON7 (650267) 115.0 kV Transmission Circuit #1 b.2. WAGENER 7 (650285) 115.0 kV to WAGENER 3 (650185) 345.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_457 | Single Phase Fault with Stuck Breaker on NEPARSN4 138.00 (533005) 138 kV Bus a. Apply Fault at the NEPARSN4 138.00 (533005) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEPARSN4 (533005) 138.0 kV to NEOSHON4 (533022) 138.0 kV Transmission Circuit #1 b.2. NEPARSN4 (533005) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_458 | Single Phase Fault with Stuck Breaker on EDWRDVL5 161.00 (532912) 161 kV Bus a. Apply Fault at the EDWRDVL5 161.00 (532912) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. EDWARVL3 (533238) 115.0 kV to MUND 3 (533282) 115.0 kV Transmission Circuit #1 b.2. EDWARVL3 (533238) 115.0 kV to EDWRDVL5 (532912) 161.0 kV to EDWRDVL1 (532940) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_459 | Single Phase Fault with Stuck Breaker on PARSONS2 69.000 (533704) 69 kV Bus a. Apply Fault at the PARSONS2 69.000 (533704) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PARSONS2 (533704) 69.0 kV to ORDNJCT2 (533703) 69.0 kV Transmission Circuit #1 b.2. PARSONS2 (533704) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_460 | Single Phase Fault with Stuck Breaker on HOOVERN2 69.000 (533805) 69 kV Bus a. Apply Fault at the HOOVERN2 69.000 (533805) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERN2 (533805) 69.0 kV to WATER1 2 (533855) 69.0 kV Transmission Circuit #1 b.2. HOOVERN2 (533805) 69.0 kV to VISTAPK2 (533849) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_461 | Single Phase Fault with Stuck Breaker on SHERIDN2 69.000 (533841) 69 kV Bus a. Apply Fault at the SHERIDN2 69.000 (533841) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHERIDN2 (533841) 69.0 kV to HOOVERS2 (533806) 69.0 kV Transmission Circuit #1 b.2. SHERIDN2 (533841) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_462 | Single Phase Fault with Stuck Breaker on HARPER 4 138.00 (539668) 138 kV Bus a. Apply Fault at the HARPER 4 138.00 (539668) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARPER 4 (539668) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. HARPER 4 (539668) 138.0 kV to MILANTP4 (539675) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_463 | Single Phase Fault with Stuck Breaker on KCSOUTH5 161.00 (541245) 161 kV Bus a. Apply Fault at the KCSOUTH5 161.00 (541245) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KCSOUTH5 (541245) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 b.2. KCSOUTH5 (541245) 161.0 kV to G18-054-TAP (541231) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_464 | Single Phase Fault with Stuck Breaker on SUB M-161 161.00 (548814) 161 kV Bus a. Apply Fault at the SUB M-161 161.00 (548814) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB M (548815) 69.0 kV to SUB M-161 (548814) 161.0 kV Two Winding #1 b.2. SUB M (548815) 69.0 kV to SUB J (548811) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_465 | Single Phase Fault with Stuck Breaker on 5CHOTEAU2 161.00 (301348) 161 kV Bus a. Apply Fault at the 5CHOTEAU2 161.00 (301348) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 5CHOTEAU2 (301348) 161.0 kV to 5SPORTSMAN (300741) 161.0 kV Transmission Circuit #1 b.2. 5CHOTEAU2 (301348) 161.0 kV to 5CHOTEAU1 (300069) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_466 | Single Phase Fault with Stuck Breaker on 7SPORTSMAN 345.00 (300740) 345 kV Bus a. Apply Fault at the 7SPORTSMAN 345.00 (300740) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 7SPORTSMAN (300740) 345.0 kV to GRDA1 7 (512650) 345.0 kV Transmission Circuit #1 b.2. 7SPORTSMAN (300740) 345.0 kV to 5SPORTSMAN (300741) 161.0 kV Two Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_467 | Single Phase Fault with Stuck Breaker on WWDBORDT 345.00 (755000) 345 kV Bus a. Apply Fault at the WWDBORDT 345.00 (755000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WWDBORDT (755000) 345.0 kV to WWRDEHV7 (515375) 345.0 kV Transmission Circuit #1 b.2. WWDBORDT (755000) 345.0 kV to CHISHOLM7 (511553) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_468 | Single Phase Fault with Stuck Breaker on GEN-2017-203345.00 (760809) 345 kV Bus a. Apply Fault at the GEN-2017-203345.00 (760809) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-203 (760809) 345.0 kV to RENFROW7 (515543) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-203 (760809) 345.0 kV to G17-203XFMR1 (760810) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_469 | Single Phase Fault with Stuck Breaker on PRSIMN_CRK1 345.00 (585430) 345 kV Bus a. Apply Fault at the PRSIMN_CRK1 345.00 (585430) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PRSIMN_CRK1 (585430) 345.0 kV to PRSIMN_CRK2 (585440) 345.0 kV Transmission Circuit #1 b.2. PRSIMN_CRK1 (585430) 345.0 kV to G07621119-20 (515599) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_470 | Single Phase Fault with Stuck Breaker on GEN-2015-095138.00 (585300) 138 kV Bus a. Apply Fault at the GEN-2015-095138.00 (585300) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-095 (585300) 138.0 kV to DGRASSE4 (515853) 138.0 kV Transmission Circuit #1 b.2. GEN-2015-095 (585300) 138.0 kV to G15-095-XF-1 (585301) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_471 | Single Phase Fault with Stuck Breaker on GEN-2016-020138.00 (587140) 138 kV Bus a. Apply Fault at the GEN-2016-020138.00 (587140) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-020 (587140) 138.0 kV to MOORLND4 (520999) 138.0 kV Transmission Circuit #1 b.2. GEN-2016-020 (587140) 138.0 kV to G16-020XFMR1 (587141) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_472 | Single Phase Fault with Stuck Breaker on G16-111-TAP 345.00 (587884) 345 kV Bus a. Apply Fault at the G16-111-TAP 345.00 (587884) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G16-111-TAP (587884) 345.0 kV to RENO 7 (532771) 345.0 kV Transmission Circuit #1 b.2. G16-111-TAP (587884) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_473 | Single Phase Fault with Stuck Breaker on G17-004-TAP 345.00 (588494) 345 kV Bus a. Apply Fault at the G17-004-TAP 345.00 (588494) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-004-TAP (588494) 345.0 kV to SUMMIT 7 (532773) 345.0 kV Transmission Circuit #1 b.2. G17-004-TAP (588494) 345.0 kV to ELMCREEK7 (539805) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_474 | Single Phase Fault with Stuck Breaker on GEN-2017-125345.00 (761901) 345 kV Bus a. Apply Fault at the GEN-2017-125345.00 (761901) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-125 (761901) 345.0 kV to GEN-2017-128 (761922) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-125 (761901) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_475 | Single Phase Fault with Stuck Breaker on GEN-2017-191345.00 (761943) 345 kV Bus a. Apply Fault at the GEN-2017-191345.00 (761943) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-191 (761943) 345.0 kV to SWISVAL7 (532774) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-191 (761943) 345.0 kV to G17-191XFM1 (761944) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_476 | Single Phase Fault with Stuck Breaker on GEN-2016-073345.00 (587500) 345 kV Bus a. Apply Fault at the GEN-2016-073345.00 (587500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-073 (587500) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-073 (587500) 345.0 kV to G16-073XFMR1 (587501) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_477 | Single Phase Fault with Stuck Breaker on GEN-2017-220345.00 (760284) 345 kV Bus a. Apply Fault at the GEN-2017-220345.00 (760284) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-220 (760284) 345.0 kV to BUFFALO7 (532782) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-220 (760284) 345.0 kV to G17-220-XFM1 (760285) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_478 | Single Phase Fault with Stuck Breaker on G17-209-TAP 345.00 (760921) 345 kV Bus a. Apply Fault at the G17-209-TAP 345.00 (760921) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-209-TAP (760921) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #1 b.2. G17-209-TAP (760921) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_479 | Single Phase Fault with Stuck Breaker on GEN-2017-086345.00 (589240) 345 kV Bus a. Apply Fault at the GEN-2017-086345.00 (589240) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-086 (589240) 345.0 kV to VIOLA 7 (532798) 345.0 kV Transmission Circuit #2 b.2. GEN-2017-086 (589240) 345.0 kV to G17-086XFMR1 (589241) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_480 | Single Phase Fault with Stuck Breaker on GILL 4 138.00 (533047) 138 kV Bus a. Apply Fault at the GILL 4 138.00 (533047) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL 4 (533047) 138.0 kV to VIOLA 4 (533075) 138.0 kV Transmission Circuit #1 b.2. GILL 4 (533047) 138.0 kV to GILL W 4 (533045) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_481 | Single Phase Fault with Stuck Breaker on GEN-2017-226138.00 (760641) 138 kV Bus a. Apply Fault at the GEN-2017-226138.00 (760641) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-226 (760641) 138.0 kV to G17-226XFMR1 (760642) 34.5 kV Two Winding #1 b.2. GEN-2017-226 (760641) 138.0 kV to G17-227XFMR1 (760662) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_482 | Single Phase Fault with Stuck Breaker on MCPHER 3 115.00 (533428) 115 kV Bus a. Apply Fault at the MCPHER 3 115.00 (533428) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCPHER 3 (533428) 115.0 kV to WMCPHER3 (533438) 115.0 kV Transmission Circuit #1 b.2. MCPHER 3 (533428) 115.0 kV to REFINRY3 (533427) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_483 | Single Phase Fault with Stuck Breaker on LABETTS2 69.000 (533696) 69 kV Bus a. Apply Fault at the LABETTS2 69.000 (533696) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LABETTS2 (533696) 69.0 kV to NEOSHON2 (533768) 69.0 kV Transmission Circuit #1 b.2. LABETTS2 (533696) 69.0 kV to ALTAMNS2 (533672) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_484 | Single Phase Fault with Stuck Breaker on BARBER 4 138.00 (539674) 138 kV Bus a. Apply Fault at the BARBER 4 138.00 (539674) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 4 (539674) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. BARBER 4 (539674) 138.0 kV to BARBER 3 (539760) 115.0 kV to BARBER-T (539917) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_485 | Single Phase Fault with Stuck Breaker on THISTLE7 345.00 (539801) 345 kV Bus a. Apply Fault at the THISTLE7 345.00 (539801) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THISTLE4 (539804) 138.0 kV to FLATRDG4 (539638) 138.0 kV Transmission Circuit #1 b.2. THISTLE4 (539804) 138.0 kV to THISTLE7 (539801) 345.0 kV to THISTLE T1 (539802) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_486 | Single Phase Fault with Stuck Breaker on GEN-2017-018345.00 (588630) 345 kV Bus a. Apply Fault at the GEN-2017-018345.00 (588630) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-018 (588630) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-018 (588630) 345.0 kV to G17-018XFMR1 (588631) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_487 | Single Phase Fault with Stuck Breaker on GEN-2008-124345.00 (579480) 345 kV Bus a. Apply Fault at the GEN-2008-124345.00 (579480) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2008-124 (579480) 345.0 kV to IRONWOOD7 (539803) 345.0 kV Transmission Circuit #1 b.2. GEN-2008-124 (579480) 345.0 kV to G08-124XFMR1 (579481) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_488 | Single Phase Fault with Stuck Breaker on SMTHVL 5 161.00 (541204) 161 kV Bus a. Apply Fault at the SMTHVL 5 161.00 (541204) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SMTHVL 5 (541204) 161.0 kV to PLTCTY 5 (541221) 161.0 kV Transmission Circuit #1 b.2. SMTHVL 5 (541204) 161.0 kV to NASHUA 5 (541203) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_489 | Single Phase Fault with Stuck Breaker on NCONGRS5 161.00 (541318) 161 kV Bus a. Apply Fault at the NCONGRS5 161.00 (541318) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NCONGRS5 (541318) 161.0 kV to TWA 5 (541214) 161.0 kV Transmission Circuit #1 b.2. NCONGRS5 (541318) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_490 | Single Phase Fault with Stuck Breaker on STROTHR5 161.00 (541246) 161 kV Bus a. Apply Fault at the STROTHR5 161.00 (541246) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STROTHR5 (541246) 161.0 kV to WSTELEC5 (541222) 161.0 kV Transmission Circuit #1 b.2. STROTHR5 (541246) 161.0 kV to PRALEE 5 (541206) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_491 | Single Phase Fault with Stuck Breaker on HOOKRD 5 161.00 (541249) 161 kV Bus a. Apply Fault at the HOOKRD 5 161.00 (541249) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOKRD 5 (541249) 161.0 kV to LKWINBG5 (541243) 161.0 kV Transmission Circuit #1 b.2. HOOKRD 5 (541249) 161.0 kV to LNGVW 5 (541224) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_492 | Single Phase Fault with Stuck Breaker on TIFFANY5 161.00 (543026) 161 kV Bus a. Apply Fault at the TIFFANY5 161.00 (543026) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TIFFANY5 (543026) 161.0 kV to RNRIDGE5 (541230) 161.0 kV Transmission Circuit #1 b.2. TIFFANY5 (543026) 161.0 kV to WETHRBY5 (543017) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_493 | Single Phase Fault with Stuck Breaker on RGAFBTP2 69.000 (541322) 69 kV Bus a. Apply Fault at the RGAFBTP2 69.000 (541322) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RGAFBTP2 (541322) 69.0 kV to GRDVWTP2 (541284) 69.0 kV Transmission Circuit #1 b.2. RGAFBTP2 (541322) 69.0 kV to BELTON 2 (541289) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_494 | Single Phase Fault with Stuck Breaker on GEN-2017-115345.00 (760746) 345 kV Bus a. Apply Fault at the GEN-2017-115345.00 (760746) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-115 (760746) 345.0 kV to HOLT 7 (541510) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-115 (760746) 345.0 kV to G17-115XFMR1 (760747) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_495 | Single Phase Fault with Stuck Breaker on MERRIAM5 161.00 (543032) 161 kV Bus a. Apply Fault at the MERRIAM5 161.00 (543032) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MERRIAM5 (543032) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. MERRIAM5 (543032) 161.0 kV to MERRIAM_CAP5 (542947) 161.0 kV Transmission Circuit #r | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_496 | Single Phase Fault with Stuck Breaker on NEASTS5 161.00 (542985) 161 kV Bus a. Apply Fault at the NEASTS5 161.00 (542985) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEASTS5 (542985) 161.0 kV to GRAND W5 (542988) 161.0 kV Transmission Circuit #1 b.2. NEASTS5 (542985) 161.0 kV to CHOUTEU5 (543011) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_497 | Single Phase Fault with Stuck Breaker on GEN-2016-157345.00 (588300) 345 kV Bus a. Apply Fault at the GEN-2016-157345.00 (588300) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-157 (588300) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-157 (588300) 345.0 kV to GEN-2016-158 (588310) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_498 | Single Phase Fault with Stuck Breaker on GEN-2017-195345.00 (762279) 345 kV Bus a. Apply Fault at the GEN-2017-195345.00 (762279) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-195 (762279) 345.0 kV to W.GRDNR7 (542965) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-195 (762279) 345.0 kV to G17-195XFM1 (762280) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_499 | Single Phase Fault with Stuck Breaker on BNSF 5 161.00 (543132) 161 kV Bus a. Apply Fault at the BNSF 5 161.00 (543132) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BNSF 5 (543132) 161.0 kV to WGARDNR5 (542966) 161.0 kV Transmission Circuit #1 b.2. BNSF 5 (543132) 161.0 kV to MOONLT 5 (543044) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_500 | Single Phase Fault with Stuck Breaker on HICKMAN5 161.00 (542994) 161 kV Bus a. Apply Fault at the HICKMAN5 161.00 (542994) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HICKMAN5 (542994) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. HICKMAN5 (542994) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_501 | Single Phase Fault with Stuck Breaker on ANTIOCH5 161.00 (543050) 161 kV Bus a. Apply Fault at the ANTIOCH5 161.00 (543050) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ANTIOCH5 (543050) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. ANTIOCH5 (543050) 161.0 kV to OXFORD 5 (543046) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_502 | Single Phase Fault with Stuck Breaker on REDEL 5 161.00 (543053) 161 kV Bus a. Apply Fault at the REDEL 5 161.00 (543053) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. REDEL 5 (543053) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. REDEL 5 (543053) 161.0 kV to MARTCIT5 (543002) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_503 | Single Phase Fault with Stuck Breaker on BUCYRUS5 161.00 (543057) 161 kV Bus a. Apply Fault at the BUCYRUS5 161.00 (543057) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUCYRUS5 (543057) 161.0 kV to STILWEL5 (542969) 161.0 kV Transmission Circuit #1 b.2. BUCYRUS5 (543057) 161.0 kV to WAGSTAF5 (543068) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_504 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHS_XF5 (543130) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit #z2 b.2. HAWTHS_XF5 (543130) 161.0 kV to HAWT11_2 (543663) 69.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_505 | Single Phase Fault with Stuck Breaker on G17-183-TAP 345.00 (761383) 345 kV Bus a. Apply Fault at the G17-183-TAP 345.00 (761383) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-183-TAP (761383) 345.0 kV to NASHUA 7 (542980) 345.0 kV Transmission Circuit #1 b.2. G17-183-TAP (761383) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_506 | Single Phase Fault with Stuck Breaker on TERRACE5 161.00 (542991) 161 kV Bus a. Apply Fault at the TERRACE5 161.00 (542991) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TERRACE5 (542991) 161.0 kV to NAVY 5 (542989) 161.0 kV Transmission Circuit #1 b.2. TERRACE5 (542991) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_507 | Single Phase Fault with Stuck Breaker on TOMHAWK5 161.00 (543035) 161 kV Bus a. Apply Fault at the TOMHAWK5 161.00 (543035) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TOMHAWK5 (543035) 161.0 kV to BENDIX 5 (542992) 161.0 kV Transmission Circuit #1 b.2. TOMHAWK5 (543035) 161.0 kV to INDIAN_CK_5 (543127) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_508 | Single Phase Fault with Stuck Breaker on FOREST 5 161.00 (543001) 161 kV Bus a. Apply Fault at the FOREST 5 161.00 (543001) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FOREST 5 (543001) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 b.2. FOREST 5 (543001) 161.0 kV to MIDTOWN5 (542996) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_509 | Single Phase Fault with Stuck Breaker on BUNKRDG5 161.00 (543008) 161 kV Bus a. Apply Fault at the BUNKRDG5 161.00 (543008) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUNKRDG5 (543008) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 b.2. BUNKRDG5 (543008) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_510 | Single Phase Fault with Stuck Breaker on WINJT S5 161.00 (543010) 161 kV Bus a. Apply Fault at the WINJT S5 161.00 (543010) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT S5 (543010) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT S5 (543010) 161.0 kV to STHTOWN5 (542993) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_511 | Single Phase Fault with Stuck Breaker on WINJT N5 161.00 (543009) 161 kV Bus a. Apply Fault at the WINJT N5 161.00 (543009) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WINJT N5 (543009) 161.0 kV to LEEDS 5 (542997) 161.0 kV Transmission Circuit #1 b.2. WINJT N5 (543009) 161.0 kV to LVISTA 5 (542998) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_512 | Single Phase Fault with Stuck Breaker on NKANCTY5 161.00 (543018) 161 kV Bus a. Apply Fault at the NKANCTY5 161.00 (543018) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NKANCTY5 (543018) 161.0 kV to AVONDAL5 (543015) 161.0 kV Transmission Circuit #1 b.2. NKANCTY5 (543018) 161.0 kV to NEASTN5 (543666) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_513 | Single Phase Fault with Stuck Breaker on SHOLCRK5 161.00 (543029) 161 kV Bus a. Apply Fault at the SHOLCRK5 161.00 (543029) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHOLCRK5 (543029) 161.0 kV to NASHUA-5 (543028) 161.0 kV Transmission Circuit #1 b.2. SHOLCRK5 (543029) 161.0 kV to GLADSTN5 (543016) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_514 | Single Phase Fault with Stuck Breaker on LINECRK5 161.00 (543025) 161 kV Bus a. Apply Fault at the LINECRK5 161.00 (543025) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LINECRK5 (543025) 161.0 kV to BARRY 5 (543019) 161.0 kV Transmission Circuit #1 b.2. LINECRK5 (543025) 161.0 kV to RIVRSID5 (543021) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_515 | Single Phase Fault with Stuck Breaker on LENEXA 5 161.00 (543038) 161 kV Bus a. Apply Fault at the LENEXA 5 161.00 (543038) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #1 b.2. LENEXA 5 (543038) 161.0 kV to CRAIG 5 (542978) 161.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_516 | Single Phase Fault with Stuck Breaker on SHAWNEE5 161.00 (543041) 161 kV Bus a. Apply Fault at the SHAWNEE5 161.00 (543041) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SHAWNEE5 (543041) 161.0 kV to SHWNMSN5 (543031) 161.0 kV Transmission Circuit #1 b.2. SHAWNEE5 (543041) 161.0 kV to BARBER 5 (546651) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_517 | Single Phase Fault with Stuck Breaker on COL PAL2 69.000 (546687) 69 kV Bus a. Apply Fault at the COL PAL2 69.000 (546687) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COL PAL2 (546687) 69.0 kV to KAW 2 (546678) 69.0 kV Transmission Circuit #1 b.2. COL PAL2 (546687) 69.0 kV to MUNCIE 2 (546681) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_518 | Single Phase Fault with Stuck Breaker on BARBER 5 161.00 (546651) 161 kV Bus a. Apply Fault at the BARBER 5 161.00 (546651) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BARBER 2 (546691) 69.0 kV to KAW 2 (546678) 69.0 kV Transmission Circuit #1 b.2. BARBER 2 (546691) 69.0 kV to BARBER 5 (546651) 161.0 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_519 | Single Phase Fault with Stuck Breaker on STL439 5 161.00 (547498) 161 kV Bus a. Apply Fault at the STL439 5 161.00 (547498) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STL439 5 (547498) 161.0 kV to JOP389 5 (547483) 161.0 kV Transmission Circuit #1 b.2. STL439 5 (547498) 161.0 kV to JOP145 5 (547470) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_520 | Single Phase Fault with Stuck Breaker on RIV406 2 69.000 (547602) 69 kV Bus a. Apply Fault at the RIV406 2 69.000 (547602) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. RIV406 2 (547602) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. RIV406 2 (547602) 69.0 kV to BAX271 2 (547554) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_521 | Single Phase Fault with Stuck Breaker on GLF339 2 69.000 (547690) 69 kV Bus a. Apply Fault at the GLF339 2 69.000 (547690) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GLF339 2 (547690) 69.0 kV to RIV167 2 (547541) 69.0 kV Transmission Circuit #1 b.2. GLF339 2 (547690) 69.0 kV to GAL278T (547728) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_522 | Single Phase Fault with Stuck Breaker on SUB R 69.000 (548830) 69 kV Bus a. Apply Fault at the SUB R 69.000 (548830) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SUB R (548830) 69.0 kV to SHRNKRD (548809) 69.0 kV Transmission Circuit #1 b.2. SUB R (548830) 69.0 kV to SUB K (548801) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_523 | Single Phase Fault with Stuck Breaker on KCPL JCT 69.000 (548832) 69 kV Bus a. Apply Fault at the KCPL JCT 69.000 (548832) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KCPL JCT (548832) 69.0 kV to SUB F (548803) 69.0 kV Transmission Circuit #1 b.2. KCPL JCT (548832) 69.0 kV to SUB E (548804) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_524 | Single Phase Fault with Stuck Breaker on STRLNGRD 69.000 (548826) 69 kV Bus a. Apply Fault at the STRLNGRD 69.000 (548826) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. STRLNGRD (548826) 69.0 kV to SUB N (548821) 69.0 kV Transmission Circuit #1 b.2. STRLNGRD (548826) 69.0 kV to SUB C (548825) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_525 | Single Phase Fault with Stuck Breaker on GEN-2015-052345.00 (584900) 345 kV Bus a. Apply Fault at the GEN-2015-052345.00 (584900) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2015-052 (584900) 345.0 kV to G15-052T (560053) 345.0 kV Transmission Circuit #1 b.2. GEN-2015-052 (584900) 345.0 kV to G15-052XFMR1 (584901) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_526 | Single Phase Fault with Stuck Breaker on GEN-2016-003345.00 (587020) 345 kV Bus a. Apply Fault at the GEN-2016-003345.00 (587020) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2016-003 (587020) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 b.2. GEN-2016-003 (587020) 345.0 kV to G16-003XFMR1 (587021) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_527 | Single Phase Fault with Stuck Breaker on GEN-2017-011345.00 (588560) 345 kV Bus a. Apply Fault at the GEN-2017-011345.00 (588560) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2017-011 (588560) 345.0 kV to G16-003-TAP (560071) 345.0 kV Transmission Circuit #1 b.2. GEN-2017-011 (588560) 345.0 kV to G17-011XFMR1 (588561) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_528 | Single Phase Fault with Stuck Breaker on GEN-2014-001345.00 (583850) 345 kV Bus a. Apply Fault at the GEN-2014-001345.00 (583850) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GEN-2014-001 (583850) 345.0 kV to G14-001-TAP (562476) 345.0 kV Transmission Circuit #1 b.2. GEN-2014-001 (583850) 345.0 kV to G14-001XFMR2 (583854) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_529 | Single Phase Fault with Stuck Breaker on G17-022-TAP 138.00 (588664) 138 kV Bus a. Apply Fault at the G17-022-TAP 138.00 (588664) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G17-022-TAP (588664) 138.0 kV to ALTOONA4 (533001) 138.0 kV Transmission Circuit #1 b.2. G17-022-TAP (588664) 138.0 kV to NEPARSN4 (533005) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_530 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWT11_2 (543663) 69.0 kV to HAWTH 2 (543080) 69.0 kV Transmission Circuit # b.2. HAWT11_2 (543663) 69.0 kV to HAWTHS_XF5 (543130) 161.0 kV Two Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_531 | Single Phase Fault with Stuck Breaker on HAWTHS_XF5 161.00 (543130) 161 kV Bus a. Apply Fault at the HAWTHS_XF5 161.00 (543130) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWT12_2 (543664) 69.0 kV to HAWTH 2 (543080) 69.0 kV Transmission Circuit # b.2. HAWT12_2 (543664) 69.0 kV to HAWTHS_XF5 (543130) 161.0 kV Two Winding #12 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_532 | Single Phase Fault with Stuck Breaker on FLINTCR7 345.00 (506935) 345 kV Bus a. Apply Fault at the FLINTCR7 345.00 (506935) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FLINTCR7 (506935) 345.0 kV to TONECE7 (512750) 345.0 kV Transmission Circuit #1 b.2. FLINTCR7 (506935) 345.0 kV to SHIPERD7 (506979) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_533 | Single Phase Fault with Stuck Breaker on T.NO.--7 345.00 (509852) 345 kV Bus a. Apply Fault at the T.NO.--7 345.00 (509852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. T.NO.--7 (509852) 345.0 kV to N.E.S.-7 (510406) 345.0 kV Transmission Circuit #1 b.2. T.NO.--7 (509852) 345.0 kV to WEKIWA-7 (509755) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_534 | Single Phase Fault with Stuck Breaker on DELWARE7 345.00 (510380) 345 kV Bus a. Apply Fault at the DELWARE7 345.00 (510380) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DELWARE7 (510380) 345.0 kV to NEOSHO 7 (532793) 345.0 kV Transmission Circuit #1 b.2. DELWARE7 (510380) 345.0 kV to DELWARE4 (510379) 138.0 kV to DELAWAR1 (510370) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_535 | Single Phase Fault with Stuck Breaker on MAID 5 161.00 (512648) 161 kV Bus a. Apply Fault at the MAID 5 161.00 (512648) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MAID 2 (512626) 69.0 kV to AMERCAST S2 (512681) 69.0 kV Transmission Circuit #1 b.2. MAID 2 (512626) 69.0 kV to MAID 5 (512648) 161.0 kV to MAITER1 1 (512836) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_536 | Single Phase Fault with Stuck Breaker on GRDA1 5 161.00 (512656) 161 kV Bus a. Apply Fault at the GRDA1 5 161.00 (512656) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDA1 2 (512727) 69.0 kV to MAIDTP2 (512625) 69.0 kV Transmission Circuit #1 b.2. GRDA1 2 (512727) 69.0 kV to GRDA1 5 (512656) 161.0 kV to GRDA1 1 (512816) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_537 | Single Phase Fault with Stuck Breaker on TONECE7 345.00 (512750) 345 kV Bus a. Apply Fault at the TONECE7 345.00 (512750) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. TONECE5 (512751) 161.0 kV to TONECE7 (512750) 345.0 kV to TONECE1 (512752) 13.2 kV Three Winding #1 b.2. TONECE5 (512751) 161.0 kV to SILMCTY5 (512643) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_538 | Single Phase Fault with Stuck Breaker on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IGLOOV1 5 (513593) 161.0 kV to HERRON 5 (513591) 161.0 kV Transmission Circuit #1 b.2. IGLOOV1 5 (513593) 161.0 kV to IGLOOV 7 (513596) 345.0 kV to IGLOTER1 1 (513592) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_539 | Single Phase Fault with Stuck Breaker on IGLOOV 7 345.00 (513596) 345 kV Bus a. Apply Fault at the IGLOOV 7 345.00 (513596) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IGLOOV2 5 (513595) 161.0 kV to HERRON 5 (513591) 161.0 kV Transmission Circuit #1 b.2. IGLOOV2 5 (513595) 161.0 kV to IGLOOV 7 (513596) 345.0 kV to IGLOTER2 1 (513594) 13.2 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_540 | Single Phase Fault with Stuck Breaker on KNOBHIL2 69.000 (514794) 69 kV Bus a. Apply Fault at the KNOBHIL2 69.000 (514794) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. KNOBHIL2 (514794) 69.0 kV to ALVAOGE2 (514792) 69.0 kV Transmission Circuit #1 b.2. KNOBHIL2 (514794) 69.0 kV to CZYCRVT2 (515560) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_541 | Single Phase Fault with Stuck Breaker on DGRASSE7 345.00 (515852) 345 kV Bus a. Apply Fault at the DGRASSE7 345.00 (515852) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #2 b.2. DGRASSE7 (515852) 345.0 kV to THISTLE7 (539801) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_542 | Single Phase Fault with Stuck Breaker on MOORLND4 138.00 (520999) 138 kV Bus a. Apply Fault at the MOORLND4 138.00 (520999) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MOORLND2 (520995) 69.0 kV to CRTSJCT2 (521197) 69.0 kV Transmission Circuit #1 b.2. MOORLND2 (520995) 69.0 kV to MOORLND4 (520999) 138.0 kV to MLNDTERT (521180) 2.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_543 | Single Phase Fault with Stuck Breaker on HITCHLAND 7345.00 (523097) 345 kV Bus a. Apply Fault at the HITCHLAND 7345.00 (523097) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR21 (523094) 13.2 kV Three Winding #2 b.2. HITCHLAND 6 (523095) 230.0 kV to HITCHLAND 7 (523097) 345.0 kV to HITCHLD_TR01 (523091) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_544 | Single Phase Fault with Stuck Breaker on G06-44 115.00 (560577) 115 kV Bus a. Apply Fault at the G06-44 115.00 (560577) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. G06-44 (560577) 115.0 kV to G06-44-3 (560582) 34.5 kV Two Winding #1 b.2. G06-44 (560577) 115.0 kV to G06-44-4 (560583) 34.5 kV Two Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_545 | Single Phase Fault with Stuck Breaker on POSTROCK7 345.00 (530583) 345 kV Bus a. Apply Fault at the POSTROCK7 345.00 (530583) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. POSTROCK6 (530584) 230.0 kV to POSTROCK7 (530583) 345.0 kV to POSTROCK1 (530673) 13.8 kV Three Winding #1 b.2. POSTROCK6 (530584) 230.0 kV to S HAYS6 (530582) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_546 | Single Phase Fault with Stuck Breaker on GRDNCTY3 115.00 (531445) 115 kV Bus a. Apply Fault at the GRDNCTY3 115.00 (531445) 115 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRDNCTY3 (531445) 115.0 kV to HOLCOMB3 (531448) 115.0 kV Transmission Circuit #1 b.2. GRDNCTY3 (531445) 115.0 kV to SWNDTAP3 (531476) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_547 | Single Phase Fault with Stuck Breaker on SETAB 7 345.00 (531465) 345 kV Bus a. Apply Fault at the SETAB 7 345.00 (531465) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SETAB 7 (531465) 345.0 kV to MINGO 7 (531451) 345.0 kV Transmission Circuit #1 b.2. SETAB 7 (531465) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_548 | Single Phase Fault with Stuck Breaker on HARBNGR7 345.00 (531512) 345 kV Bus a. Apply Fault at the HARBNGR7 345.00 (531512) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HARBNGR7 (531512) 345.0 kV to CARPENTER 7 (523823) 345.0 kV Transmission Circuit #z1 b.2. HARBNGR7 (531512) 345.0 kV to HARBNGR3 (531510) 115.0 kV to HARBNGR-T (531511) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_549 | Single Phase Fault with Stuck Breaker on LANG 7 345.00 (532769) 345 kV Bus a. Apply Fault at the LANG 7 345.00 (532769) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LANG 3 (533304) 115.0 kV to LANG 7 (532769) 345.0 kV to LANG 1 (532808) 14.4 kV Three Winding #1 b.2. LANG 3 (533304) 115.0 kV to EAST ST3 (533301) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_550 | Single Phase Fault with Stuck Breaker on MORRIS 7 345.00 (532770) 345 kV Bus a. Apply Fault at the MORRIS 7 345.00 (532770) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MORRIS 6 (532863) 230.0 kV to MCDOWEL6 (532862) 230.0 kV Transmission Circuit #1 b.2. MORRIS 6 (532863) 230.0 kV to MORRIS 7 (532770) 345.0 kV to MORRIS1X1 (532809) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_551 | Single Phase Fault with Stuck Breaker on SWISVAL6 230.00 (532856) 230 kV Bus a. Apply Fault at the SWISVAL6 230.00 (532856) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWISVAL6 (532856) 230.0 kV to LAWHILL6 (532853) 230.0 kV Transmission Circuit #1 b.2. SWISVAL6 (532856) 230.0 kV to AUBURN 6 (532851) 230.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_552 | Single Phase Fault with Stuck Breaker on 87TH 7 345.00 (532775) 345 kV Bus a. Apply Fault at the 87TH 7 345.00 (532775) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. 87TH 3 (533283) 115.0 kV to 87TH 7 (532775) 345.0 kV to 87TH 1X1 (532818) 13.8 kV Three Winding #1 b.2. 87TH 3 (533283) 115.0 kV to TIMBRLN3 (533273) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_553 | Single Phase Fault with Stuck Breaker on BENTON 7 345.00 (532791) 345 kV Bus a. Apply Fault at the BENTON 7 345.00 (532791) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN1 1 (532821) 13.8 kV Three Winding #1 b.2. BENTON 4 (532986) 138.0 kV to BENTON 7 (532791) 345.0 kV to BENTN2 1 (532822) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_554 | Single Phase Fault with Stuck Breaker on ROSEHIL4 138.00 (533062) 138 kV Bus a. Apply Fault at the ROSEHIL4 138.00 (533062) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ROSEHIL4 (533062) 138.0 kV to ELPASO 4 (533039) 138.0 kV Transmission Circuit #1 b.2. ROSEHIL4 (533062) 138.0 kV to WEAVER 4 (532991) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_555 | Single Phase Fault with Stuck Breaker on CIRCLE 6 230.00 (532871) 230 kV Bus a. Apply Fault at the CIRCLE 6 230.00 (532871) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CIRCLE 3 (533413) 115.0 kV to CIRCLE 6 (532871) 230.0 kV to CIRCLE 1 (532892) 13.8 kV Three Winding #1 b.2. CIRCLE 3 (533413) 115.0 kV to HEC 3 (533419) 115.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_556 | Single Phase Fault with Stuck Breaker on NEOSHOS4 138.00 (533020) 138 kV Bus a. Apply Fault at the NEOSHOS4 138.00 (533020) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS4 (533020) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. NEOSHOS4 (533020) 138.0 kV to NEOSHO 4 (533021) 138.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_557 | Single Phase Fault with Stuck Breaker on BUTLERS4 138.00 (532989) 138 kV Bus a. Apply Fault at the BUTLERS4 138.00 (532989) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. BUTLERS2 (533609) 69.0 kV to FRNTR N2 (533593) 69.0 kV Transmission Circuit #1 b.2. BUTLERS2 (533609) 69.0 kV to BUTLERS4 (532989) 138.0 kV to BUTLER2X (533118) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_558 | Single Phase Fault with Stuck Breaker on MIDIANW2 69.000 (533597) 69 kV Bus a. Apply Fault at the MIDIANW2 69.000 (533597) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MIDIANW2 (533597) 69.0 kV to MIDIANE2 (533610) 69.0 kV Transmission Circuit #z1 b.2. MIDIANW2 (533597) 69.0 kV to CHESNEY2 (533589) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_559 | Single Phase Fault with Stuck Breaker on HALSTD 4 138.00 (533011) 138 kV Bus a. Apply Fault at the HALSTD 4 138.00 (533011) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HALSTED2 (533736) 69.0 kV to MUDCRKJ2 (533744) 69.0 kV Transmission Circuit #1 b.2. HALSTED2 (533736) 69.0 kV to HALSTD 4 (533011) 138.0 kV to HALST1 1 (533092) 13.2 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_560 | Single Phase Fault with Stuck Breaker on NEOSHO 4 138.00 (533021) 138 kV Bus a. Apply Fault at the NEOSHO 4 138.00 (533021) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHOS2 (533778) 69.0 kV to NEOSHO 4 (533021) 138.0 kV to NSES 2X1 (532710) 13.2 kV Three Winding #1 b.2. NEOSHOS2 (533778) 69.0 kV to BAKER 2 (532926) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_561 | Single Phase Fault with Stuck Breaker on NEOSHON4 138.00 (533022) 138 kV Bus a. Apply Fault at the NEOSHON4 138.00 (533022) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NEOSHON2 (533768) 69.0 kV to NEOSHON4 (533022) 138.0 kV to NEC U3 (532711) 12.0 kV Three Winding #1 b.2. NEOSHON2 (533768) 69.0 kV to NEOSHOS2 (533778) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_562 | Single Phase Fault with Stuck Breaker on CHISHLM2 69.000 (533786) 69 kV Bus a. Apply Fault at the CHISHLM2 69.000 (533786) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CHISHLM2 (533786) 69.0 kV to RIPLEYE2 (533859) 69.0 kV Transmission Circuit #1 b.2. CHISHLM2 (533786) 69.0 kV to GRANT 2 (533799) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_563 | Single Phase Fault with Stuck Breaker on COWSKIN2 69.000 (533788) 69 kV Bus a. Apply Fault at the COWSKIN2 69.000 (533788) 69 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COWSKIN2 (533788) 69.0 kV to WESTLNK2 (533854) 69.0 kV Transmission Circuit #1 b.2. COWSKIN2 (533788) 69.0 kV to GODDTAP2 (533879) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_564 | Single Phase Fault with Stuck Breaker on GILL E 4 138.00 (533044) 138 kV Bus a. Apply Fault at the GILL E 4 138.00 (533044) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL W 2 (533796) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 2 (533107) 13.2 kV Three Winding #1 b.2. GILL W 2 (533796) 69.0 kV to GILL E 4 (533044) 138.0 kV to GEC U3 (532733) 14.4 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_565 | Single Phase Fault with Stuck Breaker on GILL S 4 138.00 (533046) 138 kV Bus a. Apply Fault at the GILL S 4 138.00 (533046) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GILL E 2 (533795) 69.0 kV to GILL S 4 (533046) 138.0 kV to GILL S 1 (533106) 13.2 kV Three Winding #1 b.2. GILL E 2 (533795) 69.0 kV to GILLJCT2 (533798) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_566 | Single Phase Fault with Stuck Breaker on HOOVERS4 138.00 (533050) 138 kV Bus a. Apply Fault at the HOOVERS4 138.00 (533050) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOOVERS2 (533806) 69.0 kV to HOOVERS4 (533050) 138.0 kV to HOOVR1 1 (533108) 13.2 kV Three Winding #1 b.2. HOOVERS2 (533806) 69.0 kV to WATER2 2 (533856) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_567 | Single Phase Fault with Stuck Breaker on NOEASTE4 138.00 (533060) 138 kV Bus a. Apply Fault at the NOEASTE4 138.00 (533060) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOEASTE2 (533823) 69.0 kV to NOEASTE4 (533060) 138.0 kV to NEAST5X1 (533111) 13.2 kV Three Winding #1 b.2. NOEASTE2 (533823) 69.0 kV to NOEASTW2 (533822) 69.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_568 | Single Phase Fault with Stuck Breaker on NOEASTW4 138.00 (533061) 138 kV Bus a. Apply Fault at the NOEASTW4 138.00 (533061) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. NOEASTW2 (533822) 69.0 kV to NOEASTW4 (533061) 138.0 kV to NEAST3X1 (533110) 11.3 kV Three Winding #1 b.2. NOEASTW2 (533822) 69.0 kV to INNOVAT2 (533811) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_569 | Single Phase Fault with Stuck Breaker on MARMTNW5 161.00 (532935) 161 kV Bus a. Apply Fault at the MARMTNW5 161.00 (532935) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MARMTNW5 (532935) 161.0 kV to NEOSHO 5 (532937) 161.0 kV Transmission Circuit #1 b.2. MARMTNW5 (532935) 161.0 kV to MARMTNE5 (532934) 161.0 kV Transmission Circuit #z1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_570 | Single Phase Fault with Stuck Breaker on ALTOONA4 138.00 (533001) 138 kV Bus a. Apply Fault at the ALTOONA4 138.00 (533001) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ALTOONA4 (533001) 138.0 kV to G17-022-TAP (588664) 138.0 kV Transmission Circuit #1 b.2. ALTOONA4 (533001) 138.0 kV to TAYLOR 4 (533006) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_571 | Single Phase Fault with Stuck Breaker on LIBERTY4 138.00 (533003) 138 kV Bus a. Apply Fault at the LIBERTY4 138.00 (533003) 138 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LIBERTY4 (533003) 138.0 kV to TV1MNDV4 (533008) 138.0 kV Transmission Circuit #1 b.2. LIBERTY4 (533003) 138.0 kV to DEARING4 (533002) 138.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_572 | Single Phase Fault with Stuck Breaker on SPEARVL6 230.00 (539695) 230 kV Bus a. Apply Fault at the SPEARVL6 230.00 (539695) 230 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SPEARVL6 (539695) 230.0 kV to GRTBEND6 (539679) 230.0 kV Transmission Circuit #1 b.2. SPEARVL6 (539695) 230.0 kV to SPEARVL3 (539694) 115.0 kV to SPERVLTT (539935) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_573 | Single Phase Fault with Stuck Breaker on PECULR 7 345.00 (541198) 345 kV Bus a. Apply Fault at the PECULR 7 345.00 (541198) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. PECULR 5 (541342) 161.0 kV to PECULR 7 (541198) 345.0 kV to PECULRT (541372) 13.8 kV Three Winding #11 b.2. PECULR 5 (541342) 161.0 kV to BELTONS5 (541340) 161.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_574 | Single Phase Fault with Stuck Breaker on SIBLEY 7 345.00 (541201) 345 kV Bus a. Apply Fault at the SIBLEY 7 345.00 (541201) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SIBLEY 5 (541202) 161.0 kV to SIBLEYPL (541250) 161.0 kV Transmission Circuit #1 b.2. SIBLEY 5 (541202) 161.0 kV to SIBLEY 7 (541201) 345.0 kV to SIBLEY T (541360) 13.8 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_575 | Single Phase Fault with Stuck Breaker on HAWTH 7 345.00 (542972) 345 kV Bus a. Apply Fault at the HAWTH 7 345.00 (542972) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HAWTHN5 (543665) 161.0 kV to HAWTH 7 (542972) 345.0 kV to HAWT T20 (543644) 13.8 kV Three Winding #20 b.2. HAWTHN5 (543665) 161.0 kV to HAWTHS5 (542973) 161.0 kV Transmission Circuit # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_576 | Single Phase Fault with Stuck Breaker on CRAIG 7 345.00 (542977) 345 kV Bus a. Apply Fault at the CRAIG 7 345.00 (542977) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T11 (543641) 13.8 kV Three Winding #11 b.2. CRAIG 5 (542978) 161.0 kV to CRAIG 7 (542977) 345.0 kV to CRAI T22 (543642) 13.8 kV Three Winding #22 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_577 | Single Phase Fault with Stuck Breaker on LAC3_STAR7 345.00 (543667) 345 kV Bus a. Apply Fault at the LAC3_STAR7 345.00 (543667) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC3_STAR7 (543667) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h b.2. LAC3_STAR7 (543667) 345.0 kV to LAC3_Y1 (543662) 6.9 kV Two Winding #y | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_578 | Single Phase Fault with Stuck Breaker on LAC8_STAR7 345.00 (543669) 345 kV Bus a. Apply Fault at the LAC8_STAR7 345.00 (543669) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. LAC8_STAR7 (543669) 345.0 kV to LACYGNE7 (542981) 345.0 kV Transmission Circuit #h b.2. LAC8_STAR7 (543669) 345.0 kV to LAC8_Z1 (543672) 4.0 kV Two Winding #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_579 | Single Phase Fault with Stuck Breaker on IATAN 7 345.00 (542982) 345 kV Bus a. Apply Fault at the IATAN 7 345.00 (542982) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. IATAN5 (541350) 161.0 kV to WESTON 5 (541351) 161.0 kV Transmission Circuit #1 b.2. IATAN5 (541350) 161.0 kV to IATAN 7 (542982) 345.0 kV to IATAN 11 (541150) 14.4 kV Three Winding #11 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_580 | Single Phase Fault with Stuck Breaker on ORO110 5 161.00 (547467) 161 kV Bus a. Apply Fault at the ORO110 5 161.00 (547467) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. ORO110 2 (547534) 69.0 kV to ORO110 5 (547467) 161.0 kV to ORO110 1 (547703) 12.5 kV Three Winding #1 b.2. ORO110 2 (547534) 69.0 kV to WEB436 2 (547527) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_581 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 4 (547486) 138.0 kV to VINTAJC4 (510417) 138.0 kV Transmission Circuit #1 b.2. HOC404 4 (547486) 138.0 kV to HOC404 5 (547487) 161.0 kV to HOC404A1 (547715) 12.5 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_582 | Single Phase Fault with Stuck Breaker on HOC404 5 161.00 (547487) 161 kV Bus a. Apply Fault at the HOC404 5 161.00 (547487) 161 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOC404 2 (547601) 69.0 kV to HOC404 5 (547487) 161.0 kV to HOC404B1 (547716) 12.5 kV Three Winding #1 b.2. HOC404 2 (547601) 69.0 kV to QUA377 2 (547590) 69.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_583 | Single Phase Fault with Stuck Breaker on CBLUFFS3 345.00 (635000) 345 kV Bus a. Apply Fault at the CBLUFFS3 345.00 (635000) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF1XT9 (635025) 13.8 kV Three Winding #1 b.2. CBLUFFS5 (635001) 161.0 kV to CBLUFFS3 (635000) 345.0 kV to CBLF2XT9 (635026) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_584 | Single Phase Fault with Stuck Breaker on COOPER 3 345.00 (640139) 345 kV Bus a. Apply Fault at the COOPER 3 345.00 (640139) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. COOPER 3 (640139) 345.0 kV to ST JOE 7 (541199) 345.0 kV Transmission Circuit #1 b.2. COOPER 3 (640139) 345.0 kV to S3458 3 (645458) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Transfer | GROUP3_FAULT_585 | Single Phase Fault with Stuck Breaker on WAGENER 3 345.00 (650185) 345 kV Bus a. Apply Fault at the WAGENER 3 345.00 (650185) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. WAGENER 3 (650185) 345.0 kV to 103&ROKEBY3 (650189) 345.0 kV Transmission Circuit #1 b.2. WAGENER 3 (650185) 345.0 kV to WAGENER 7 (650285) 115.0 kV to WAGENER1 9 (650385) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_90 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_91 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_92 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_328 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to REMSEN 3 (635398) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Divergence of simulation due to low voltage after fault unable to be recovered | Reclosing Removed
02 - Nebraska | 25S | Base | GROUP2_FAULT_366 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_367 | 3 Phase fault on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_380 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_59 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to THEDFRD3 (640500) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_61 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.10. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.11. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.12. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_115 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_119 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_122 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_478 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.10. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.11. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.12. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.13. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_537 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_542 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_543 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_544 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_545 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_546 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_547 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_548 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_549 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_550 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_551 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_554 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_556 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_626 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_654 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 b.2. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_655 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_672 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_705 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_709 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_720 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_721 | Single Phase Fault with Stuck Breaker on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply Fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z b.2. GRPRAR2-LNX3 (652833) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_723 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z b.2. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25S | Base | GROUP2_FAULT_762 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25S | Base | GROUP3_FAULT_342 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations
02 - Nebraska | 25W | Base | GROUP2_FAULT_90 | 3 Phase fault on GR PRAIRIE 3345.00 (652532) 345 kV Bus a. Apply fault at the GR PRAIRIE 3345.00 (652532) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_91 | 3 Phase fault on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_92 | 3 Phase fault on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_327 | 3 Phase fault on RAUN 3 345.00 (635200) 345 kV Bus a. Apply fault at the RAUN 3 345.00 (635200) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. RAUN 3 (635200) 345.0 kV to J412 POI 3 (635252) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | No | Divergence of simulation due to low voltage after fault unable to be recovered | Reclosing Removed
02 - Nebraska | 25W | Base | GROUP2_FAULT_366 | 3 Phase fault on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. THEDFRD3 (640500) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_61 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD4 (640200) 230.0 kV to GR ISLD3 (653571) 345.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.10. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.11. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.12. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_115 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #2 b.2. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_119 | Single Phase Fault with Stuck Breaker on SWEET W3 345.00 (640374) 345 kV Bus a. Apply Fault at the SWEET W3 345.00 (640374) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_130 | Single Phase Fault with Stuck Breaker on AXTELL 3 345.00 (640065) 345 kV Bus a. Apply Fault at the AXTELL 3 345.00 (640065) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. AXTELL 3 (640065) 345.0 kV to PAULINE3 (640312) 345.0 kV Transmission Circuit #1 b.2. POSTROCK7 (530583) 345.0 kV to G16-050-TAP (560082) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_472 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP19 (652273) 13.8 kV Three Winding #1 b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to FTTHMP29 (652274) 13.8 kV Three Winding #1 b.7. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.9. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.10. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.11. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.12. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.13. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_529 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_534 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.3. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.4. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.5. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 b.8. FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV to None Three Winding #1 b.9. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.10. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_535 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_536 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_537 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_538 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_539 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_540 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP19 (652273) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_541 | Single Phase Fault with Stuck Breaker on FTTHOM1-LNX3345.00 (652806) 345 kV Bus a. Apply Fault at the FTTHOM1-LNX3345.00 (652806) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.3. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.4. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.5. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_542 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHMP29 (652274) 13.8 kV to FTTHOMP3 (652506) 345.0 kV to FTTHOMP4 (652507) 230.0 kV Three Winding #1 b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.3. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 b.4. GR PRAIRIE 3 (652532) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_543 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_546 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_548 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. MCCOOL 3 (640271) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.2. SWEET W3 (640374) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #1 b.3. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.4. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISLD T6 9 (643071) 13.8 kV Three Winding #3 b.5. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL19 (653314) 13.8 kV Three Winding #1 b.6. GR ISLD3 (653571) 345.0 kV to GR ISLD4 (640200) 230.0 kV to GR ISL29 (653316) 13.8 kV Three Winding #2 b.7. GR ISLD3 (653571) 345.0 kV to Switched Shunt Device # | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_618 | Single Phase Fault with Stuck Breaker on TRIPLEH__UA3345.00 (659433) 345 kV Bus a. Apply Fault at the TRIPLEH__UA3345.00 (659433) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX3 (652806) 345.0 kV Transmission Circuit #z b.2. FTTHOM1-LNX3 (652806) 345.0 kV to CHAPELLE-BE3 (659130) 345.0 kV Transmission Circuit #1 b.3. LELAND_O-BE3 (659105) 345.0 kV to LO.LS-FT-BE3 (659424) 345.0 kV Transmission Circuit #z b.4. LO.LS-FT-BE3 (659424) 345.0 kV to CC.LS-LO-BE3 (659428) 345.0 kV Transmission Circuit #1 b.5. CHAPELLE-BE3 (659130) 345.0 kV to TRIPLEH__UA3 (659433) 345.0 kV Transmission Circuit #1 b.6. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH1B-UA9 (659434) 34.5 kV to TRPLHH1T-UA9 (659435) 13.8 kV Three Winding #1 b.7. TRIPLEH__UA3 (659433) 345.0 kV to TRPLHH2B-UA9 (659438) 34.5 kV to TRPLHH2T-UA9 (659439) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_645 | Single Phase Fault with Stuck Breaker on THEDFRD3 345.00 (640500) 345 kV Bus a. Apply Fault at the THEDFRD3 345.00 (640500) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. THEDFRD3 (640500) 345.0 kV to GENTLMN3 (640183) 345.0 kV Transmission Circuit #1 b.2. THEDFRD3 (640500) 345.0 kV to THEDFRD7 (640381) 115.0 kV to THEDFORD9 (640570) 13.8 kV Three Winding #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_646 | Single Phase Fault with Stuck Breaker on HOLT.CO3 345.00 (640510) 345 kV Bus a. Apply Fault at the HOLT.CO3 345.00 (640510) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. HOLT.CO3 (640510) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #1 b.2. HOLT.CO3 (640510) 345.0 kV to GRPRAR1-LNX3 (652832) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_663 | Single Phase Fault with Stuck Breaker on GRPRAR1-LNX3345.00 (652832) 345 kV Bus a. Apply Fault at the GRPRAR1-LNX3345.00 (652832) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR1-LNX3 (652832) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 b.2. GRPRAR1-LNX3 (652832) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_696 | Single Phase Fault with Stuck Breaker on FTTHOMP3 345.00 (652506) 345 kV Bus a. Apply Fault at the FTTHOMP3 345.00 (652506) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOMP3 (652506) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #z b.2. FTTHOMP3 (652506) 345.0 kV to FTTHOM1-LNX5 (652808) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_700 | Single Phase Fault with Stuck Breaker on GR ISLD3 345.00 (653571) 345 kV Bus a. Apply Fault at the GR ISLD3 345.00 (653571) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD3 (653571) 345.0 kV to GR ISLD-LNX3 (653871) 345.0 kV Transmission Circuit #z b.2. GR ISLD3 (653571) 345.0 kV to MCCOOL 3 (640271) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_711 | Single Phase Fault with Stuck Breaker on FTTHOM2-LNX3345.00 (652807) 345 kV Bus a. Apply Fault at the FTTHOM2-LNX3345.00 (652807) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. FTTHOM2-LNX3 (652807) 345.0 kV to FTTHOMP3 (652506) 345.0 kV Transmission Circuit #z b.2. FTTHOM2-LNX3 (652807) 345.0 kV to GRPRAR2-LNX3 (652833) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_712 | Single Phase Fault with Stuck Breaker on GRPRAR2-LNX3345.00 (652833) 345 kV Bus a. Apply Fault at the GRPRAR2-LNX3345.00 (652833) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GRPRAR2-LNX3 (652833) 345.0 kV to GR PRAIRIE 3 (652532) 345.0 kV Transmission Circuit #z b.2. GRPRAR2-LNX3 (652833) 345.0 kV to FTTHOM2-LNX3 (652807) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_714 | Single Phase Fault with Stuck Breaker on GR ISLD-LNX3345.00 (653871) 345 kV Bus a. Apply Fault at the GR ISLD-LNX3345.00 (653871) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GR ISLD-LNX3 (653871) 345.0 kV to GR ISLD3 (653571) 345.0 kV Transmission Circuit #z b.2. GR ISLD-LNX3 (653871) 345.0 kV to HOLT.CO3 (640510) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
02 - Nebraska | 25W | Base | GROUP2_FAULT_754 | Single Phase Fault with Stuck Breaker on GENTLMN3 345.00 (640183) 345 kV Bus a. Apply Fault at the GENTLMN3 345.00 (640183) 345 kV Bus b. Clear Fault after 16 cycles and trip the following elements: b.1. GENTLMN3 (640183) 345.0 kV to REDWILO3 (640325) 345.0 kV Transmission Circuit #1 b.2. GENTLMN3 (640183) 345.0 kV to SWEET W3 (640374) 345.0 kV Transmission Circuit #1 | P4 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
03 - Central | 25W | Base | GROUP3_FAULT_342 | 3 Phase fault on FINNEY 7345.00 (523853) 345 kV Bus a. Apply fault at the FINNEY 7345.00 (523853) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FINNEY 7 (523853) 345.0 kV to HOLCOMB7 (531449) 345.0 kV Transmission Circuit #1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the fault | P1 | Yes | Yes | Yes | Yes | Yes | No | Yes | Low voltage and controller oscillations
04 - Southeast | 25S | Transfer | 116JENK4__R_S_S__4 | 3 Phase fault on 116JENK4 (509753) 138 kV Bus a. Apply fault at the 116JENK4 (509753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 116JENK4 138.0 KV 509753 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 116JENK4__R_S_S__4 | 3 Phase fault on 116JENK4 (509753) 138 kV Bus a. Apply fault at the 116JENK4 (509753) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 116JENK4 138.0 KV 509753 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 136YALE4__R_S_S__4 | 3 Phase fault on 136YALE4 (509775) 138 kV Bus a. Apply fault at the 136YALE4 (509775) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138.0 KV 509775 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 136YALE4__R_S_S__4 | 3 Phase fault on 136YALE4 (509775) 138 kV Bus a. Apply fault at the 136YALE4 (509775) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 136YALE4 138.0 KV 509775 TO R.S.S.-4 138.0 KV 509783 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 2CARNEY__2LUTHER | 3 Phase fault on 2CARNEY (300834) 69 kV Bus a. Apply fault at the 2CARNEY (300834) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CARNEY 69.0 KV 300834 TO 2LUTHER 69.0 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 2CARNEY__2LUTHER | 3 Phase fault on 2CARNEY (300834) 69 kV Bus a. Apply fault at the 2CARNEY (300834) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2CARNEY 69.0 KV 300834 TO 2LUTHER 69.0 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 2MERIDAN__2LUTHER | 3 Phase fault on 2MERIDAN (300839) 69 kV Bus a. Apply fault at the 2MERIDAN (300839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MERIDAN 69.0 KV 300839 TO 2LUTHER 69.0 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 2MERIDAN__2LUTHER | 3 Phase fault on 2MERIDAN (300839) 69 kV Bus a. Apply fault at the 2MERIDAN (300839) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 2MERIDAN 69.0 KV 300839 TO 2LUTHER 69.0 KV 300856 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 36&MER_4__HOBBYLO4 | 3 Phase fault on 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138.0 KV 514888 TO HOBBYLO4 138.0 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 36&MER_4__HOBBYLO4 | 3 Phase fault on 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138.0 KV 514888 TO HOBBYLO4 138.0 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | 36&MER_4__SW_5TH_4 | 3 Phase fault on 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138.0 KV 514888 TO SW 5TH 4 138.0 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 36&MER_4__SW_5TH_4 | 3 Phase fault on 36&MER 4 (514888) 138 kV Bus a. Apply fault at the 36&MER 4 (514888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 36&MER 4 138.0 KV 514888 TO SW 5TH 4 138.0 KV 514920 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | 38TH_ST2__514846_0 | 3 Phase fault on 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2( 514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 514845 TO 38TH ST4 514846 TO 38TH ST1 515768 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 38TH_ST2__514846_0 | 3 Phase fault on 38TH ST2 (514845) 69 kV Bus a. Apply fault at the 38TH ST2( 514845) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST2 514845 TO 38TH ST4 514846 TO 38TH ST1 515768 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 38TH_ST4__TULSA__4 | 3 Phase fault on 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST4 138.0 KV 514846 TO TULSA 4 138.0 KV 514847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 38TH_ST4__TULSA__4 | 3 Phase fault on 38TH ST4 (514846) 138 kV Bus a. Apply fault at the 38TH ST4 (514846) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 38TH ST4 138.0 KV 514846 TO TULSA 4 138.0 KV 514847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3ADA_LA__3MINDEN_LA! | 3 Phase fault on 3ADA_LA (337360) 115 kV Bus a. Apply fault at the 3ADA_LA (337360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3ADA_LA 115.0 KV 337360 TO 3MINDEN_LA! 115.0 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3ADA_LA__3MINDEN_LA! | 3 Phase fault on 3ADA_LA (337360) 115 kV Bus a. Apply fault at the 3ADA_LA (337360) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3ADA_LA 115.0 KV 337360 TO 3MINDEN_LA! 115.0 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3COUCH%__3HOPE_E# | 3 Phase fault on 3COUCH% (337502) 115 kV Bus a. Apply fault at the 3COUCH% (337502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3COUCH% 115.0 KV 337502 TO 3HOPE.E# 115.0 KV 338848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3COUCH%__3HOPE_E# | 3 Phase fault on 3COUCH% (337502) 115 kV Bus a. Apply fault at the 3COUCH% (337502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3COUCH% 115.0 KV 337502 TO 3HOPE.E# 115.0 KV 338848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3COUCH%__3LEWISVILLE# | 3 Phase fault on 3COUCH% (337502) 115 kV Bus a. Apply fault at the 3COUCH% (337502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3COUCH% 115.0 KV 337502 TO 3LEWISVILLE# 115.0 KV 338874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3COUCH%__3LEWISVILLE# | 3 Phase fault on 3COUCH% (337502) 115 kV Bus a. Apply fault at the 3COUCH% (337502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3COUCH% 115.0 KV 337502 TO 3LEWISVILLE# 115.0 KV 338874 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3COUCH%__3MCNEIL! | 3 Phase fault on 3COUCH% (337502) 115 kV Bus a. Apply fault at the 3COUCH% (337502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3COUCH% 115.0 KV 337502 TO 3MCNEIL! 115.0 KV 337516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3COUCH%__3MCNEIL! | 3 Phase fault on 3COUCH% (337502) 115 kV Bus a. Apply fault at the 3COUCH% (337502) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3COUCH% 115.0 KV 337502 TO 3MCNEIL! 115.0 KV 337516 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3EL_DORADO!__3ELD_DONAN | 3 Phase fault on 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115.0 KV 337539 TO 3ELD DONAN 115.0 KV 337540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3EL_DORADO!__3ELD_DONAN | 3 Phase fault on 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115.0 KV 337539 TO 3ELD DONAN 115.0 KV 337540 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3EL_DORADO!__3ELD_QUINN | 3 Phase fault on 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115.0 KV 337539 TO 3ELD QUINN 115.0 KV 337560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3EL_DORADO!__3ELD_QUINN | 3 Phase fault on 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115.0 KV 337539 TO 3ELD QUINN 115.0 KV 337560 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3EL_DORADO!__3ELDORADO_E! | 3 Phase fault on 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115.0 KV 337539 TO 3ELDORADO.E! 115.0 KV 337553 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3EL_DORADO!__3ELDORADO_E! | 3 Phase fault on 3EL DORADO! (337539) 115 kV Bus a. Apply fault at the 3EL DORADO! (337539) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3EL DORADO! 115.0 KV 337539 TO 3ELDORADO.E! 115.0 KV 337553 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3KERLIN+__3EMERSON! | 3 Phase fault on 3KERLIN+ (337524) 115 kV Bus a. Apply fault at the 3KERLIN+ (337524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3KERLIN+ 115.0 KV 337524 TO 3EMERSON! 115.0 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3KERLIN+__3EMERSON! | 3 Phase fault on 3KERLIN+ (337524) 115 kV Bus a. Apply fault at the 3KERLIN+ (337524) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3KERLIN+ 115.0 KV 337524 TO 3EMERSON! 115.0 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3MINDEN_LA!__3LA_ORD_PLNT | 3 Phase fault on 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO 3LA_ORD_PLNT 115.0 KV 337362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3MINDEN_LA!__3LA_ORD_PLNT | 3 Phase fault on 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO 3LA_ORD_PLNT 115.0 KV 337362 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3MINDEN_LA!__3SAREPTA! | 3 Phase fault on 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO 3SAREPTA! 115.0 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3MINDEN_LA!__3SAREPTA! | 3 Phase fault on 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO 3SAREPTA! 115.0 KV 337363 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3MINDEN_LA!__MINDEN_3 | 3 Phase fault on 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO MINDEN-3 115.0 KV 507788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3MINDEN_LA!__MINDEN_3 | 3 Phase fault on 3MINDEN_LA! (337361) 115 kV Bus a. Apply fault at the 3MINDEN_LA! (337361) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LA! 115.0 KV 337361 TO MINDEN-3 115.0 KV 507788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3MINDEN_LG__3MINDEN_LA! | 3 Phase fault on 3MINDEN_LG (303302) 115 kV Bus a. Apply fault at the 3MINDEN_LG (303302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LG 115.0 KV 303302 TO 3MINDEN_LA! 115.0 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3MINDEN_LG__3MINDEN_LA! | 3 Phase fault on 3MINDEN_LG (303302) 115 kV Bus a. Apply fault at the 3MINDEN_LG (303302) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3MINDEN_LG 115.0 KV 303302 TO 3MINDEN_LA! 115.0 KV 337361 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3SAREPTA!__3COUCH% | 3 Phase fault on 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3SPRINGHILL 115.0 KV 337365 CKT 1 b.2.LOAD 1 337365 b.3. 3SPRINGHILL 115.0 KV 337365 TO 3TAYLOR 115.0 KV 337500 CKT 1 b.4. LOAD 1 337500 b.5. 3TAYLOR 115.0 KV 337500 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.6. LOAD IN 337514 b.7. 3MAGNLIA DOW 115.0 KV 337501 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.8. LOAD IN 337514 b.9 3MAGNLIA DOW 115.0 KV 337501 TO 3COUCH% 115.0 KV 337502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3SAREPTA!__3COUCH% | 3 Phase fault on 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3SPRINGHILL 115.0 KV 337365 CKT 1 b.2.LOAD 1 337365 b.3. 3SPRINGHILL 115.0 KV 337365 TO 3TAYLOR 115.0 KV 337500 CKT 1 b.4. LOAD 1 337500 b.5. 3TAYLOR 115.0 KV 337500 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.6. LOAD IN 337514 b.7. 3MAGNLIA DOW 115.0 KV 337501 TO 3MACEDONA 115.0 KV 337514 CKT 1 b.8. LOAD IN 337514 b.9 3MAGNLIA DOW 115.0 KV 337501 TO 3COUCH% 115.0 KV 337502 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3SAREPTA!__3CULLEN | 3 Phase fault on 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3CULLEN 115.0 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3SAREPTA!__3CULLEN | 3 Phase fault on 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3CULLEN 115.0 KV 337364 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3SAREPTA!__3EMERSON! | 3 Phase fault on 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3HAYNESVILLE 115.0 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 3HAYNESVILLE 115.0 KV 337366 TO 3EMERSON! 115.0 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3SAREPTA!__3EMERSON! | 3 Phase fault on 3SAREPTA! (337363) 115 kV Bus a. Apply fault at the 3SAREPTA! (337363) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SAREPTA! 115.0 KV 337363 TO 3HAYNESVILLE 115.0 KV 337366 CKT 1 b.2. LOAD 1 337366 b.3. LOAD LG 337366 3HAYNESVILLE 115.0 KV 337366 TO 3EMERSON! 115.0 KV 337526 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 3SMACKOVER+__3EL_DORADO! | 3 Phase fault on 3SMACKOVER+ (337537) 115 kV Bus a. Apply fault at the 3SMACKOVER+ (337537) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SMACKOVER+ 115.0 KV 337537 TO 3EL DORADO! 115.0 KV 337539 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 3SMACKOVER+__3EL_DORADO! | 3 Phase fault on 3SMACKOVER+ (337537) 115 kV Bus a. Apply fault at the 3SMACKOVER+ (337537) 115 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 3SMACKOVER+ 115.0 KV 337537 TO 3EL DORADO! 115.0 KV 337539 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 44&SUNL2__SUNNYLN2 | 3 Phase fault on 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69.0 KV 514979 TO SUNNYLN2 69.0 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 44&SUNL2__SUNNYLN2 | 3 Phase fault on 44&SUNL2 (514979) 69 kV Bus a. Apply fault at the 44&SUNL2 (514979) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 44&SUNL2 69.0 KV 514979 TO SUNNYLN2 69.0 KV 514980 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4LUTHER__4MEMORALT | 3 Phase fault on 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138.0 KV 300135 TO 4MEMORALT 138.0 KV 300136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 4LUTHER__4MEMORALT | 3 Phase fault on 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138.0 KV 300135 TO 4MEMORALT 138.0 KV 300136 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4LUTHER__4STROUD138 | 3 Phase fault on 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138.0 KV 300135 TO 4LUTHERD 138.0 KV 301372 CKT 1 b.2. LOAD 1 301372 b.3. 4WARWICK 138.0 KV 300915 TO 4LUTHERD 138.0 KV 301372 CKT 1 b.4. LOAD 1 301372 b.5. 4STROUD138 138.0 KV 300914 TO 4WARWICK 138.0 KV 300915 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 4LUTHER__4STROUD138 | 3 Phase fault on 4LUTHER (300135) 138 kV Bus a. Apply fault at the 4LUTHER (300135) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4LUTHER 138.0 KV 300135 TO 4LUTHERD 138.0 KV 301372 CKT 1 b.2. LOAD 1 301372 b.3. 4WARWICK 138.0 KV 300915 TO 4LUTHERD 138.0 KV 301372 CKT 1 b.4. LOAD 1 301372 b.5. 4STROUD138 138.0 KV 300914 TO 4WARWICK 138.0 KV 300915 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4MEMORALT__4MEMORAL | 3 Phase fault on 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138.0 KV 300136 TO 4MEMORAL 138.0 KV 301541 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | 4MEMORALT__4MEMORAL | 3 Phase fault on 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138.0 KV 300136 TO 4MEMORAL 138.0 KV 301541 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4MEMORALT__JNSKAMO4 | 3 Phase fault on 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138.0 KV 300136 TO JNSKAMO4 138.0 KV 514906 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | 4MEMORALT__JNSKAMO4 | 3 Phase fault on 4MEMORALT (300136) 138 kV Bus a. Apply fault at the 4MEMORALT (300136) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MEMORALT 138.0 KV 300136 TO JNSKAMO4 138.0 KV 514906 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4MURFBORO__SNASHVL4 | 3 Phase fault on 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 138.0 KV 337672 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 4MURFBORO__SNASHVL4 | 3 Phase fault on 4MURFBORO (337672) 138 kV Bus a. Apply fault at the 4MURFBORO (337672) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4MURFBORO 138.0 KV 337672 TO SNASHVL4 138.0 KV 507434 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 4STROUDDIST__4STROUD138 | 3 Phase fault on 4STROUDDIST (300838) 138 kV Bus a. Apply fault at the 4STROUDDIST (300838) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STROUDDIST 138.0 KV 300838 TO 4STROUD138 138.0 KV 300914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 4STROUDDIST__4STROUD138 | 3 Phase fault on 4STROUDDIST (300838) 138 kV Bus a. Apply fault at the 4STROUDDIST (300838) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 4STROUDDIST 138.0 KV 300838 TO 4STROUD138 138.0 KV 300914 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 52DEL_W4__S_HILLW4 | 3 Phase fault on 52DEL-W4 (509856) 138 kV Bus a. Apply fault at the 52DEL-W4 (509856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DEL-W4 138.0 KV 509856 TO S HILLW4 138.0 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 52DEL_W4__S_HILLW4 | 3 Phase fault on 52DEL-W4 (509856) 138 kV Bus a. Apply fault at the 52DEL-W4 (509856) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DEL-W4 138.0 KV 509856 TO S HILLW4 138.0 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 52DELTP4__T_S_E__4 | 3 Phase fault on 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138.0 KV 509776 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | 52DELTP4__T_S_E__4 | 3 Phase fault on 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138.0 KV 509776 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 52DELTP4__ZUNIS_S4 | 3 Phase fault on 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138.0 KV 509776 TO ZUNIS-S4 138.0 KV 509826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | 52DELTP4__ZUNIS_S4 | 3 Phase fault on 52DELTP4 (509776) 138 kV Bus a. Apply fault at the 52DELTP4 (509776) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELTP4 138.0 KV 509776 TO ZUNIS-S4 138.0 KV 509826 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 52DELWT4__S_HILLW4 | 3 Phase fault on 52DELWT4 (509814) 138 kV Bus a. Apply fault at the 52DELWT4 (509814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELWT4 138.0 KV 509814 TO S HILLW4 138.0 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | 52DELWT4__S_HILLW4 | 3 Phase fault on 52DELWT4 (509814) 138 kV Bus a. Apply fault at the 52DELWT4 (509814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 52DELWT4 138.0 KV 509814 TO S HILLW4 138.0 KV 509859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 53CACHE4__ARTVLTP4 | 3 Phase fault on 53CACHE4 (511509) 138 kV Bus a. Apply fault at the 53CACHE4 (511509) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53CACHE4 138.0 KV 511509 TO ARTVLTP4 138.0 KV 511537 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 53GARNT4__T_S_E__4 | 3 Phase fault on 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138.0 KV 509762 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | 53GARNT4__T_S_E__4 | 3 Phase fault on 53GARNT4 (509762) 138 kV Bus a. Apply fault at the 53GARNT4 (509762) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARNT4 138.0 KV 509762 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 53GARST4__T_S_E__4 | 3 Phase fault on 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138.0 KV 509763 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 53GARST4__T_S_E__4 | 3 Phase fault on 53GARST4 (509763) 138 kV Bus a. Apply fault at the 53GARST4 (509763) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 53GARST4 138.0 KV 509763 TO T.S.E.-4 138.0 KV 509811 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 5CDRCRST__TAHLQH_5 | 3 Phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161.0 KV 301344 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 5CDRCRST__TAHLQH_5 | 3 Phase fault on 5CDRCRST (301344) 161 kV Bus a. Apply fault at the 5CDRCRST (301344) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5CDRCRST 161.0 KV 301344 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 5PARK__TAHLQH_5 | 3 Phase fault on 5PARK (301307) 161 kV Bus a. Apply fault at the 5PARK (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161.0 KV 301307 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 5PARK__TAHLQH_5 | 3 Phase fault on 5PARK (301307) 161 kV Bus a. Apply fault at the 5PARK (301307) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5PARK 161.0 KV 301307 TO TAHLQH 5 161.0 KV 512655 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 5TRIBES2__515228_0 | 3 Phase fault on 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2( 515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES2 515227 TO 5TRIBES5 515228 TO 5TRIBES1 515723 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 5TRIBES2__515228_0 | 3 Phase fault on 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2( 515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES2 515227 TO 5TRIBES5 515228 TO 5TRIBES1 515723 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 5TRIBES2__AGENCY_2 | 3 Phase fault on 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENYSON2 69.0 KV 515217 TO 5TRIBES2 69.0 KV 515227 CKT 1 b.2. HONORHT2 69.0 KV 515216 TO TENYSON2 69.0 KV 515217 CKT 1 b.3. LOAD 1 515217 b.4. HONORHT2 69.0 KV 515216 TO AGENCY 2 69.0 KV 515229 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 5TRIBES2__AGENCY_2 | 3 Phase fault on 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. TENYSON2 69.0 KV 515217 TO 5TRIBES2 69.0 KV 515227 CKT 1 b.2. HONORHT2 69.0 KV 515216 TO TENYSON2 69.0 KV 515217 CKT 1 b.3. LOAD 1 515217 b.4. HONORHT2 69.0 KV 515216 TO AGENCY 2 69.0 KV 515229 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | 5TRIBES2__WELLSPA2 | 3 Phase fault on 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHECOTA2 69.0 KV 515201 TO 5TRIBES2 69.0 KV 515227 CKT 1 b.2. CHECOTA2 69.0 KV 515201 TO WELLS 2 69.0 KV 515202 CKT 1 b.3. LOAD 1 515202 b.4. WELLS 2 69.0 KV 515202 TO WELLSPA2 69.0 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 5TRIBES2__WELLSPA2 | 3 Phase fault on 5TRIBES2 (515227) 69 kV Bus a. Apply fault at the 5TRIBES2 (515227) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHECOTA2 69.0 KV 515201 TO 5TRIBES2 69.0 KV 515227 CKT 1 b.2. CHECOTA2 69.0 KV 515201 TO WELLS 2 69.0 KV 515202 CKT 1 b.3. LOAD 1 515202 b.4. WELLS 2 69.0 KV 515202 TO WELLSPA2 69.0 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 5TRIBES5__MUSKOGE5 | 3 Phase fault on 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161.0 KV 515228 TO HANCOK-5 161.0 KV 515250 CKT 1 b.2. LOAD 1 515250 b.3. HANCOK-5 161.0 KV 515250 TO THRERVR5 161.0 KV 515640 CKT 1 b.4. LOAD 1 515640 b.5. MUSKOGE5 161.0 KV 515222 TO THRERVR5 161.0 KV 515640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 5TRIBES5__MUSKOGE5 | 3 Phase fault on 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161.0 KV 515228 TO HANCOK-5 161.0 KV 515250 CKT 1 b.2. LOAD 1 515250 b.3. HANCOK-5 161.0 KV 515250 TO THRERVR5 161.0 KV 515640 CKT 1 b.4. LOAD 1 515640 b.5. MUSKOGE5 161.0 KV 515222 TO THRERVR5 161.0 KV 515640 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 5TRIBES5__PECANCK5 | 3 Phase fault on 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161.0 KV 515228 TO PECANCK5 161.0 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | 5TRIBES5__PECANCK5 | 3 Phase fault on 5TRIBES5 (515228) 161 kV Bus a. Apply fault at the 5TRIBES5 (515228) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 5TRIBES5 161.0 KV 515228 TO PECANCK5 161.0 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 77MEM_W4__E_61ST_4 | 3 Phase fault on 77MEM-W4 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 138.0 KV 509766 TO E.61ST-4 138.0 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | 77MEM_W4__E_61ST_4 | 3 Phase fault on 77MEM-W4 (509766) 138 kV Bus a. Apply fault at the 77MEM-W4 (509766) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 77MEM-W4 138.0 KV 509766 TO E.61ST-4 138.0 KV 509831 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 7SAREPTA%__7EL_DORADO | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 7SAREPTA%__7EL_DORADO | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO 7EL DORADO 345.0 KV 337562 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 7SAREPTA%__LONGWD_7 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 7SAREPTA%__LONGWD_7 | 3 Phase fault on 7SAREPTA% (337376) 345 kV Bus a. Apply fault at the 7SAREPTA% (337376) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 7SAREPTA% 345.0 KV 337376 TO LONGWD 7 345.0 KV 508809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 81YALEN4__81YALTP4 | 3 Phase fault on 81YALEN4 (509730) 138 kV Bus a. Apply fault at the 81YALEN4 (509730) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALEN4 138.0 KV 509730 TO 81YALTP4 138.0 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 81YALEN4__81YALTP4 | 3 Phase fault on 81YALEN4 (509730) 138 kV Bus a. Apply fault at the 81YALEN4 (509730) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALEN4 138.0 KV 509730 TO 81YALTP4 138.0 KV 509809 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 81YALTP4__SHILETP4 | 3 Phase fault on 81YALTP4 (509809) 138 kV Bus a. Apply fault at the 81YALTP4 (509809) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138.0 KV 509809 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 81YALTP4__SHILETP4 | 3 Phase fault on 81YALTP4 (509809) 138 kV Bus a. Apply fault at the 81YALTP4 (509809) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 81YALTP4 138.0 KV 509809 TO SHILETP4 138.0 KV 509813 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 84TH_ST4__BELISLE4 | 3 Phase fault on 84TH ST4 (514843) 138 kV Bus a. Apply fault at the 84TH ST4 (514843) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84TH ST4 138.0 KV 514843 TO BELISLE4 138.0 KV 514844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 84TH_ST4__BELISLE4 | 3 Phase fault on 84TH ST4 (514843) 138 kV Bus a. Apply fault at the 84TH ST4 (514843) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. 84TH ST4 138.0 KV 514843 TO BELISLE4 138.0 KV 514844 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8ANO%__337912_0 | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO%( 337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8ANO%__337912_0 | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO%( 337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 337909 TO 5ANO% 337912 TO 1ANO AUX 337913 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8ANO%__8P_HILL% | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 8P.HILL% 500.0 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | 8ANO%__8P_HILL% | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO 8P.HILL% 500.0 KV 337922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8ANO%__FTSMITH8 | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO FTSMITH8 500.0 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8ANO%__FTSMITH8 | 3 Phase fault on 8ANO% (337909) 500 kV Bus a. Apply fault at the 8ANO% (337909) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8ANO% 500.0 KV 337909 TO FTSMITH8 500.0 KV 515305 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8EL_DORADO%__337539_0 | 3 Phase fault on 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO%( 337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8EL_DORADO%__337539_0 | 3 Phase fault on 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO%( 337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 3EL DORADO! 337539 TO 1EL DORADO3 337566 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8EL_DORADO%__337562_0 | 3 Phase fault on 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO%( 337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8EL_DORADO%__337562_0 | 3 Phase fault on 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO%( 337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 337561 TO 7EL DORADO 337562 TO 1EL DORADO2 337565 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8EL_DORADO%__8PANDA% | 3 Phase fault on 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8EL_DORADO%__8PANDA% | 3 Phase fault on 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8PANDA% 500.0 KV 338440 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8EL_DORADO%__8SHERIDAN% | 3 Phase fault on 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8SHERIDAN% 500.0 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8EL_DORADO%__8SHERIDAN% | 3 Phase fault on 8EL DORADO% (337561) 500 kV Bus a. Apply fault at the 8EL DORADO% (337561) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8EL DORADO% 500.0 KV 337561 TO 8SHERIDAN% 500.0 KV 337643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8HAPPYVALY%__8ANO% | 3 Phase fault on 8HAPPYVALY% (337811) 500 kV Bus a. Apply fault at the 8HAPPYVALY% (337811) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8ANO% 500.0 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8HAPPYVALY%__8ANO% | 3 Phase fault on 8HAPPYVALY% (337811) 500 kV Bus a. Apply fault at the 8HAPPYVALY% (337811) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8HAPPYVALY% 500.0 KV 337811 TO 8ANO% 500.0 KV 337909 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8MCNEIL%__8EL_DORADO% | 3 Phase fault on 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500.0 KV 337515 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8MCNEIL%__8EL_DORADO% | 3 Phase fault on 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500.0 KV 337515 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8MCNEIL%__8ETTA% | 3 Phase fault on 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500.0 KV 337515 TO 8ETTA% 500.0 KV 337754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8MCNEIL%__8ETTA% | 3 Phase fault on 8MCNEIL% (337515) 500 kV Bus a. Apply fault at the 8MCNEIL% (337515) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MCNEIL% 500.0 KV 337515 TO 8ETTA% 500.0 KV 337754 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8MT_OLIVE%__8EL_DORADO% | 3 Phase fault on 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500.0 KV 337368 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8MT_OLIVE%__8EL_DORADO% | 3 Phase fault on 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500.0 KV 337368 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8MT_OLIVE%__LAYFLD8 | 3 Phase fault on 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500.0 KV 337368 TO LAYFLD8 500.0 KV 509366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8MT_OLIVE%__LAYFLD8 | 3 Phase fault on 8MT_OLIVE% (337368) 500 kV Bus a. Apply fault at the 8MT_OLIVE% (337368) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8MT_OLIVE% 500.0 KV 337368 TO LAYFLD8 500.0 KV 509366 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8SHERIDAN%__8MABELVALE% | 3 Phase fault on 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MABELVALE% 500.0 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8SHERIDAN%__8MABELVALE% | 3 Phase fault on 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MABELVALE% 500.0 KV 337808 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8SHERIDAN%__8MAGNETCOVE% | 3 Phase fault on 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8SHERIDAN%__8MAGNETCOVE% | 3 Phase fault on 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8MAGNETCOVE% 500.0 KV 337763 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8SHERIDAN%__8WHT_BLUFF% | 3 Phase fault on 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8WHT BLUFF% 500.0 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8SHERIDAN%__8WHT_BLUFF% | 3 Phase fault on 8SHERIDAN% (337643) 500 kV Bus a. Apply fault at the 8SHERIDAN% (337643) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8SHERIDAN% 500.0 KV 337643 TO 8WHT BLUFF% 500.0 KV 337651 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8STERLING%__337415_0 | 3 Phase fault on 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING%( 337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 337420 TO 3STERLING% 337415 TO 1STERLING3 337412 CKT 3 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8STERLING%__337415_0 | 3 Phase fault on 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING%( 337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 337420 TO 3STERLING% 337415 TO 1STERLING3 337412 CKT 3 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8STERLING%__8EL_DORADO% | 3 Phase fault on 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500.0 KV 337420 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8STERLING%__8EL_DORADO% | 3 Phase fault on 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500.0 KV 337420 TO 8EL DORADO% 500.0 KV 337561 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8STERLING%__8PERRYVILLE% | 3 Phase fault on 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500.0 KV 337420 TO 8PERRYVILLE% 500.0 KV 337427 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8STERLING%__8PERRYVILLE% | 3 Phase fault on 8STERLING% (337420) 500 kV Bus a. Apply fault at the 8STERLING% (337420) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING% 500.0 KV 337420 TO 8PERRYVILLE% 500.0 KV 337427 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | 8STERLING2%__8STERLING% | 3 Phase fault on 8STERLING2% (337413) 500 kV Bus a. Apply fault at the 8STERLING2% (337413) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING2% 500.0 KV 337413 TO 8STERLING% 500.0 KV 337420 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | 8STERLING2%__8STERLING% | 3 Phase fault on 8STERLING2% (337413) 500 kV Bus a. Apply fault at the 8STERLING2% (337413) 500 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. 8STERLING2% 500.0 KV 337413 TO 8STERLING% 500.0 KV 337420 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ACME_4__FRNKLNS4 | 3 Phase fault on ACME 4 (520802) 138 kV Bus a. Apply fault at the ACME 4 (520802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 138.0 KV 520802 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ACME_4__FRNKLNS4 | 3 Phase fault on ACME 4 (520802) 138 kV Bus a. Apply fault at the ACME 4 (520802) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ACME 4 138.0 KV 520802 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | AGENCY_2__515230_0 | 3 Phase fault on AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2( 515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 515229 TO AGENCY 5 515230 TO AGENCY 1 515701 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | AGENCY_2__515230_0 | 3 Phase fault on AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2( 515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 515229 TO AGENCY 5 515230 TO AGENCY 1 515701 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | AGENCY_2__JAMESVL2 | 3 Phase fault on AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 69.0 KV 515229 TO JAMESVL2 69.0 KV 515240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | AGENCY_2__JAMESVL2 | 3 Phase fault on AGENCY 2 (515229) 69 kV Bus a. Apply fault at the AGENCY 2 (515229) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 2 69.0 KV 515229 TO JAMESVL2 69.0 KV 515240 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | AGENCY_5__MSKPTAP5 | 3 Phase fault on AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161.0 KV 515230 TO EUCLID 5 161.0 KV 515251 CKT 1 b.2. LOAD 1 515251 b.3. MSKPTAP5 161.0 KV 515232 TO EUCLID 5 161.0 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | AGENCY_5__MSKPTAP5 | 3 Phase fault on AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161.0 KV 515230 TO EUCLID 5 161.0 KV 515251 CKT 1 b.2. LOAD 1 515251 b.3. MSKPTAP5 161.0 KV 515232 TO EUCLID 5 161.0 KV 515251 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | AGENCY_5__PECANCK5 | 3 Phase fault on AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161.0 KV 515230 TO PECANCK5 161.0 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | AGENCY_5__PECANCK5 | 3 Phase fault on AGENCY 5 (515230) 161 kV Bus a. Apply fault at the AGENCY 5 (515230) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. AGENCY 5 161.0 KV 515230 TO PECANCK5 161.0 KV 515234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK2__CADDO__2 | 3 Phase fault on ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANADARK2__CADDO__2 | 3 Phase fault on ANADARK2 (520810) 69 kV Bus a. Apply fault at the ANADARK2 (520810) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK2 69.0 KV 520810 TO CADDO 2 69.0 KV 520838 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK4__520810_0 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ANADARK4__520810_0 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4( 520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 520814 TO ANADARK2 520810 TO ADRKTERT 521181 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK4__CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ANADARK4__CHERRYRD_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK4__FLETCH_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ANADARK4__FLETCH_4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO GEORGIA4 138.0 KV 520923 CKT 1 b.2. LOAD 1 520923 b.3. FLETCH-4 138.0 KV 520912 TO GEORGIA4 138.0 KV 520923 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANADARK4__TUTLETP4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 b.2. LOAD 1 521031 b.3. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ANADARK4__TUTLETP4 | 3 Phase fault on ANADARK4 (520814) 138 kV Bus a. Apply fault at the ANADARK4 (520814) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANADARK4 138.0 KV 520814 TO POCASET4 138.0 KV 521031 CKT 1 b.2. LOAD 1 521031 b.3. POCASET4 138.0 KV 521031 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANDRCKT2__MAUDT__2 | 3 Phase fault on ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 509657 TO ANDRCKT2 69.0 KV 509658 CKT 1 b.2. MAUDT 2 69.0 KV 509653 TO MAUD 2 69.0 KV 509657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANDRCKT2__MAUDT__2 | 3 Phase fault on ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MAUD 2 69.0 KV 509657 TO ANDRCKT2 69.0 KV 509658 CKT 1 b.2. MAUDT 2 69.0 KV 509653 TO MAUD 2 69.0 KV 509657 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANDRCKT2__SPRNGHL2 | 3 Phase fault on ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRCKT2 69.0 KV 509658 TO SIMMS 2 69.0 KV 509659 CKT 1 b.2. LOAD 1 509659 b.3. SIMMS 2 69.0 KV 509659 TO SDEKALB2 69.0 KV 509660 CKT 1 b.4. LOAD 1 509660 b.5. SDEKALB2 69.0 KV 509660 TO WDEKALB2 69.0 KV 509661 CKT 1 b.6. LOAD 1 509661 b.7. WDEKALB2 69.0 KV 509661 TO SPRNGHL2 69.0 KV 509662 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANDRCKT2__SPRNGHL2 | 3 Phase fault on ANDRCKT2 (509658) 69 kV Bus a. Apply fault at the ANDRCKT2 (509658) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRCKT2 69.0 KV 509658 TO SIMMS 2 69.0 KV 509659 CKT 1 b.2. LOAD 1 509659 b.3. SIMMS 2 69.0 KV 509659 TO SDEKALB2 69.0 KV 509660 CKT 1 b.4. LOAD 1 509660 b.5. SDEKALB2 69.0 KV 509660 TO WDEKALB2 69.0 KV 509661 CKT 1 b.6. LOAD 1 509661 b.7. WDEKALB2 69.0 KV 509661 TO SPRNGHL2 69.0 KV 509662 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ANDRSNC4__MUNZCTY4 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 b.2. LOAD 1 508056 b.3. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ANDRSNC4__MUNZCTY4 | 3 Phase fault on ANDRSNC4 (508050) 138 kV Bus a. Apply fault at the ANDRSNC4 (508050) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ANDRSNC4 138.0 KV 508050 TO BRYANML4 138.0 KV 508056 CKT 1 b.2. LOAD 1 508056 b.3. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARCADIA_138kV_514907 | Apply single-phase fault on: JNSKAMO4 138.0 KV 514906 TO ARCADIA 138.0 KV 514907 CKT 1, near ARCADIA 138kV for 7 cycles with stuck breaker at ARCADIA 138kV. Clear Fault after 16 cycles and trip: ARCADIA 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 and BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 and BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 and DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARCADIA_138kV_514907 | Apply single-phase fault on: JNSKAMO4 138.0 KV 514906 TO ARCADIA 138.0 KV 514907 CKT 1, near ARCADIA 138kV for 7 cycles with stuck breaker at ARCADIA 138kV. Clear Fault after 16 cycles and trip: ARCADIA 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 and BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 and BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 and DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARCADIA_345kV_514908 | Apply single-phase fault on: ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1, near ARCADIA 345kV for 6 cycles with stuck breaker at ARCADIA 345kV. Clear Fault after 16 cycles and trip: NORTWST7 345.0 KV 514880 TO ARCADIA 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARCADIA_345kV_514908 | Apply single-phase fault on: ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1, near ARCADIA 345kV for 6 cycles with stuck breaker at ARCADIA 345kV. Clear Fault after 16 cycles and trip: NORTWST7 345.0 KV 514880 TO ARCADIA 345.0 KV 514908 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARCADIA4__514908_0 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4( 514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ARCADIA4__514908_0 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4( 514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 514907 TO ARCADIA7 514908 TO ARCADI31 515704 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARCADIA4__DANFRTH4 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ARCADIA4__DANFRTH4 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 b.2. LOAD 1 515461 b.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARCADIA4__LGARBER4 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ARCADIA4__LGARBER4 | 3 Phase fault on ARCADIA4 (514907) 138 kV Bus a. Apply fault at the ARCADIA4 (514907) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARCADIA4 138.0 KV 514907 TO LGARBER4 138.0 KV 515465 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARCADIA7__GEN_2017_132 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-132 345.0 KV 760032 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ARCADIA7__GEN_2017_132 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO GEN-2017-132 345.0 KV 760032 CKT 4 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARCADIA7__REDBUD_7 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ARCADIA7__REDBUD_7 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO REDBUD 7 345.0 KV 514909 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARCADIA7__SEMINOL7 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | ARCADIA7__SEMINOL7 | 3 Phase fault on ARCADIA7 (514908) 345 kV Bus a. Apply fault at the ARCADIA7 (514908) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. ARCADIA7 345.0 KV 514908 TO SEMINOL7 345.0 KV 515045 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARSHILL2__507711_0 | 3 Phase fault on ARSHILL2 (507710) 69 kV Bus a. Apply fault at the ARSHILL2( 507710) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARSHILL2__507711_0 | 3 Phase fault on ARSHILL2 (507710) 69 kV Bus a. Apply fault at the ARSHILL2( 507710) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL2 507710 TO ARSHILL4 507711 TO ARSH2-1 507714 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARSHILL4__FTHUMBG4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO FTHUMBG4 138.0 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARSHILL4__FTHUMBG4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO FTHUMBG4 138.0 KV 507731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARSHILL4__LIEBERM4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO LIEBERM4 138.0 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARSHILL4__LIEBERM4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO LIEBERM4 138.0 KV 508806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARSHILL4__MCWILLI4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARSHILL4__MCWILLI4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO MCWILLI4 138.0 KV 507742 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARSHILL4__RAINES_4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO RAINES 4 138.0 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARSHILL4__RAINES_4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO RAINES 4 138.0 KV 507749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARSHILL4__STLGENS4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO STLGENS4 138.0 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARSHILL4__STLGENS4 | 3 Phase fault on ARSHILL4 (507711) 138 kV Bus a. Apply fault at the ARSHILL4 (507711) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARSHILL4 138.0 KV 507711 TO STLGENS4 138.0 KV 507789 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ARTVLTP4__ARTVILL4 | 3 Phase fault on ARTVLTP4 (511537) 138 kV Bus a. Apply fault at the ARTVLTP4 (511537) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ARTVLTP4 138.0 KV 511537 TO ARTVILL4 138.0 KV 511538 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ASHDWN_W__4__PATTERS4 | 3 Phase fault on ASHDWN_W 4 (504124) 138 kV Bus a. Apply fault at the ASHDWN_W 4 (504124) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138.0 KV 504124 TO PATTERS4 138.0 KV 507431 CKT 1 b.2. ASHDWN_W 4 138.0 KV 504124 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ASHDWN_W__4__PATTERS4 | 3 Phase fault on ASHDWN_W 4 (504124) 138 kV Bus a. Apply fault at the ASHDWN_W 4 (504124) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASHDWN_W 4 138.0 KV 504124 TO PATTERS4 138.0 KV 507431 CKT 1 b.2. ASHDWN_W 4 138.0 KV 504124 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ASPEN__4__MOORLND4 | 3 Phase fault on ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ASPEN__4__MOORLND4 | 3 Phase fault on ASPEN 4 (520462) 138 kV Bus a. Apply fault at the ASPEN 4 (520462) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ASPEN 4 138.0 KV 520462 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | B_BOWTP4__CRAIGJT4 | 3 Phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOWTP4 138.0 KV 510888 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | B_BOWTP4__CRAIGJT4 | 3 Phase fault on B.BOWTP4 (510888) 138 kV Bus a. Apply fault at the B.BOWTP4 (510888) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B.BOWTP4 138.0 KV 510888 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | B111___4__BA101ST4 | 3 Phase fault on B111---4 (509767) 138 kV Bus a. Apply fault at the B111---4 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138.0 KV 509767 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | B111___4__BA101ST4 | 3 Phase fault on B111---4 (509767) 138 kV Bus a. Apply fault at the B111---4 (509767) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. B111---4 138.0 KV 509767 TO BA101ST4 138.0 KV 509768 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BA_N_ST4__ONETA__4 | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BA_N_ST4__ONETA__4 | 3 Phase fault on BA.N-ST4 (509786) 138 kV Bus a. Apply fault at the BA.N-ST4 (509786) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA.N-ST4 138.0 KV 509786 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BA101_N4__ONETA__4 | 3 Phase fault on BA101-N4 (509769) 138 kV Bus a. Apply fault at the BA101-N4 (509769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138.0 KV 509769 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BA101_N4__ONETA__4 | 3 Phase fault on BA101-N4 (509769) 138 kV Bus a. Apply fault at the BA101-N4 (509769) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101-N4 138.0 KV 509769 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BA101ST4__ONETA__4 | 3 Phase fault on BA101ST4 (509768) 138 kV Bus a. Apply fault at the BA101ST4 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138.0 KV 509768 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BA101ST4__ONETA__4 | 3 Phase fault on BA101ST4 (509768) 138 kV Bus a. Apply fault at the BA101ST4 (509768) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BA101ST4 138.0 KV 509768 TO ONETA--4 138.0 KV 509806 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BADGER_7__BLUWND_7 | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO BLUWND 7 345.0 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BADGER_7__BLUWND_7 | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO BLUWND 7 345.0 KV 515686 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BADGER_7__G16_003_TAP | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | BADGER_7__G16_003_TAP | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO G16-003-TAP 345.0 KV 560071 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | BADGER_7__GEN_2015_082 | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO GEN-2015-082 345.0 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BADGER_7__GEN_2015_082 | 3 Phase fault on BADGER 7 (515677) 345 kV Bus a. Apply fault at the BADGER 7 (515677) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BADGER 7 345.0 KV 515677 TO GEN-2015-082 345.0 KV 585190 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___2__508054_0 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2( 508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___2__508054_0 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2( 508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 508053 TO BANN 4 508054 TO BANN1-1 508097 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___2__LSORDTP2 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___2__LSORDTP2 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO LSORDTP2 69.0 KV 508063 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___2__SUGHLWT2 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO REDLICK2 69.0 KV 508073 CKT 1 b.2. LOAD 1 508073 b.3. REDLICK2 69.0 KV 508073 TO RICHMND2 69.0 KV 508076 CKT 1 b.4. LOAD 1 508076 b.5. NW_TEXAR 2 69.0 KV 504109 TO RICHMND2 69.0 KV 508076 CKT 1 b.6. LOAD 1 508076 b.7. NW_TEXAR 2 69.0 KV 504109 TO SUGHLWT2 69.0 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___2__SUGHLWT2 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO REDLICK2 69.0 KV 508073 CKT 1 b.2. LOAD 1 508073 b.3. REDLICK2 69.0 KV 508073 TO RICHMND2 69.0 KV 508076 CKT 1 b.4. LOAD 1 508076 b.5. NW_TEXAR 2 69.0 KV 504109 TO RICHMND2 69.0 KV 508076 CKT 1 b.6. LOAD 1 508076 b.7. NW_TEXAR 2 69.0 KV 504109 TO SUGHLWT2 69.0 KV 508082 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___2__TEXOPER2 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO KINGHWY2 69.0 KV 508061 CKT 1 b.2. LOAD 1 508061 b.3. KINGHWY2 69.0 KV 508061 TO TEXOPER2 69.0 KV 508087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN___2__TEXOPER2 | 3 Phase fault on BANN 2 (508053) 69 kV Bus a. Apply fault at the BANN 2 (508053) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 2 69.0 KV 508053 TO KINGHWY2 69.0 KV 508061 CKT 1 b.2. LOAD 1 508061 b.3. KINGHWY2 69.0 KV 508061 TO TEXOPER2 69.0 KV 508087 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___4__NWT_BNT4 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | BANN___4__NWT_BNT4 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO NWT-BNT4 138.0 KV 508070 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___4__REDSPRG4 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | BANN___4__REDSPRG4 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO REDSPRG4 138.0 KV 508075 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN___4__SETEXAR4 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | BANN___4__SETEXAR4 | 3 Phase fault on BANN 4 (508054) 138 kV Bus a. Apply fault at the BANN 4 (508054) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BANN 4 138.0 KV 508054 TO SETEXAR4 138.0 KV 508078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BANN4_138kV_508054 | Apply single-phase fault on: NWTBNT4 138KV 508070 TO BANN4 138KV 508054 CKT 1, near BANN 4 138 kV for 7 cycles with stuck breaker at BANN 4 138 kV. Clear Fault after 16 cycles and trip: BANN4 138KV 508054 TO REDSPRG4 138KV 508075 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BANN4_138kV_508054 | Apply single-phase fault on: NWTBNT4 138KV 508070 TO BANN4 138KV 508054 CKT 1, near BANN 4 138 kV for 7 cycles with stuck breaker at BANN 4 138 kV. Clear Fault after 16 cycles and trip: BANN4 138KV 508054 TO REDSPRG4 138KV 508075 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BARITE_RD_4__BARITERDTP_4 | 3 Phase fault on BARITE-RD 4 (504379) 138 kV Bus a. Apply fault at the BARITE-RD 4 (504379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARITE-RD 4 138.0 KV 504379 TO BARITERDTP 4 138.0 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BARITE_RD_4__BARITERDTP_4 | 3 Phase fault on BARITE-RD 4 (504379) 138 kV Bus a. Apply fault at the BARITE-RD 4 (504379) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BARITE-RD 4 138.0 KV 504379 TO BARITERDTP 4 138.0 KV 507463 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BC_SW__4__SLKHILLS_4 | 3 Phase fault on BC SW 4 (520512) 138 kV Bus a. Apply fault at the BC SW 4 (520512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC SW 4 138.0 KV 520512 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BC_SW__4__SLKHILLS_4 | 3 Phase fault on BC SW 4 (520512) 138 kV Bus a. Apply fault at the BC SW 4 (520512) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BC SW 4 138.0 KV 520512 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BCV_SW_4__CHERRYRD_4 | 3 Phase fault on BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BCV_SW_4__CHERRYRD_4 | 3 Phase fault on BCV SW 4 (520513) 138 kV Bus a. Apply fault at the BCV SW 4 (520513) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCV SW 4 138.0 KV 520513 TO CHERRYRD 4 138.0 KV 521129 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BCVI_HVB__SLKHILLS_4 | 3 Phase fault on BCVI_HVB (520514) 138 kV Bus a. Apply fault at the BCVI_HVB (520514) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCVI_HVB 138.0 KV 520514 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BCVI_HVB__SLKHILLS_4 | 3 Phase fault on BCVI_HVB (520514) 138 kV Bus a. Apply fault at the BCVI_HVB (520514) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BCVI_HVB 138.0 KV 520514 TO SLKHILLS 4 138.0 KV 521103 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BEELINE4__EXPGLNT4 | 3 Phase fault on BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE4 138.0 KV 515247 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BEELINE4__EXPGLNT4 | 3 Phase fault on BEELINE4 (515247) 138 kV Bus a. Apply fault at the BEELINE4 (515247) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEELINE4 138.0 KV 515247 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BELISLE4__38TH_ST4 | 3 Phase fault on BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138.0 KV 514844 TO 38TH ST4 138.0 KV 514846 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BELISLE4__38TH_ST4 | 3 Phase fault on BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138.0 KV 514844 TO 38TH ST4 138.0 KV 514846 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BELISLE4__WESTERN4 | 3 Phase fault on BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138.0 KV 514844 TO WESTERN4 138.0 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BELISLE4__WESTERN4 | 3 Phase fault on BELISLE4 (514844) 138 kV Bus a. Apply fault at the BELISLE4 (514844) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BELISLE4 138.0 KV 514844 TO WESTERN4 138.0 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BEVYTAP5__FTSMTHE5 | 3 Phase fault on BEVYTAP5 (515299) 161 kV Bus a. Apply fault at the BEVYTAP5 (515299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161.0 KV 515299 TO FTSMTHE5 161.0 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BEVYTAP5__FTSMTHE5 | 3 Phase fault on BEVYTAP5 (515299) 161 kV Bus a. Apply fault at the BEVYTAP5 (515299) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BEVYTAP5 161.0 KV 515299 TO FTSMTHE5 161.0 KV 515300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BINGERJ4__NIJECT_4 | 3 Phase fault on BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO NIJECT 4 138.0 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BINGERJ4__NIJECT_4 | 3 Phase fault on BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO NIJECT 4 138.0 KV 521010 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BINGERJ4__SICKLES4 | 3 Phase fault on BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO SICKLES4 138.0 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BINGERJ4__SICKLES4 | 3 Phase fault on BINGERJ4 (520827) 138 kV Bus a. Apply fault at the BINGERJ4 (520827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BINGERJ4 138.0 KV 520827 TO SICKLES4 138.0 KV 521050 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BLANCH_2__LIEBERM2 | 3 Phase fault on BLANCH-2 (508801) 69 kV Bus a. Apply fault at the BLANCH-2 (508801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69.0 KV 508801 TO LIEBERM2 69.0 KV 508805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BLANCH_2__LIEBERM2 | 3 Phase fault on BLANCH-2 (508801) 69 kV Bus a. Apply fault at the BLANCH-2 (508801) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCH-2 69.0 KV 508801 TO LIEBERM2 69.0 KV 508805 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BLANCHD4__MAUD___4 | 3 Phase fault on BLANCHD4 (511508) 138 kV Bus a. Apply fault at the BLANCHD4 (511508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 511508 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BLANCHD4__MAUD___4 | 3 Phase fault on BLANCHD4 (511508) 138 kV Bus a. Apply fault at the BLANCHD4 (511508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLANCHD4 138.0 KV 511508 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BLUEBEL2__515242_0 | 3 Phase fault on BLUEBEL2 (515241) 69 kV Bus a. Apply fault at the BLUEBEL2( 515241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BLUEBEL2__515242_0 | 3 Phase fault on BLUEBEL2 (515241) 69 kV Bus a. Apply fault at the BLUEBEL2( 515241) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL2 515241 TO BLUEBEL4 515242 TO BLUEBEL1 515706 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BLUEBEL2_69kV_515241 | Apply single-phase fault on: SAPULPA2 69KV 515236 TO BLUEBEL2 69KV 515241 CKT 1 and SAPULPA2 69KV 515236 TO BEELINE2 69KV 515246 CKT 1, near BLUEBEL2 69kV for 7 cycles with stuck breaker at BLUEBEL2 69kV. Clear Fault after 16 cycles and trip: PRNCVLT2 69KV 515037 TO BLUEBEL2 69KV 515241 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BLUEBEL2_69kV_515241 | Apply single-phase fault on: SAPULPA2 69KV 515236 TO BLUEBEL2 69KV 515241 CKT 1 and SAPULPA2 69KV 515236 TO BEELINE2 69KV 515246 CKT 1, near BLUEBEL2 69kV for 7 cycles with stuck breaker at BLUEBEL2 69kV. Clear Fault after 16 cycles and trip: PRNCVLT2 69KV 515037 TO BLUEBEL2 69KV 515241 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BLUEBEL4__BOWDEN_4 | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138.0 KV 515242 TO BOWDEN 4 138.0 KV 515243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BLUEBEL4__BOWDEN_4 | 3 Phase fault on BLUEBEL4 (515242) 138 kV Bus a. Apply fault at the BLUEBEL4 (515242) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BLUEBEL4 138.0 KV 515242 TO BOWDEN 4 138.0 KV 515243 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BLUEBEL4_138kV_515242 | Apply single-phase fault on: BRISTOW4 138KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1, near BLUEBEL4 138kV for 7 cycles with stuck breaker at BLUEBEL4 138kV. Clear Fault after 16 cycles and trip: BLUEBEL4 138.0 KV 515242 TO BOWDEN4 138.0 KV 515243 CKT 1 and BOWDEN4 138.0 KV 515243 TO HICKORY4 138.0 KV 515244 CKT 1 and POLECTP4 138.0 KV 515218 TO HICKORY4 138.0 KV 515244 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BLUEBEL4_138kV_515242 | Apply single-phase fault on: BRISTOW4 138KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1, near BLUEBEL4 138kV for 7 cycles with stuck breaker at BLUEBEL4 138kV. Clear Fault after 16 cycles and trip: BLUEBEL4 138.0 KV 515242 TO BOWDEN4 138.0 KV 515243 CKT 1 and BOWDEN4 138.0 KV 515243 TO HICKORY4 138.0 KV 515244 CKT 1 and POLECTP4 138.0 KV 515218 TO HICKORY4 138.0 KV 515244 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BORDER_____7__TUCO_INT___7 | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO TUCO_INT 7 345.0 KV 525832 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BORDER_____7__WWDBORDT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BORDER_____7__WWDBORDT | 3 Phase fault on BORDER 7 (515458) 345 kV Bus a. Apply fault at the BORDER 7 (515458) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BORDER 7 345.0 KV 515458 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BORDER7_345kV_515458 | Apply single-phase fault on: BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, near BORDER 7 345 kV for 6 cycles with stuck breaker at BORDER 7 345 kV. Clear Fault after 16 cycles and trip: BORDER7 345KV 515458 TO WWDBORDT 345KV 755000 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BORDER7_345kV_515458 | Apply single-phase fault on: BORDER7 345KV 515458 TO TUCO_INT7 345KV 525832 CKT 1, near BORDER 7 345 kV for 6 cycles with stuck breaker at BORDER 7 345 kV. Clear Fault after 16 cycles and trip: BORDER7 345KV 515458 TO WWDBORDT 345KV 755000 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BOWMAN_2__KNGINDT2 | 3 Phase fault on BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69.0 KV 514813 TO KNGINDT2 69.0 KV 515625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BOWMAN_2__KNGINDT2 | 3 Phase fault on BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69.0 KV 514813 TO KNGINDT2 69.0 KV 515625 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BOWMAN_2__OMKINGF2 | 3 Phase fault on BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69.0 KV 514813 TO OMKINGF2 69.0 KV 529280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BOWMAN_2__OMKINGF2 | 3 Phase fault on BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69.0 KV 514813 TO OMKINGF2 69.0 KV 529280 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BOWMAN_2__TURCRKT2 | 3 Phase fault on BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69.0 KV 514813 TO TURCRKT2 69.0 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BOWMAN_2__TURCRKT2 | 3 Phase fault on BOWMAN 2 (514813) 69 kV Bus a. Apply fault at the BOWMAN 2 (514813) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BOWMAN 2 69.0 KV 514813 TO TURCRKT2 69.0 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRANCH5_161kV_515316 | Apply single-phase fault on: NMAGZIN5 161KV 507190 TO BRANCH5 161KV 515316 CKT 1, near BRANCH5 161kV for 7 cycles with stuck breaker at BRANCH5 161kV. Clear Fault after 16 cycles and trip: BRANCH5 161KV 515316 TO GRNDPRT5 161.0 KV 515524 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRANCH5_161kV_515316 | Apply single-phase fault on: NMAGZIN5 161KV 507190 TO BRANCH5 161KV 515316 CKT 1, near BRANCH5 161kV for 7 cycles with stuck breaker at BRANCH5 161kV. Clear Fault after 16 cycles and trip: BRANCH5 161KV 515316 TO GRNDPRT5 161.0 KV 515524 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRANCH5_69kV_515313 | Apply single-phase fault on: BOONVIL2 69KV 507183 TO BRANCH5 69KV 515313 CKT 1 and BOONEVIL2 69KV 504172 TO BOONVIL2 69KV 507183 CKT 1 and BOONEVIL2 69KV 504172 TO WBOONVL2 69KV 507198 CKT 1, near BRANCH5 69kV for 7 cycles with stuck breaker at BRANCH5 69kV. Clear Fault after 16 cycles and trip: BRANCH2 69KV 515313 TO PENDER2 69.0 KV 515317 CKT 1 and and PENDER2 69.0 KV 515317 TO HELBERG2 69.0 KV 515325 CKT 1 and AVECOZK2 69.0 KV 515324 TO HELBERG2 69.0 KV 515325 CKT 1 and COALHIL2 69.0 KV 515322 TO AVECOZK2 69.0 KV 515324 CKT 1 and LSPARDRA2 69.0 KV 515320 TO COALHIL2 69.0 KV 515322 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRANCH5_69kV_515313 | Apply single-phase fault on: BOONVIL2 69KV 507183 TO BRANCH5 69KV 515313 CKT 1 and BOONEVIL2 69KV 504172 TO BOONVIL2 69KV 507183 CKT 1 and BOONEVIL2 69KV 504172 TO WBOONVL2 69KV 507198 CKT 1, near BRANCH5 69kV for 7 cycles with stuck breaker at BRANCH5 69kV. Clear Fault after 16 cycles and trip: BRANCH2 69KV 515313 TO PENDER2 69.0 KV 515317 CKT 1 and and PENDER2 69.0 KV 515317 TO HELBERG2 69.0 KV 515325 CKT 1 and AVECOZK2 69.0 KV 515324 TO HELBERG2 69.0 KV 515325 CKT 1 and COALHIL2 69.0 KV 515322 TO AVECOZK2 69.0 KV 515324 CKT 1 and LSPARDRA2 69.0 KV 515320 TO COALHIL2 69.0 KV 515322 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRCKWND4__BRECKNR4 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRCKWND4__BRECKNR4 | 3 Phase fault on BRCKWND4 (514642) 138 kV Bus a. Apply fault at the BRCKWND4 (514642) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRCKWND4 138.0 KV 514642 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRECKNR4__ENIDINT4 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRECKNR4__ENIDINT4 | 3 Phase fault on BRECKNR4 (514815) 138 kV Bus a. Apply fault at the BRECKNR4 (514815) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRECKNR4 138.0 KV 514815 TO ENIDINT4 138.0 KV 515383 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRIDGCR4__TUTLETP4 | 3 Phase fault on BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRIDGCR4__TUTLETP4 | 3 Phase fault on BRIDGCR4 (520501) 138 kV Bus a. Apply fault at the BRIDGCR4 (520501) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRIDGCR4 138.0 KV 520501 TO TUTLETP4 138.0 KV 521072 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRISTOW_138kV_515035 | Apply single-phase fault on: BRISTOW4 138KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1, near BRISTOW 138kV for 7 cycles with stuck breaker at BRISTOW 138kV. Clear Fault after 16 cycles and trip: BRISTOW4 138KV 515035 TO BEGGS 4 138.0 KV 515249 CKT 1 and PECANCK4 138KV 515233 TO BEGGS 4 138.0 KV 515249 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRISTOW_138kV_515035 | Apply single-phase fault on: BRISTOW4 138KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1, near BRISTOW 138kV for 7 cycles with stuck breaker at BRISTOW 138kV. Clear Fault after 16 cycles and trip: BRISTOW4 138KV 515035 TO BEGGS 4 138.0 KV 515249 CKT 1 and PECANCK4 138KV 515233 TO BEGGS 4 138.0 KV 515249 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRISTOW2__515035_0 | 3 Phase fault on BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2( 515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 515034 TO BRISTOW4 515035 TO BRISTOW1 515709 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRISTOW2__515035_0 | 3 Phase fault on BRISTOW2 (515034) 69 kV Bus a. Apply fault at the BRISTOW2( 515034) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW2 515034 TO BRISTOW4 515035 TO BRISTOW1 515709 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRISTOW4__BLUEBEL4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRISTOW4__BLUEBEL4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO BLUEBEL4 138.0 KV 515242 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRISTOW4__GEN_2017_240 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO GEN-2017-240 138.0 KV 760158 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRISTOW4__GEN_2017_240 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO GEN-2017-240 138.0 KV 760158 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRISTOW4__GRNWOOD4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO GRNWOOD4 138.0 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRISTOW4__GRNWOOD4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO GRNWOOD4 138.0 KV 515417 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRISTOW4__KEYWEST4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO KEYWEST4 138.0 KV 515048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRISTOW4__KEYWEST4 | 3 Phase fault on BRISTOW4 (515035) 138 kV Bus a. Apply fault at the BRISTOW4 (515035) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRISTOW4 138.0 KV 515035 TO KEYWEST4 138.0 KV 515048 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRKN_BW4__CRAIGJT4 | 3 Phase fault on BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138.0 KV 505614 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRKN_BW4__CRAIGJT4 | 3 Phase fault on BRKN BW4 (505614) 138 kV Bus a. Apply fault at the BRKN BW4 (505614) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRKN BW4 138.0 KV 505614 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BROWN4_138kV_515157 | Apply single-phase fault on: BROWN4 138KV 515157 TO STRRDTP4 138.0 KV 515944 CKT 1, near BROWN4 138kV for 7 cycles with stuck breaker at BROWN4 138kV. Clear Fault after 16 cycles and trip: SBROWN4 138KV 505602 TO BROWN 4 138.0 KV 515157 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BROWN4_138kV_515157 | Apply single-phase fault on: BROWN4 138KV 515157 TO STRRDTP4 138.0 KV 515944 CKT 1, near BROWN4 138kV for 7 cycles with stuck breaker at BROWN4 138kV. Clear Fault after 16 cycles and trip: SBROWN4 138KV 505602 TO BROWN 4 138.0 KV 515157 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BROWNTP4_138kV_515152 | Apply single-phase fault on: LTLCITY4 138KV 515151 TO BROWNTP4 138KV 515152 CKT 1 and CANEYCK4 138KV 515150 TO LTLCITY4 138KV 515151 CKT 1, near BROWNTP4 138kV for 7 cycles with stuck breaker at BROWNTP4 138kV. Clear Fault after 16 cycles and trip: BROWNTP4 138KV 515152 TO BODLE4 138.0 KV 515155 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BROWNTP4_138kV_515152 | Apply single-phase fault on: LTLCITY4 138KV 515151 TO BROWNTP4 138KV 515152 CKT 1 and CANEYCK4 138KV 515150 TO LTLCITY4 138KV 515151 CKT 1, near BROWNTP4 138kV for 7 cycles with stuck breaker at BROWNTP4 138kV. Clear Fault after 16 cycles and trip: BROWNTP4 138KV 515152 TO BODLE4 138.0 KV 515155 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BRYANML4__MUNZCTY4 | 3 Phase fault on BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BRYANML4__MUNZCTY4 | 3 Phase fault on BRYANML4 (508056) 138 kV Bus a. Apply fault at the BRYANML4 (508056) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BRYANML4 138.0 KV 508056 TO MUNZCTY4 138.0 KV 508064 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUFFALO7__THISTLE7 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUFFALO7__THISTLE7 | 3 Phase fault on BUFFALO7 (532782) 345 kV Bus a. Apply fault at the BUFFALO7 (532782) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BUFFALO7 345.0 KV 532782 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUFORDR2__DEKALB_2 | 3 Phase fault on BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69.0 KV 508287 TO DEKALB 2 69.0 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUFORDR2__DEKALB_2 | 3 Phase fault on BUFORDR2 (508287) 69 kV Bus a. Apply fault at the BUFORDR2 (508287) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUFORDR2 69.0 KV 508287 TO DEKALB 2 69.0 KV 508289 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BULFOOT4__BULFTTP4 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BULFOOT4__BULFTTP4 | 3 Phase fault on BULFOOT4 (515960) 138 kV Bus a. Apply fault at the BULFOOT4 (515960) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFOOT4 138.0 KV 515960 TO BULFTTP4 138.0 KV 520535 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BULFTTP4__DOVERSW4 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BULFTTP4__DOVERSW4 | 3 Phase fault on BULFTTP4 (520535) 138 kV Bus a. Apply fault at the BULFTTP4 (520535) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BULFTTP4 138.0 KV 520535 TO DOVERSW4 138.0 KV 520882 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BUNCHCK4__BRECKNR4 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BUNCHCK4__BRECKNR4 | 3 Phase fault on BUNCHCK4 (514701) 138 kV Bus a. Apply fault at the BUNCHCK4 (514701) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BUNCHCK4 138.0 KV 514701 TO BRECKNR4 138.0 KV 514815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BVRCNTY7__BADGER_7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BVRCNTY7__BADGER_7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO BADGER 7 345.0 KV 515677 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | BVRCNTY7__HITCHLAND__7 | 3 Phase fault on BVRCNTY7 (515554) 345 kV Bus a. Apply fault at the BVRCNTY7 (515554) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. BVRCNTY7 345.0 KV 515554 TO HITCHLAND 7 345.0 KV 523097 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | C_RIVER4__TALAWANDA__4 | 3 Phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | C_RIVER4__TALAWANDA__4 | 3 Phase fault on C-RIVER4 (510946) 138 kV Bus a. Apply fault at the C-RIVER4 (510946) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. C-RIVER4 138.0 KV 510946 TO TALAWANDA 4 138.0 KV 510951 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | C_RIVER7__510946_0 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | C_RIVER7__510946_0 | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7( 515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 515422 TO C-RIVER4 510946 TO C-RIVER1 510947 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | C_RIVER7__FIREWHL_TAP | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | C_RIVER7__FIREWHL_TAP | 3 Phase fault on C-RIVER7 (515422) 345 kV Bus a. Apply fault at the C-RIVER7 (515422) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. C-RIVER7 345.0 KV 515422 TO FIREWHL-TAP 345.0 KV 588839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CADDO__2__WASHITA2 | 3 Phase fault on CADDO 2 (520838) 69 kV Bus a. Apply fault at the CADDO 2 (520838) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CADDO 2 69.0 KV 520838 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CADDO__2__WASHITA2 | 3 Phase fault on CADDO 2 (520838) 69 kV Bus a. Apply fault at the CADDO 2 (520838) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CADDO 2 69.0 KV 520838 TO WASHITA2 69.0 KV 521088 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | CALRYTP2__MUSKOGE2 | 3 Phase fault on CALRYTP2 (515211) 69 kV Bus a. Apply fault at the CALRYTP2 (515211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALRYTP2 69.0 KV 515211 TO MUSKOGE2 69.0 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CALRYTP2__MUSKOGE2 | 3 Phase fault on CALRYTP2 (515211) 69 kV Bus a. Apply fault at the CALRYTP2 (515211) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALRYTP2 69.0 KV 515211 TO MUSKOGE2 69.0 KV 515221 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CALUMET4__CONCHO_4 | 3 Phase fault on CALUMET4 (520839) 138 kV Bus a. Apply fault at the CALUMET4 (520839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALUMET4 138.0 KV 520839 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CALUMET4__CONCHO_4 | 3 Phase fault on CALUMET4 (520839) 138 kV Bus a. Apply fault at the CALUMET4 (520839) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CALUMET4 138.0 KV 520839 TO CONCHO 4 138.0 KV 520865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CANA___4__CALUMET4 | 3 Phase fault on CANA 4 (520502) 138 kV Bus a. Apply fault at the CANA 4 (520502) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138.0 KV 520502 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CANA___4__CALUMET4 | 3 Phase fault on CANA 4 (520502) 138 kV Bus a. Apply fault at the CANA 4 (520502) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CANA 4 138.0 KV 520502 TO CALUMET4 138.0 KV 520839 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CANADN7__515606_0 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7( 515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 515605 TO CANDN11 515606 TO CANDNT1 515608 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CANADN7__515606_0 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7( 515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 515605 TO CANDN11 515606 TO CANDNT1 515608 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CANADN7__515607_0 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7( 515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 515605 TO CANDN12 515607 TO CANDNT2 515609 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CANADN7__515607_0 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7( 515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 515605 TO CANDN12 515607 TO CANDNT2 515609 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CANADN7__FSHRTAP7 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 345.0 KV 515605 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CANADN7__FSHRTAP7 | 3 Phase fault on CANADN7 (515605) 345 kV Bus a. Apply fault at the CANADN7 (515605) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CANADN7 345.0 KV 515605 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CANEYCK4_138kV_515150 | Apply single-phase fault on: CANEYCK4 138KV 515150 TO LTLCITY4 138KV 515151 CKT 1 and LTLCITY4 138KV 515151 TO BROWNTP4 138KV 515152 CKT 1, near CANEYCK4 138kV for 7 cycles with stuck breaker at CANEYCK4 138kV. Clear Fault after 16 cycles and trip: JOHNCO4 138KV 514808 TO CANEYCK4 138KV 515150 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CANEYCK4_138kV_515150 | Apply single-phase fault on: CANEYCK4 138KV 515150 TO LTLCITY4 138KV 515151 CKT 1 and LTLCITY4 138KV 515151 TO BROWNTP4 138KV 515152 CKT 1, near CANEYCK4 138kV for 7 cycles with stuck breaker at CANEYCK4 138kV. Clear Fault after 16 cycles and trip: JOHNCO4 138KV 514808 TO CANEYCK4 138KV 515150 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CANGAS4_138kV_511540 | Apply single-phase fault on: CANGAS4 138KV 511540 TO REDROCKRD4 138KV 511548 CKT 1, near CANGAS4 138kV for 7 cycles with stuck breaker at CANGAS4 138kV. Clear Fault after 16 cycles and trip: CANGAS4 138KV 511540 TO JENSEN4 138KV 514821 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CANGAS4_138kV_511540 | Apply single-phase fault on: CANGAS4 138KV 511540 TO REDROCKRD4 138KV 511548 CKT 1, near CANGAS4 138kV for 7 cycles with stuck breaker at CANGAS4 138kV. Clear Fault after 16 cycles and trip: CANGAS4 138KV 511540 TO JENSEN4 138KV 514821 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARNEG_4__S_W_S__4 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARNEG_4__S_W_S__4 | 3 Phase fault on CARNEG-4 (511445) 138 kV Bus a. Apply fault at the CARNEG-4 (511445) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARNEG-4 138.0 KV 511445 TO S.W.S.-4 138.0 KV 511477 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARROLL6__DOLHILL6 | 3 Phase fault on CARROLL6 (500140) 230 kV Bus a. Apply fault at the CARROLL6 (500140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARROLL6 230.0 KV 500140 TO DOLHILL6 230.0 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARROLL6__DOLHILL6 | 3 Phase fault on CARROLL6 (500140) 230 kV Bus a. Apply fault at the CARROLL6 (500140) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARROLL6 230.0 KV 500140 TO DOLHILL6 230.0 KV 500260 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARSN_S4__DENVR_C4 | 3 Phase fault on CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138.0 KV 509756 TO KENSH-W4 138.0 KV 509777 CKT 1 b.2. LOAD 1 509777 b.3. DENVR-C4 138.0 KV 509742 TO KENSH-W4 138.0 KV 509777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARSN_S4__DENVR_C4 | 3 Phase fault on CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138.0 KV 509756 TO KENSH-W4 138.0 KV 509777 CKT 1 b.2. LOAD 1 509777 b.3. DENVR-C4 138.0 KV 509742 TO KENSH-W4 138.0 KV 509777 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARSN_S4__T_P_S__4 | 3 Phase fault on CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138.0 KV 509756 TO T.P.S.-4 138.0 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARSN_S4__T_P_S__4 | 3 Phase fault on CARSN-S4 (509756) 138 kV Bus a. Apply fault at the CARSN-S4 (509756) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-S4 138.0 KV 509756 TO T.P.S.-4 138.0 KV 509788 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARSN_T4__CARSN_C4 | 3 Phase fault on CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO UNIONAV4 138.0 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138.0 KV 509740 TO CARSN-C4 138.0 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARSN_T4__CARSN_C4 | 3 Phase fault on CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO UNIONAV4 138.0 KV 509740 CKT 1 b.2. LOAD 1 509740 b.3. UNIONAV4 138.0 KV 509740 TO CARSN-C4 138.0 KV 509749 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARSN_T4__S_S____4 | 3 Phase fault on CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARSN_T4__S_S____4 | 3 Phase fault on CARSN-T4 (509739) 138 kV Bus a. Apply fault at the CARSN-T4 (509739) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARSN-T4 138.0 KV 509739 TO S.S.---4 138.0 KV 509815 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARTER_4__CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CARTER_4__CHIKSAW4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO CHIKSAW4 138.0 KV 515171 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARTER_4__HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CARTER_4__HONEYCK4 | 3 Phase fault on CARTER 4 (515138) 138 kV Bus a. Apply fault at the CARTER 4 (515138) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTER 4 138.0 KV 515138 TO HONEYCK4 138.0 KV 515643 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARTRCO4__GEN_2017_027 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CARTRCO4__GEN_2017_027 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO GEN-2017-027 138.0 KV 588710 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CARTRCO4__ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265). Crashes using default acceleration of 0.6 | Remove Reclose. Disable the PPC for GEN-2017-232 (760265). Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | CARTRCO4__ORIGINW4 | 3 Phase fault on CARTRCO4 (515561) 138 kV Bus a. Apply fault at the CARTRCO4 (515561) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CARTRCO4 138.0 KV 515561 TO ORIGINW4 138.0 KV 515563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | CASHION4__TWNLKJT4 | 3 Phase fault on CASHION4 (520479) 138 kV Bus a. Apply fault at the CASHION4 (520479) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138.0 KV 520479 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CASHION4__TWNLKJT4 | 3 Phase fault on CASHION4 (520479) 138 kV Bus a. Apply fault at the CASHION4 (520479) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CASHION4 138.0 KV 520479 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CDRDLTP4__MOORLND4 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138.0 KV 520425 TO CDRDLTP4 138.0 KV 520848 CKT 1 b.2. PIC4 138.0 KV 520425 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CDRDLTP4__MOORLND4 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. PIC4 138.0 KV 520425 TO CDRDLTP4 138.0 KV 520848 CKT 1 b.2. PIC4 138.0 KV 520425 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CDRDLTP4__OKEENE_4 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CDRDLTP4__OKEENE_4 | 3 Phase fault on CDRDLTP4 (520848) 138 kV Bus a. Apply fault at the CDRDLTP4 (520848) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CDRDLTP4 138.0 KV 520848 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CEDARLN4__SOONRTP4 | 3 Phase fault on CEDARLN4 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CEDARLN4__SOONRTP4 | 3 Phase fault on CEDARLN4 (514948) 138 kV Bus a. Apply fault at the CEDARLN4 (514948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDARLN4 138.0 KV 514948 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CEDRDAL4__CDRDLTP4 | 3 Phase fault on CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138.0 KV 520507 TO CDRDLTP4 138.0 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CEDRDAL4__CDRDLTP4 | 3 Phase fault on CEDRDAL4 (520507) 138 kV Bus a. Apply fault at the CEDRDAL4 (520507) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CEDRDAL4 138.0 KV 520507 TO CDRDLTP4 138.0 KV 520848 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHAMSPR5__506945_0 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5( 506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 506944 TO CHAMSPR7 506945 TO CHAMSPR1 506919 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHAMSPR5__506945_0 | 3 Phase fault on CHAMSPR5 (506944) 161 kV Bus a. Apply fault at the CHAMSPR5( 506944) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAMSPR5 506944 TO CHAMSPR7 506945 TO CHAMSPR1 506919 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHAMSPR7__CLARKSV7 | 3 Phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO CLARKSV7 345.0 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHAMSPR7__CLARKSV7 | 3 Phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO CLARKSV7 345.0 KV 509745 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHAMSPR7__TONTITN7 | 3 Phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO TONTITN7 345.0 KV 506959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHAMSPR7__TONTITN7 | 3 Phase fault on CHAMSPR7 (506945) 345 kV Bus a. Apply fault at the CHAMSPR7 (506945) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHAMSPR7 345.0 KV 506945 TO TONTITN7 345.0 KV 506959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHAN+TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHAN+TASCOS6__POTTER_CO__6 | 3 Phase fault on CHAN+TASCOS6 (523869) 230 kV Bus a. Apply fault at the CHAN+TASCOS6 (523869) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAN+TASCOS6 230.0 KV 523869 TO POTTER_CO 6 230.0 KV 523959 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHAPELH4__CHAPLHL4 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHAPELH4__CHAPLHL4 | 3 Phase fault on CHAPELH4 (508337) 138 kV Bus a. Apply fault at the CHAPELH4 (508337) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHAPELH4 138.0 KV 508337 TO CHAPLHL4 138.0 KV 509664 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHEEKTP4_138kV_515415 | Apply single-phase fault on: LONEGRV4 138KV 515144 TO CHEEKTP4 138KV 515415 CKT 1 and SUNNYSD4 138KV 515135 TO LONEGRV4 138KV 515144 CKT 1, near CHEEKTP4 138kV for 7 cycles with stuck breaker at CHEEKTP4 138kV. Clear Fault after 16 cycles and trip: WOLFCRK4 138KV 515143 TO CHEEKTP4 138KV 515415 CKT 1 and DILLARD4 138KV 515142 TO WOLFCRK4 138KV 515143 CKT 1 and HLTNTAP4 138KV 515141 TO DILLARD4 138KV 515142 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CHEEKTP4_138kV_515415 | Apply single-phase fault on: LONEGRV4 138KV 515144 TO CHEEKTP4 138KV 515415 CKT 1 and SUNNYSD4 138KV 515135 TO LONEGRV4 138KV 515144 CKT 1, near CHEEKTP4 138kV for 7 cycles with stuck breaker at CHEEKTP4 138kV. Clear Fault after 16 cycles and trip: WOLFCRK4 138KV 515143 TO CHEEKTP4 138KV 515415 CKT 1 and DILLARD4 138KV 515142 TO WOLFCRK4 138KV 515143 CKT 1 and HLTNTAP4 138KV 515141 TO DILLARD4 138KV 515142 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHIKSAW4_138kV_515171 | Apply single-phase fault on: CARTER4 138KV 515138 TO CHIKSAW4 138KV 515171 CKT 1, near CHIKSAW4 138kV for 7 cycles with stuck breaker at CHIKSAW4 138kV. Clear Fault after 16 cycles and trip: TOTAL4 138KV 515165 TO CHIKSAW4 138KV 515171 CKT 1 and TOTAL4 138KV 515165 TO AIRPRKT4 138KV 515169 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHIKSAW4_138kV_515171 | Apply single-phase fault on: CARTER4 138KV 515138 TO CHIKSAW4 138KV 515171 CKT 1, near CHIKSAW4 138kV for 7 cycles with stuck breaker at CHIKSAW4 138kV. Clear Fault after 16 cycles and trip: TOTAL4 138KV 515165 TO CHIKSAW4 138KV 515171 CKT 1 and TOTAL4 138KV 515165 TO AIRPRKT4 138KV 515169 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHISHOLM_345kV_511553 | Apply single-phase fault on: CHISHOLM7 345KV 511553 TO WWBORDT 345.0 KV 755000 CKT 1, near CHISHOLM7 345 kV for 6 cycles with stuck breaker at CHISHOLM7 345 kV. Clear Fault after 16 cycles and trip: CHISHOLM7 345KV 511553 TO G16037TAP 345KV 560078 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHISHOLM_345kV_511553 | Apply single-phase fault on: CHISHOLM7 345KV 511553 TO WWBORDT 345.0 KV 755000 CKT 1, near CHISHOLM7 345 kV for 6 cycles with stuck breaker at CHISHOLM7 345 kV. Clear Fault after 16 cycles and trip: CHISHOLM7 345KV 511553 TO G16037TAP 345KV 560078 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHISHOLM6__511553_0 | 3 Phase fault on CHISHOLM6 (511557) 230 kV Bus a. Apply fault at the CHISHOLM6( 511557) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHISHOLM6 511557 TO CHISHOLM7 511553 TO CHISHOLM1 511558 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHISHOLM7__G16_037_TAP | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO G16-037-TAP 345.0 KV 560078 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHISHOLM7__WWDBORDT | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHISHOLM7__WWDBORDT | 3 Phase fault on CHISHOLM7 (511553) 345 kV Bus a. Apply fault at the CHISHOLM7 (511553) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CHISHOLM7 345.0 KV 511553 TO WWDBORDT 345.0 KV 755000 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CHTWOOD4__JONESSB4 | 3 Phase fault on CHTWOOD4 (514842) 138 kV Bus a. Apply fault at the CHTWOOD4 (514842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CHTWOOD4__JONESSB4 | 3 Phase fault on CHTWOOD4 (514842) 138 kV Bus a. Apply fault at the CHTWOOD4 (514842) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CHTWOOD4 138.0 KV 514842 TO JONESSB4 138.0 KV 515480 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CIMARON4__514901_0 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CIMARON4__514901_0 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4( 514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CIMARON4 514898 TO CIMARON7 514901 TO CIMARO21 515715 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CIMARON4__MCCLAIN4 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138.0 KV 514895 TO CIMARON4 138.0 KV 514898 CKT 1 b.2. SARA 4 138.0 KV 514895 TO MCCLAIN4 138.0 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CIMARON4__MCCLAIN4 | 3 Phase fault on CIMARON4 (514898) 138 kV Bus a. Apply fault at the CIMARON4 (514898) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. SARA 4 138.0 KV 514895 TO CIMARON4 138.0 KV 514898 CKT 1 b.2. SARA 4 138.0 KV 514895 TO MCCLAIN4 138.0 KV 514902 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | CIMARON4_138kV_514898 | Apply single-phase fault on: HAYMAKR4 138KV 514863 TO CIMARON4 138KV 514898 CKT 1 and DIVISION4 138KV 514853 TO HAYMAKR4 138KV 514863 CKT 1, near CIMARON4 138kV for 7 cycles with stuck breaker at CIMARON4 138kV. Clear Fault after 16 cycles and trip: CZECHAL4 138KV 514894 TO CIMARON4 138KV 514898 CKT 1 and XEROX4 138KV 514893 TO CZECHAL4 138KV 514894 CKT 1 and XEROX4 138KV 514893 TO MORGAN4 138KV 514896 CKT 1 and MUSTANG4 138KV 514861 TO MORGAN4 138KV 514896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CIMARON4_138kV_514898 | Apply single-phase fault on: HAYMAKR4 138KV 514863 TO CIMARON4 138KV 514898 CKT 1 and DIVISION4 138KV 514853 TO HAYMAKR4 138KV 514863 CKT 1, near CIMARON4 138kV for 7 cycles with stuck breaker at CIMARON4 138kV. Clear Fault after 16 cycles and trip: CZECHAL4 138KV 514894 TO CIMARON4 138KV 514898 CKT 1 and XEROX4 138KV 514893 TO CZECHAL4 138KV 514894 CKT 1 and XEROX4 138KV 514893 TO MORGAN4 138KV 514896 CKT 1 and MUSTANG4 138KV 514861 TO MORGAN4 138KV 514896 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CIMARON7__FSHRTAP7 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CIMARON7__FSHRTAP7 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO FSHRTAP7 345.0 KV 515610 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25S | Transfer | CIMARON7__MATHWSN7 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CIMARON7__MATHWSN7 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO MATHWSN7 345.0 KV 515497 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25S | Transfer | CIMARON7__NSUB345 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CIMARON7__NSUB345 | 3 Phase fault on CIMARON7 (514901) 345 kV Bus a. Apply fault at the CIMARON7 (514901) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | GEN-2016-119 (587953, 587958) trips on Voltage Protection | Disable Voltage Protection for GEN-2016-119 (587953, 587958)
04 - Southeast | 25S | Transfer | CIMARON7_345kV_514901 | Apply single-phase fault on: MINCO7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1, near CIMARON7 345kV for 6 cycles with stuck breaker at CIMARON7 345kV. Clear Fault after 16 cycles and trip: CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CIMARON7_345kV_514901 | Apply single-phase fault on: MINCO7 345.0 KV 514801 TO CIMARON7 345.0 KV 514901 CKT 1, near CIMARON7 345kV for 6 cycles with stuck breaker at CIMARON7 345kV. Clear Fault after 16 cycles and trip: CIMARON7 345.0 KV 514901 TO NSUB345 345.0 KV 555234 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKCOUNTY7__THISTLE7 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLARKCOUNTY7__THISTLE7 | 3 Phase fault on CLARKCOUNTY7 (539800) 345 kV Bus a. Apply fault at the CLARKCOUNTY7 (539800) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKCOUNTY7 345.0 KV 539800 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKSV7__GEN_2017_140 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-140 345.0 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CLARKSV7__GEN_2017_140 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-140 345.0 KV 760389 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKSV7__GEN_2017_213 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-213 345.0 KV 760368 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | CLARKSV7__GEN_2017_213 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO GEN-2017-213 345.0 KV 760368 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | CLARKSV7__MUSKOGE7 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CLARKSV7__MUSKOGE7 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKSV7__ONETA__7 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CLARKSV7__ONETA__7 | 3 Phase fault on CLARKSV7 (509745) 345 kV Bus a. Apply fault at the CLARKSV7 (509745) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CLARKSV7 345.0 KV 509745 TO ONETA--7 345.0 KV 509807 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLARKSV7_345kV_509749 | Apply single-phase fault on: CLARKSV7 345KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1, near CLARKSV7 345kV for 6 cycles with stuck breaker at CLARKSV7 345kV. Clear Fault after 16 cycles and trip: CHAMSPR7 345KV 506945 TO CLARKSV7 345KV 509745 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLARKSV7_345kV_509749 | Apply single-phase fault on: CLARKSV7 345KV 509745 TO MUSKOGE7 345.0 KV 515224 CKT 1, near CLARKSV7 345kV for 6 cycles with stuck breaker at CLARKSV7 345kV. Clear Fault after 16 cycles and trip: CHAMSPR7 345KV 506945 TO CLARKSV7 345KV 509745 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLASSEN4__TROSPER4 | 3 Phase fault on CLASSEN4 (514922) 138 kV Bus a. Apply fault at the CLASSEN4 (514922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 b.2. LOAD 1 515851 b.3. LIGHTCK4 138.0 KV 514923 TO CROSTWN4 138.0 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CLASSEN4__TROSPER4 | 3 Phase fault on CLASSEN4 (514922) 138 kV Bus a. Apply fault at the CLASSEN4 (514922) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLASSEN4 138.0 KV 514922 TO CROSTWN4 138.0 KV 515851 CKT 1 b.2. LOAD 1 515851 b.3. LIGHTCK4 138.0 KV 514923 TO CROSTWN4 138.0 KV 515851 CKT 1 b.4. LOAD 1 515851 b.5. LIGHTCK4 138.0 KV 514923 TO TROSPER4 138.0 KV 514963 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | CLVLDSW4__AMBERTP4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLVLDSW4__AMBERTP4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO AMBERTP4 138.0 KV 520530 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLVLDSW4__ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLVLDSW4__ANADARK4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO ANADARK4 138.0 KV 520814 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CLVLDSW4__COGAR__4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CLVLDSW4__COGAR__4 | 3 Phase fault on CLVLDSW4 (520508) 138 kV Bus a. Apply fault at the CLVLDSW4 (520508) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CLVLDSW4 138.0 KV 520508 TO COGAR 4 138.0 KV 520859 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CMBLCRK4__CMBLTP_4 | 3 Phase fault on CMBLCRK4 (515930) 138 kV Bus a. Apply fault at the CMBLCRK4 (515930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138.0 KV 515930 TO CMBLTP 4 138.0 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CMBLCRK4__CMBLTP_4 | 3 Phase fault on CMBLCRK4 (515930) 138 kV Bus a. Apply fault at the CMBLCRK4 (515930) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLCRK4 138.0 KV 515930 TO CMBLTP 4 138.0 KV 520474 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CMBLTP_4__FOURCTP4 | 3 Phase fault on CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO FOURCTP4 138.0 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CMBLTP_4__FOURCTP4 | 3 Phase fault on CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO FOURCTP4 138.0 KV 520545 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CMBLTP_4__KGFSHSW4 | 3 Phase fault on CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO REEDING4 138.0 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. KGFSHSW4 138.0 KV 520533 TO REEDING4 138.0 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CMBLTP_4__KGFSHSW4 | 3 Phase fault on CMBLTP 4 (520474) 138 kV Bus a. Apply fault at the CMBLTP 4 (520474) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CMBLTP 4 138.0 KV 520474 TO REEDING4 138.0 KV 521037 CKT 1 b.2. LOAD 1 521037 b.3. KGFSHSW4 138.0 KV 520533 TO REEDING4 138.0 KV 521037 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COGEN_G1__509834_0 | 3 Phase fault on COGEN G1 (511953) 18 kV Bus a. Apply fault at the COGEN G1( 511953) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COGEN G1 511953 TO COGENT 7 509834 TO COGEN S1 511954 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COGEN_G1__509834_0 | 3 Phase fault on COGEN G1 (511953) 18 kV Bus a. Apply fault at the COGEN G1( 511953) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COGEN G1 511953 TO COGENT 7 509834 TO COGEN S1 511954 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COGEN_G2__509834_0 | 3 Phase fault on COGEN G2 (511955) 18 kV Bus a. Apply fault at the COGEN G2( 511955) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COGEN G2 511955 TO COGENT 7 509834 TO COGEN S2 511956 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COGEN_G2__509834_0 | 3 Phase fault on COGEN G2 (511955) 18 kV Bus a. Apply fault at the COGEN G2( 511955) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COGEN G2 511955 TO COGENT 7 509834 TO COGEN S2 511956 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COGEN_G3__509834_0 | 3 Phase fault on COGEN G3 (511957) 18 kV Bus a. Apply fault at the COGEN G3( 511957) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COGEN G3 511957 TO COGENT 7 509834 TO COGEN S3 511958 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COGEN_G3__509834_0 | 3 Phase fault on COGEN G3 (511957) 18 kV Bus a. Apply fault at the COGEN G3( 511957) 18 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COGEN G3 511957 TO COGENT 7 509834 TO COGEN S3 511958 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | COMANC_2__L_E_S__2 | 3 Phase fault on COMANC-2 (511436) 69 kV Bus a. Apply fault at the COMANC-2 (511436) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-2 69.0 KV 511436 TO L.E.S.-2 69.0 KV 511466 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | COMANC_4__112GORE4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO 112GORE4 138.0 KV 511488 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | COMANC_4__COMMTAP4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO COMMTAP4 138.0 KV 511494 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | COMANC_4__L_E_S__4 | 3 Phase fault on COMANC-4 (511437) 138 kV Bus a. Apply fault at the COMANC-4 (511437) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMANC-4 138.0 KV 511437 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | COMMTAP4__OMDUNCN4 | 3 Phase fault on COMMTAP4 (511494) 138 kV Bus a. Apply fault at the COMMTAP4 (511494) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. COMMTAP4 138.0 KV 511494 TO OMDUNCN4 138.0 KV 529304 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CRAIGJT4__MTRIVER4 | 3 Phase fault on CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIGJT4 138.0 KV 510890 TO MTRIVER4 138.0 KV 521004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | CRAIGJT4__MTRIVER4 | 3 Phase fault on CRAIGJT4 (510890) 138 kV Bus a. Apply fault at the CRAIGJT4 (510890) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRAIGJT4 138.0 KV 510890 TO MTRIVER4 138.0 KV 521004 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CRESENT4__GEN_2016_032 | 3 Phase fault on CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO GEN-2016-032 138.0 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CRESENT4__GEN_2016_032 | 3 Phase fault on CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO GEN-2016-032 138.0 KV 587210 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CRESENT4__TWNLKSW4 | 3 Phase fault on CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CRESENT4__TWNLKSW4 | 3 Phase fault on CRESENT4 (515377) 138 kV Bus a. Apply fault at the CRESENT4 (515377) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CRESENT4 138.0 KV 515377 TO TWNLKSW4 138.0 KV 521073 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CRSRDSW7__515449_0 | 3 Phase fault on CRSRDSW7 (515448) 345 kV Bus a. Apply fault at the CRSRDSW7( 515448) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRSRDSW7 515448 TO CRSRDW11 515449 TO CRSRDWT1 515451 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CRSRDSW7__515449_0 | 3 Phase fault on CRSRDSW7 (515448) 345 kV Bus a. Apply fault at the CRSRDSW7( 515448) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRSRDSW7 515448 TO CRSRDW11 515449 TO CRSRDWT1 515451 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CRSRDSW7__515450_0 | 3 Phase fault on CRSRDSW7 (515448) 345 kV Bus a. Apply fault at the CRSRDSW7( 515448) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRSRDSW7 515448 TO CRSRDW21 515450 TO CRSRDWT2 515452 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CRSRDSW7__515450_0 | 3 Phase fault on CRSRDSW7 (515448) 345 kV Bus a. Apply fault at the CRSRDSW7( 515448) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. CRSRDSW7 515448 TO CRSRDW21 515450 TO CRSRDWT2 515452 CKT 2 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CTNWOOD4__ARCADIA4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CTNWOOD4__ARCADIA4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO ARCADIA4 138.0 KV 514907 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CTNWOOD4__CRESENT4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CTNWOOD4__CRESENT4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO CRESENT4 138.0 KV 515377 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CTNWOOD4__LBRTYLK4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CTNWOOD4__LBRTYLK4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO LBRTYLK4 138.0 KV 515373 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CTNWOOD4__PINE_ST4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CTNWOOD4__PINE_ST4 | 3 Phase fault on CTNWOOD4 (514827) 138 kV Bus a. Apply fault at the CTNWOOD4 (514827) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CTNWOOD4 138.0 KV 514827 TO PINE ST4 138.0 KV 514829 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | CZECHAL4__CIMARON4 | 3 Phase fault on CZECHAL4 (514894) 138 kV Bus a. Apply fault at the CZECHAL4 (514894) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CZECHAL4 138.0 KV 514894 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | CZECHAL4__CIMARON4 | 3 Phase fault on CZECHAL4 (514894) 138 kV Bus a. Apply fault at the CZECHAL4 (514894) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. CZECHAL4 138.0 KV 514894 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | DANFRTH4__ARCADIA4 | 3 Phase fault on DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 b.2. LOAD 1 514833 b.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DANFRTH4__ARCADIA4 | 3 Phase fault on DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. BURGETT4 138.0 KV 514510 TO DANFRTH4 138.0 KV 514833 CKT 1 b.2. LOAD 1 514833 b.3. BURGETT4 138.0 KV 514510 TO RNDBARN4 138.0 KV 515461 CKT 1 b.4. LOAD 1 515461 b.5. ARCADIA4 138.0 KV 514907 TO RNDBARN4 138.0 KV 515461 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DANFRTH4__KETCH__4 | 3 Phase fault on DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DANFRTH4__KETCH__4 | 3 Phase fault on DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO KETCH 4 138.0 KV 514834 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DANFRTH4__MEMRIAL4 | 3 Phase fault on DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 b.2. LOAD 1 515469 b.3. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DANFRTH4__MEMRIAL4 | 3 Phase fault on DANFRTH4 (514833) 138 kV Bus a. Apply fault at the DANFRTH4 (514833) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DANFRTH4 138.0 KV 514833 TO HAFERSB4 138.0 KV 515469 CKT 1 b.2. LOAD 1 515469 b.3. EASTERN4 138.0 KV 514832 TO HAFERSB4 138.0 KV 515469 CKT 1 b.4. LOAD 1 515469 b.5. EASTERN4 138.0 KV 514832 TO MEMRIAL4 138.0 KV 514835 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DAYTON_4__HOBBYLO4 | 3 Phase fault on DAYTON 4 (514892) 138 kV Bus a. Apply fault at the DAYTON 4 (514892) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 138.0 KV 514892 TO HOBBYLO4 138.0 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DAYTON_4__HOBBYLO4 | 3 Phase fault on DAYTON 4 (514892) 138 kV Bus a. Apply fault at the DAYTON 4 (514892) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DAYTON 4 138.0 KV 514892 TO HOBBYLO4 138.0 KV 515338 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | DEEPFKT2__DEEPFRK2 | 3 Phase fault on DEEPFKT2 (514970) 69 kV Bus a. Apply fault at the DEEPFKT2 (514970) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69.0 KV 514970 TO DEEPFRK2 69.0 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DEEPFKT2__DEEPFRK2 | 3 Phase fault on DEEPFKT2 (514970) 69 kV Bus a. Apply fault at the DEEPFKT2 (514970) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEEPFKT2 69.0 KV 514970 TO DEEPFRK2 69.0 KV 514974 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DELWARE7__N_E_S__7 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DELWARE7__N_E_S__7 | 3 Phase fault on DELWARE7 (510380) 345 kV Bus a. Apply fault at the DELWARE7 (510380) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DELWARE7 345.0 KV 510380 TO N.E.S.-7 345.0 KV 510406 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DENVR_W4__DENV_WTAP4 | 3 Phase fault on DENVR-W4 (509748) 138 kV Bus a. Apply fault at the DENVR-W4 (509748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-W4 138.0 KV 509748 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DENVR_W4__DENV_WTAP4 | 3 Phase fault on DENVR-W4 (509748) 138 kV Bus a. Apply fault at the DENVR-W4 (509748) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DENVR-W4 138.0 KV 509748 TO DENV_WTAP4 138.0 KV 509896 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DEQUEEN4__CRAIGJT4 | 3 Phase fault on DEQUEEN4 (507419) 138 kV Bus a. Apply fault at the DEQUEEN4 (507419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN4 138.0 KV 507419 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DEQUEEN4__CRAIGJT4 | 3 Phase fault on DEQUEEN4 (507419) 138 kV Bus a. Apply fault at the DEQUEEN4 (507419) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DEQUEEN4 138.0 KV 507419 TO CRAIGJT4 138.0 KV 510890 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE4__515852_0 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4( 515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE4__515852_0 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4( 515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 515853 TO DGRASSE7 515852 TO DGRASSE1 515854 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE4__GEN_2015_095 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2015-095 138.0 KV 585300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE4__GEN_2015_095 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO GEN-2015-095 138.0 KV 585300 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE4__MOORLND4 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE4__MOORLND4 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO MOORLND4 138.0 KV 520999 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE4__ROSEVLY4 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE4__ROSEVLY4 | 3 Phase fault on DGRASSE4 (515853) 138 kV Bus a. Apply fault at the DGRASSE4 (515853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DGRASSE4 138.0 KV 515853 TO ROSEVLY4 138.0 KV 520436 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DGRASSE7__THISTLE7 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DGRASSE7__THISTLE7 | 3 Phase fault on DGRASSE7 (515852) 345 kV Bus a. Apply fault at the DGRASSE7 (515852) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DGRASSE7 345.0 KV 515852 TO THISTLE7 345.0 KV 539801 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DIANA__4__508832_0 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DIANA__4__508832_0 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4( 508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 508831 TO DIANA 7 508832 TO DIANA-N1 508845 CKT 3 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DIANA__4__DIANASW4 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO DIANASW4 138.0 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DIANA__4__DIANASW4 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO DIANASW4 138.0 KV 509639 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DIANA__4__NGPLTAP4 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO NGPLTAP4 138.0 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DIANA__4__NGPLTAP4 | 3 Phase fault on DIANA 4 (508831) 138 kV Bus a. Apply fault at the DIANA 4 (508831) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DIANA 4 138.0 KV 508831 TO NGPLTAP4 138.0 KV 508837 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DIVISION4_138kV_514853 | Apply single-phase fault on: DIVISION4 138KV 514853 TO HAYMAKR4 138KV 514863 CKT 1 and HAYMAKR4 138KV 514863 TO CIMARON4 138KV 514898 CKT 1, near DIVISION4 138kV for 7 cycles with stuck breaker at DIVISION4 138kV. Clear Fault after 16 cycles and trip: LAKESID4 138KV 514849 TO DIVISION4 138KV 514853 CKT 1 and HEFNER4 138KV 514848 TO LAKESID4 138KV 514849 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DIVISION4_138kV_514853 | Apply single-phase fault on: DIVISION4 138KV 514853 TO HAYMAKR4 138KV 514863 CKT 1 and HAYMAKR4 138KV 514863 TO CIMARON4 138KV 514898 CKT 1, near DIVISION4 138kV for 7 cycles with stuck breaker at DIVISION4 138kV. Clear Fault after 16 cycles and trip: LAKESID4 138KV 514849 TO DIVISION4 138KV 514853 CKT 1 and HEFNER4 138KV 514848 TO LAKESID4 138KV 514849 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DMNDSPG7__516004_0 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL11 516004 TO DMNDST11 516008 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DMNDSPG7__516004_0 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL11 516004 TO DMNDST11 516008 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DMNDSPG7__516005_0 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL21 516005 TO DMNDST21 516007 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DMNDSPG7__516005_0 | 3 Phase fault on DMNDSPG7 (516006) 345 kV Bus a. Apply fault at the DMNDSPG7( 516006) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DMNDSPG7 516006 TO DMNDSL21 516005 TO DMNDST21 516007 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOLHILL7__SW_SHV_7 | 3 Phase fault on DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOLHILL7__SW_SHV_7 | 3 Phase fault on DOLHILL7 (500250) 345 kV Bus a. Apply fault at the DOLHILL7 (500250) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DOLHILL7 345.0 KV 500250 TO SW SHV 7 345.0 KV 507760 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOUGLTP4__CLASSEN4 | 3 Phase fault on DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138.0 KV 514868 TO CLASSEN4 138.0 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | DOUGLTP4__CLASSEN4 | 3 Phase fault on DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138.0 KV 514868 TO CLASSEN4 138.0 KV 514922 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | DOUGLTP4__MUSTANG4 | 3 Phase fault on DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 b.2. WESTOAK4 138.0 KV 514866 TO MERIDAN4 138.0 KV 514867 CKT 1 b.3. LOAD 1 514867 b.4. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 b.5. LOAD 1 514866 b.6. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | DOUGLTP4__MUSTANG4 | 3 Phase fault on DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. MERIDAN4 138.0 KV 514867 TO DOUGLTP4 138.0 KV 514868 CKT 1 b.2. WESTOAK4 138.0 KV 514866 TO MERIDAN4 138.0 KV 514867 CKT 1 b.3. LOAD 1 514867 b.4. COUNCIL4 138.0 KV 514865 TO WESTOAK4 138.0 KV 514866 CKT 1 b.5. LOAD 1 514866 b.6. MUSTANG4 138.0 KV 514861 TO COUNCIL4 138.0 KV 514865 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | DOUGLTP4__WESTERN4 | 3 Phase fault on DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138.0 KV 514868 TO WESTERN4 138.0 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | DOUGLTP4__WESTERN4 | 3 Phase fault on DOUGLTP4 (514868) 138 kV Bus a. Apply fault at the DOUGLTP4 (514868) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOUGLTP4 138.0 KV 514868 TO WESTERN4 138.0 KV 514869 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | DOVERSW2__HENESEY2 | 3 Phase fault on DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO HENESEY2 69.0 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERSW2__HENESEY2 | 3 Phase fault on DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO HENESEY2 69.0 KV 520940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERSW2__LACEY__2 | 3 Phase fault on DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO LACEY 2 69.0 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | DOVERSW2__LACEY__2 | 3 Phase fault on DOVERSW2 (520881) 69 kV Bus a. Apply fault at the DOVERSW2 (520881) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW2 69.0 KV 520881 TO LACEY 2 69.0 KV 520967 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERSW4__520881_0 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.3
04 - Southeast | 25W | Transfer | DOVERSW4__520881_0 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4( 520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 520882 TO DOVERSW2 520881 TO DVRTERT 521166 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | DOVERSW4__GEN_2016_118 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | DOVERSW4__GEN_2016_118 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2016-118 138.0 KV 587940 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | DOVERSW4__GEN_2018_011 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Generator Islanded. Crashes using default acceleration of 0.6 | Remove Reclose. Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | DOVERSW4__GEN_2018_011 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO GEN-2018-011 138.0 KV 762493 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6. Generator Islanded | Lower acceleration to 0.2. Remove Reclose
04 - Southeast | 25S | Transfer | DOVERSW4__OKEENE_4 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERSW4__OKEENE_4 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERSW4 138.0 KV 520882 TO OKEENE 4 138.0 KV 521016 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | DOVERSW4__TWNLKSW4 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 b.2. TWNLAKE4 138.0 KV 520540 TO DOVER 4 138.0 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERSW4__TWNLKSW4 | 3 Phase fault on DOVERSW4 (520882) 138 kV Bus a. Apply fault at the DOVERSW4 (520882) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVER 4 138.0 KV 520879 TO DOVERSW4 138.0 KV 520882 CKT 1 b.2. TWNLAKE4 138.0 KV 520540 TO DOVER 4 138.0 KV 520879 CKT 1 b.3. LOAD 1 520879 b.4. TWNLAKE4 138.0 KV 520540 TO TWNLKSW4 138.0 KV 521073 CKT Z1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25W | Transfer | DOVERSW4_138kV_520881 | Apply single-phase fault on: DOVERSW2 138KV 520881 TO DOVERTP2 138KV 514772 CKT 1, near DOVERSW2 69 kV for 7 cycles with stuck breaker at DOVERSW2 69 kV. Clear Fault after 16 cycles and trip: DOVERSW2 138KV 520881 TO LACEY2 138KV 520967 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERSW4_138kV_520881 | Apply single-phase fault on: DOVERSW2 138KV 520881 TO DOVERTP2 138KV 514772 CKT 1, near DOVERSW2 69 kV for 7 cycles with stuck breaker at DOVERSW2 69 kV. Clear Fault after 16 cycles and trip: DOVERSW2 138KV 520881 TO LACEY2 138KV 520967 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERSW4_138kV_520882 | Apply single-phase fault on: BULFTTP4 138KV 520535 TO DOVERSW4 138KV 520882 CKT 1, near DOVERSW4 138kV for 7 cycles with stuck breaker at DOVERSW4 138kV. Clear Fault after 16 cycles and trip: NKNGFSH4 138KV 520603 TO DOVERSW4 138KV 520882 CKT 1 and KGFSJCT4 138KV 520405 TO NKNGFSH4 138KV 520603 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERSW4_138kV_520882 | Apply single-phase fault on: BULFTTP4 138KV 520535 TO DOVERSW4 138KV 520882 CKT 1, near DOVERSW4 138kV for 7 cycles with stuck breaker at DOVERSW4 138kV. Clear Fault after 16 cycles and trip: NKNGFSH4 138KV 520603 TO DOVERSW4 138KV 520882 CKT 1 and KGFSJCT4 138KV 520405 TO NKNGFSH4 138KV 520603 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERTP2__DOVERSW2 | 3 Phase fault on DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO DOVERSW2 69.0 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERTP2__DOVERSW2 | 3 Phase fault on DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO DOVERSW2 69.0 KV 520881 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERTP2__REDWING2 | 3 Phase fault on DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO REDWING2 69.0 KV 515976 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERTP2__REDWING2 | 3 Phase fault on DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO REDWING2 69.0 KV 515976 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DOVERTP2__TURCRKT2 | 3 Phase fault on DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO TURCRKT2 69.0 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DOVERTP2__TURCRKT2 | 3 Phase fault on DOVERTP2 (514772) 69 kV Bus a. Apply fault at the DOVERTP2 (514772) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DOVERTP2 69.0 KV 514772 TO TURCRKT2 69.0 KV 515517 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER_4__514934_0 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4( 514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 514933 TO DRAPER 7 514934 TO DRAPER21 515792 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DRAPER_4__514934_0 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4( 514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 514933 TO DRAPER 7 514934 TO DRAPER21 515792 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER_4__BARNES_4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | DRAPER_4__BARNES_4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO BARNES 4 138.0 KV 515003 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER_4__MIDWEST4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | DRAPER_4__MIDWEST4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER_4__SOONRTP4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | DRAPER_4__SOONRTP4 | 3 Phase fault on DRAPER 4 (514933) 138 kV Bus a. Apply fault at the DRAPER 4 (514933) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DRAPER 4 138.0 KV 514933 TO SOONRTP4 138.0 KV 514949 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER_7__NSUB345 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NSUB345 345.0 KV 555234 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DRAPER_7__NSUB345 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO NSUB345 345.0 KV 555234 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER_7__SEMINOL7 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DRAPER_7__SEMINOL7 | 3 Phase fault on DRAPER 7 (514934) 345 kV Bus a. Apply fault at the DRAPER 7 (514934) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. DRAPER 7 345.0 KV 514934 TO SEMINOL7 345.0 KV 515045 CKT 3 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 6 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DRAPER4_138kV_514933 | Apply single-phase fault on: DRAPER4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1, near DRAPER4 138kV for 7 cycles with stuck breaker at DRAPER4 138kV. Clear Fault after 16 cycles and trip: DRAPER4 138.0 KV 514933 TO BARNES4 138.0 KV 515003 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DRAPER4_138kV_514933 | Apply single-phase fault on: DRAPER4 138.0 KV 514933 TO MIDWEST4 138.0 KV 514946 CKT 1, near DRAPER4 138kV for 7 cycles with stuck breaker at DRAPER4 138kV. Clear Fault after 16 cycles and trip: DRAPER4 138.0 KV 514933 TO BARNES4 138.0 KV 515003 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DUGLASV2__MAUDT__2 | 3 Phase fault on DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69.0 KV 509645 TO MAUDT 2 69.0 KV 509653 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DUGLASV2__MAUDT__2 | 3 Phase fault on DUGLASV2 (509645) 69 kV Bus a. Apply fault at the DUGLASV2 (509645) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUGLASV2 69.0 KV 509645 TO MAUDT 2 69.0 KV 509653 CKT NO c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Crashes using default acceleration of 0.6 | Lower acceleration to 0.2
04 - Southeast | 25S | Transfer | DUNJEE_4__RENO___4 | 3 Phase fault on DUNJEE 4 (514884) 138 kV Bus a. Apply fault at the DUNJEE 4 (514884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 138.0 KV 514884 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DUNJEE_4__RENO___4 | 3 Phase fault on DUNJEE 4 (514884) 138 kV Bus a. Apply fault at the DUNJEE 4 (514884) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DUNJEE 4 138.0 KV 514884 TO RENO 4 138.0 KV 514973 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | DVISION4__CIMARON4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO HAYMAKR4 138.0 KV 514863 CKT 1 b.2. LOAD 1 514863 b.3. HAYMAKR4 138.0 KV 514863 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | DVISION4__CIMARON4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO HAYMAKR4 138.0 KV 514863 CKT 1 b.2. LOAD 1 514863 b.3. HAYMAKR4 138.0 KV 514863 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | DVISION4__MUSTANG4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO MUSTANG4 138.0 KV 514861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | DVISION4__MUSTANG4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO MUSTANG4 138.0 KV 514861 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | DVISION4__NORTWST4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO RICHRDS4 138.0 KV 514862 CKT 1 b.2. LOAD 1 514862 b.3. RICHRDS4 138.0 KV 514862 TO PIEDMNT4 138.0 KV 514864 CKT 1 b.4. LOAD 1 514864 b.5. PIEDMNT4 138.0 KV 514864 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | DVISION4__NORTWST4 | 3 Phase fault on DVISION4 (514853) 138 kV Bus a. Apply fault at the DVISION4 (514853) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DVISION4 138.0 KV 514853 TO RICHRDS4 138.0 KV 514862 CKT 1 b.2. LOAD 1 514862 b.3. RICHRDS4 138.0 KV 514862 TO PIEDMNT4 138.0 KV 514864 CKT 1 b.4. LOAD 1 514864 b.5. PIEDMNT4 138.0 KV 514864 TO NORTWST4 138.0 KV 514879 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | MSTNG 7G (515669) and MSTNG 6G (515668) trips on Voltage Protection | Disable Voltage Protection for MSTNG 7G (515669) and MSTNG 6G (515668)
04 - Southeast | 25S | Transfer | DX____W2__S_S____2 | 3 Phase fault on DX----W2 (509796) 69 kV Bus a. Apply fault at the DX----W2 (509796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69.0 KV 509796 TO S.S.---2 69.0 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | DX____W2__S_S____2 | 3 Phase fault on DX----W2 (509796) 69 kV Bus a. Apply fault at the DX----W2 (509796) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. DX----W2 69.0 KV 509796 TO S.S.---2 69.0 KV 509816 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EARLSBORO__4__MAUD___4 | 3 Phase fault on EARLSBORO 4 (510948) 138 kV Bus a. Apply fault at the EARLSBORO 4 (510948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138.0 KV 510948 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EARLSBORO__4__MAUD___4 | 3 Phase fault on EARLSBORO 4 (510948) 138 kV Bus a. Apply fault at the EARLSBORO 4 (510948) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EARLSBORO 4 138.0 KV 510948 TO MAUD 4 138.0 KV 515055 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EKNGFSH4__EKFSHTP4 | 3 Phase fault on EKNGFSH4 (520484) 138 kV Bus a. Apply fault at the EKNGFSH4 (520484) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138.0 KV 520484 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EKNGFSH4__EKFSHTP4 | 3 Phase fault on EKNGFSH4 (520484) 138 kV Bus a. Apply fault at the EKNGFSH4 (520484) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EKNGFSH4 138.0 KV 520484 TO EKFSHTP4 138.0 KV 520600 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EL_RENO_138kV_520893 | Apply single-phase fault on: JENSEN4 138KV 514821 TO ELRENO4 138KV 520893 CKT 1, near EL RENO 138kV for 7 cycles with stuck breaker at EL RENO 138kV. Clear Fault after 16 cycles and trip: ELRENO4 138KV 520893 TO SCOTTSW4 138KV 520899 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EL_RENO_138kV_520893 | Apply single-phase fault on: JENSEN4 138KV 514821 TO ELRENO4 138KV 520893 CKT 1, near EL RENO 138kV for 7 cycles with stuck breaker at EL RENO 138kV. Clear Fault after 16 cycles and trip: ELRENO4 138KV 520893 TO SCOTTSW4 138KV 520899 CKT 1 | P4_MEPPI | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EL_RENO4__CIMARON4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EL_RENO4__CIMARON4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO CIMARON4 138.0 KV 514898 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EL_RENO4__JENSENT4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EL_RENO4__JENSENT4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO JENSENT4 138.0 KV 514820 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EL_RENO4__ROMNOSE4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EL_RENO4__ROMNOSE4 | 3 Phase fault on EL-RENO4 (514819) 138 kV Bus a. Apply fault at the EL-RENO4 (514819) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EL-RENO4 138.0 KV 514819 TO OMEGA 4 138.0 KV 515962 CKT 1 b.2. LOAD 1 515962 b.3. ROMNOSE4 138.0 KV 514823 TO OMEGA 4 138.0 KV 515962 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELGINJT2__511486_0 | 3 Phase fault on ELGINJT2 (511487) 69 kV Bus a. Apply fault at the ELGINJT2( 511487) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT2 511487 TO ELGINJT4 511486 TO ELGJT1-1 511412 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELGINJT4__ELSWORTH___4 | 3 Phase fault on ELGINJT4 (511486) 138 kV Bus a. Apply fault at the ELGINJT4 (511486) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELGINJT4 138.0 KV 511486 TO ELSWORTH 4 138.0 KV 511563 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELKCITY6__CHISHOLM6 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELKCITY6__CHISHOLM6 | 3 Phase fault on ELKCITY6 (511490) 230 kV Bus a. Apply fault at the ELKCITY6 (511490) 230 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCITY6 230.0 KV 511490 TO CHISHOLM6 230.0 KV 511557 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELKCTY_4__511490_0 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4( 511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELKCTY_4__511490_0 | 3 Phase fault on ELKCTY-4 (511458) 138 kV Bus a. Apply fault at the ELKCTY-4( 511458) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELKCTY-4 511458 TO ELKCITY6 511490 TO ELKC2-1 511482 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELRENO_2__514819_0 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELRENO_2__514819_0 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2( 514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 514818 TO EL-RENO4 514819 TO EL RENO1 515722 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ELRENO_2__OKRCHET2 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2 (514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 69.0 KV 514818 TO OKRCHET2 69.0 KV 515506 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ELRENO_2__OKRCHET2 | 3 Phase fault on ELRENO 2 (514818) 69 kV Bus a. Apply fault at the ELRENO 2 (514818) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ELRENO 2 69.0 KV 514818 TO OKRCHET2 69.0 KV 515506 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EMPIRE_4__FLETCH_4 | 3 Phase fault on EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138.0 KV 520900 TO FLETCH-4 138.0 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EMPIRE_4__FLETCH_4 | 3 Phase fault on EMPIRE 4 (520900) 138 kV Bus a. Apply fault at the EMPIRE 4 (520900) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EMPIRE 4 138.0 KV 520900 TO FLETCH-4 138.0 KV 520912 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | ERLSBOR2__FRSTHIL2 | 3 Phase fault on ERLSBOR2 (515073) 69 kV Bus a. Apply fault at the ERLSBOR2 (515073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FRSTHIL2 69.0 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | ERLSBOR2__FRSTHIL2 | 3 Phase fault on ERLSBOR2 (515073) 69 kV Bus a. Apply fault at the ERLSBOR2 (515073) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. ERLSBOR2 69.0 KV 515073 TO FRSTHIL2 69.0 KV 515074 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EUFREST2__WELLSPA2 | 3 Phase fault on EUFREST2 (515214) 69 kV Bus a. Apply fault at the EUFREST2 (515214) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFREST2 69.0 KV 515214 TO WELLSPA2 69.0 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EUFREST2__WELLSPA2 | 3 Phase fault on EUFREST2 (515214) 69 kV Bus a. Apply fault at the EUFREST2 (515214) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EUFREST2 69.0 KV 515214 TO WELLSPA2 69.0 KV 515215 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EXPLGLN4__EXPGLNT4 | 3 Phase fault on EXPLGLN4 (515248) 138 kV Bus a. Apply fault at the EXPLGLN4 (515248) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLGLN4 138.0 KV 515248 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EXPLGLN4__EXPGLNT4 | 3 Phase fault on EXPLGLN4 (515248) 138 kV Bus a. Apply fault at the EXPLGLN4 (515248) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EXPLGLN4 138.0 KV 515248 TO EXPGLNT4 138.0 KV 515473 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | EYLAU__4__BUCHANN4 | 3 Phase fault on EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138.0 KV 509655 TO BUCHANN4 138.0 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | EYLAU__4__BUCHANN4 | 3 Phase fault on EYLAU 4 (509655) 138 kV Bus a. Apply fault at the EYLAU 4 (509655) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. EYLAU 4 138.0 KV 509655 TO BUCHANN4 138.0 KV 509656 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAIRVEW2__OKEENE_2 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAIRVEW2__OKEENE_2 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OKEENE 2 69.0 KV 521015 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAIRVEW2__OMFAIRV2 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OMFAIRV2 69.0 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAIRVEW2__OMFAIRV2 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO OMFAIRV2 69.0 KV 529343 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FAIRVEW2__RNGWODJ2 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FAIRVEW2__RNGWODJ2 | 3 Phase fault on FAIRVEW2 (520909) 69 kV Bus a. Apply fault at the FAIRVEW2 (520909) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FAIRVEW2 69.0 KV 520909 TO RNGWODJ2 69.0 KV 521039 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLE_TAP4__G16_097_TAP | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO G16-097-TAP 138.0 KV 587794 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLE_TAP4__L_E_S__4 | 3 Phase fault on FLE TAP4 (511423) 138 kV Bus a. Apply fault at the FLE TAP4 (511423) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLE TAP4 138.0 KV 511423 TO L.E.S.-4 138.0 KV 511467 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLETCH_4__520911_0 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4( 520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLETCH_4__520911_0 | 3 Phase fault on FLETCH-4 (520912) 138 kV Bus a. Apply fault at the FLETCH-4( 520912) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCH-4 520912 TO FLETCHR2 520911 TO FLCHTERT 521168 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLETCHR4__FLE_TAP4 | 3 Phase fault on FLETCHR4 (511422) 138 kV Bus a. Apply fault at the FLETCHR4 (511422) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLETCHR4 138.0 KV 511422 TO FLE TAP4 138.0 KV 511423 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLOURNY2__507727_0 | 3 Phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2( 507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLOURNY2__507727_0 | 3 Phase fault on FLOURNY2 (507726) 69 kV Bus a. Apply fault at the FLOURNY2( 507726) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY2 507726 TO FLOURNY4 507727 TO FLOURNY1 507740 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FLOURNY4__SW_SHV_4 | 3 Phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY4 138.0 KV 507727 TO GENMOTR4 138.0 KV 507732 CKT 1 b.2. LOAD 1 507732 b.3. GENMOTR4 138.0 KV 507732 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FLOURNY4__SW_SHV_4 | 3 Phase fault on FLOURNY4 (507727) 138 kV Bus a. Apply fault at the FLOURNY4 (507727) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FLOURNY4 138.0 KV 507727 TO GENMOTR4 138.0 KV 507732 CKT 1 b.2. LOAD 1 507732 b.3. GENMOTR4 138.0 KV 507732 TO SW SHV 4 138.0 KV 507759 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FOREMAN2__PATTERS2 | 3 Phase fault on FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69.0 KV 507421 TO PATTERS2 69.0 KV 507429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FOREMAN2__PATTERS2 | 3 Phase fault on FOREMAN2 (507421) 69 kV Bus a. Apply fault at the FOREMAN2 (507421) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOREMAN2 69.0 KV 507421 TO PATTERS2 69.0 KV 507429 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FOURCTP4__FOURCNT4 | 3 Phase fault on FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO FOURCNT4 138.0 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FOURCTP4__FOURCNT4 | 3 Phase fault on FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO FOURCNT4 138.0 KV 520546 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FOURCTP4__TWNLKJT4 | 3 Phase fault on FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FOURCTP4__TWNLKJT4 | 3 Phase fault on FOURCTP4 (520545) 138 kV Bus a. Apply fault at the FOURCTP4 (520545) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FOURCTP4 138.0 KV 520545 TO TWNLKJT4 138.0 KV 520847 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRANKLN4__FRNKLNS4 | 3 Phase fault on FRANKLN4 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138.0 KV 520913 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FRANKLN4__FRNKLNS4 | 3 Phase fault on FRANKLN4 (520913) 138 kV Bus a. Apply fault at the FRANKLN4 (520913) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRANKLN4 138.0 KV 520913 TO FRNKLNS4 138.0 KV 520917 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRMNTAP4__BRECKNR4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.2. LOAD 1 514712 b.3. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.4. LOAD 1 515641 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FRMNTAP4__BRECKNR4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO FAIRMON4 138.0 KV 514712 CKT 1 b.2. LOAD 1 514712 b.3. FAIRMON4 138.0 KV 514712 TO PLNSMEN4 138.0 KV 515641 CKT 1 b.4. LOAD 1 515641 b.5. BRECKNR4 138.0 KV 514815 TO PLNSMEN4 138.0 KV 515641 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRMNTAP4__SO4TH__4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FRMNTAP4__SO4TH__4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO SO4TH 4 138.0 KV 514731 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRMNTAP4__WOODRNG4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FRMNTAP4__WOODRNG4 | 3 Phase fault on FRMNTAP4 (514709) 138 kV Bus a. Apply fault at the FRMNTAP4 (514709) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRMNTAP4 138.0 KV 514709 TO WOODRNG4 138.0 KV 514714 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRNKLNS4__520916_0 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4( 520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 520917 TO FRNKLNS2 520916 TO FRNKTERT 521169 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | FRNKLNS4__520916_0 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4( 520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 520917 TO FRNKLNS2 520916 TO FRNKTERT 521169 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRNKLNS4__LIDDELL4 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138.0 KV 520917 TO LIDDELL4 138.0 KV 520975 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | FRNKLNS4__LIDDELL4 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138.0 KV 520917 TO LIDDELL4 138.0 KV 520975 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRNKLNS4__WMOORE_4 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | FRNKLNS4__WMOORE_4 | 3 Phase fault on FRNKLNS4 (520917) 138 kV Bus a. Apply fault at the FRNKLNS4 (520917) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRNKLNS4 138.0 KV 520917 TO WMOORE 4 138.0 KV 521123 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRSTHIL2__515075_0 | 3 Phase fault on FRSTHIL2 (515074) 69 kV Bus a. Apply fault at the FRSTHIL2( 515074) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FRSTHIL2__515075_0 | 3 Phase fault on FRSTHIL2 (515074) 69 kV Bus a. Apply fault at the FRSTHIL2( 515074) 69 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL2 515074 TO FRSTHIL4 515075 TO FRSTHIL1 515725 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FRSTHIL4__STRLGTP4 | 3 Phase fault on FRSTHIL4 (515075) 138 kV Bus a. Apply fault at the FRSTHIL4 (515075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138.0 KV 515075 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Small Voltage Oscillations observed around Sunnyside (515136) due to the PPC of GEN-2017-232 (760265) | Disable the PPC for GEN-2017-232 (760265)
04 - Southeast | 25W | Transfer | FRSTHIL4__STRLGTP4 | 3 Phase fault on FRSTHIL4 (515075) 138 kV Bus a. Apply fault at the FRSTHIL4 (515075) 138 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FRSTHIL4 138.0 KV 515075 TO STRLGTP4 138.0 KV 515286 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSMITH7__515305_0 | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7( 515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSMITH7__515305_0 | 3 Phase fault on FTSMITH7 (515302) 345 kV Bus a. Apply fault at the FTSMITH7( 515302) 345 kV Bus b. Clear fault after 6 cycles and trip the faulted elements: b.1. FTSMITH7 515302 TO FTSMITH8 515305 TO FTSMTH11 515726 CKT 1 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSMTHE5__515305_0 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5( 515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSMTHE5__515305_0 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5( 515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 515300 TO FTSMITH8 515305 TO FTSMTH31 515727 CKT 3 Threewinding Transformer | P13 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSMTHE5__COLONY_5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO COLONY 5 161.0 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25W | Transfer | FTSMTHE5__COLONY_5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO COLONY 5 161.0 KV 515345 CKT 1 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes
04 - Southeast | 25S | Transfer | FTSMTHE5__FTSMTHW5 | 3 Phase fault on FTSMTHE5 (515300) 161 kV Bus a. Apply fault at the FTSMTHE5 (515300) 161 kV Bus b. Clear fault after 7 cycles and trip the faulted elements: b.1. FTSMTHE5 161.0 KV 515300 TO FTSMTHW5 161.0 KV 515301 CKT 2 c. Wait 20 cycles, and then reclose the faulted elements in (b) back into the Fault d. Leave Fault on for 7 cycles, then trip the faulted elements in (b) and clear the Fault | P12 | Yes | Yes | Yes | Yes | Yes | Yes | Yes